## MASTER Based on SubstationLoad
SHEPD | [10 empty] | 2019 / 20
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
ABERNETHY | 242 |  | 132/33 | 2 x 60 |  | 2019-11-19 17:10 | 36.463 | 1 |  | Diverse | 36.463 | 36.5472 |  | 36.722 | 36.8126 | 36.9054 | 37.0005 | 37.0979 | 37.1978 | 37.3001 | 37.4049 | 37.5124 | 37.6225 | 37.7353 | Diversity/Losses: 1.164 | 90.17% | 67.68% | 20.04% | 10130 | [7 empty] | 38.1 | -1.637
[6 empty] | 43788.7153 |  |  |  | Aggregate | 42.4262 | 42.5243 | 42.6247 | 42.7276 | 42.833 | 42.941 | 43.0516 | 43.165 | 43.2812 | 43.4002 | 43.5222 | 43.6472 | 43.7753 | 43.9066 |  | 32.8785 | 24.6779 | 7.3083 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [13 empty] | Generation at time of BSP peak: | 0.76481 | [7 empty] | 2019-10-30 17:26 | 2019-08-31 10:55 | 2019-08-18 02:57
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 35.7337 | 35.8163 | 35.9009 | 35.9875 | 36.0763 | 36.1673 | 36.2605 | 36.356 | 36.4538 | 36.5541 | 36.6568 | 36.7621 | 36.87 | 36.9806
| 242 | ABERNETHY | 33/11 | 1 x 2.5 |  | 2019-11-22 08:00 | 3.2556 | 1 | H | H |  |  |  | 3.5243 | 3.6187 |  | 3.8152 | 3.9174 | 4.0224 | 4.1301 | 4.2407 | 4.3543 | 4.471 | 4.5907 |  | 0% | 0% | 0.3348% | 80048 | 1111 | [6 empty] | 2.78 | 0.47564
[6 empty] | 43791.3333 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 0.010901 | 80% |  | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [14 empty] | Generation at time of peak: | 0.026979 | [9 empty] | 2019-09-24 18:30
| 255 | BALBEGGIE | 33/11 | 1 x 5 |  | 2019-11-20 17:10 | 4.061 | 1 | 0 | 0 |  | 4.0611 |  | 4.0612 | 4.0613 | 4.0614 | 4.0614 | 4.0615 | 4.0616 | 4.0617 | 4.0617 | 4.0618 | 4.0619 | 4.0619 |  | 87.65% | 78.97% | 0% | 80005 | [7 empty] | 3.89 | 0.17099
[6 empty] | 43789.7153 |  |  |  |  | Committed new connections: | [14 empty] | 3.5595 | 3.2069 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.17773 |  | 2019-10-31 17:07 | 2019-06-13 08:24 | 0
| 279 | BRIDGE OF EARN | 33/11 | 2 x 15 |  | 2019-11-19 17:48 | 3.2865 | 1 | 0 | 0 |  | 3.2865 | 3.2866 |  | 3.2867 | 3.2868 | 3.2868 | 3.2869 | 3.287 | 0 | 3.2871 | 3.2871 | 3.2872 | 3.2873 |  | 91.88% | 65.94% | 0% | 80028 | 3333 | [6 empty] | 3.28 | 0.00647
[6 empty] | 43788.7417 |  |  |  |  | Committed new connections: | [14 empty] | 3.0197 | 2.1672 | 0 | 60% |  | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 17:23 | 2019-06-13 17:23 | 0
| 254 | ERROL | 33/11 | 2 x 5 |  | 2020-01-20 07:30 | 4.5323 | 1 | 0 | 0 | 4.5323 | 4.5324 | 4.5325 |  | 4.5326 | 4.5327 | 4.5328 | 4.5329 | 4.5329 | 4.533 | 4.5331 | 4.5332 | 4.5333 | 4.5334 |  | 0% | 0% | 24.56% | 80013 | [7 empty] | 4.55 | -0.017712
[6 empty] | 43850.3125 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 1.1132 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.051883 |  |  |  | 2019-07-16 02:00
| 273 | GLENDEVON | 33/11 | 1 x 8 |  | 2019-11-12 17:30 | 1.8314 | 1 | L | L | 1.8314 | 1.8416 | 1.8518 | 1.862 | 1.8724 | 1.8827 | 1.8932 | 1.9037 | 1.9142 | 1.9248 | 1.9355 | 1.9462 | 1.957 | 1.9678 |  | 0% | 0% | 0% | 80033 | 4444 | 333 | [5 empty] | 1.7943 | 0.037149
[6 empty] | 43781.7292 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 0 | 70% |  | 10% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.482 |  |  |  | 2019-06-11 18:30
| 251 | MILNATHORT | 33/11 | 2 x 15 |  | 2019-11-19 17:30 | 11.4965 | 1 | 0 | 0 | 11.4965 | 11.4968 | 11.497 | 11.4972 | 11.4974 | 11.4976 | 11.4978 | 11.498 | 11.4982 | 11.4984 | 11.4986 | 11.4989 | 11.4991 | 11.4993 |  | 0% | 0% | 19.62% | 80037 | [7 empty] | 11.0647 | 0.43188
[6 empty] | 43788.7292 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 2.2559 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.15074 |  |  |  | 2019-07-01 05:00
| 247 | HARBOUR | 33/11 | 2 x 9.5/20 |  | 2019-12-18 14:43 | 9.8876 | 1 | 0 | 0 | 9.8876 | 9.8878 | 9.8879 | 9.8881 | 9.8883 | 9.8885 | 9.8887 | 9.8888 | 9.889 | 9.8892 | 9.8894 | 9.8896 | 9.8897 | 9.8899 |  | 79.96% | 68.39% | 0% | 80019 | 222 | 5555 | [5 empty] | 9.2331 | 0.65447
[6 empty] | 43817.6132 |  |  |  |  | Committed new connections: | [14 empty] | 7.9062 | 6.762 | 0 |  | 30% |  | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 17:22 | 2019-06-24 12:02 | 0
| 271 | SCONE | 33/11 | 2 x 7.5/15 |  | 2019-12-01 17:14 | 4.0753 | 1 | 0 | 0 | 4.0753 | 4.0754 | 4.0754 | 4.0755 | 4.0756 | 4.0757 | 4.0757 | 4.0758 | 4.0759 | 4.076 | 4.076 | 4.0761 | 4.0762 | 4.0763 |  | 91.03% | 60.75% | 0% | 80008 | [7 empty] | 4.13 | -0.054715
[6 empty] | 43800.7181 |  |  |  |  | Committed new connections: | [14 empty] | 3.7097 | 2.4758 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-27 17:29 | 2019-08-11 17:21 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
ALNESS | 502 |  | 132/33 | 2 x 120 |  | 2020-01-10 13:35 | 137.5609 | 1 |  | Diverse | 137.5609 | 138.0912 | 138.6358 | 139.1948 | 139.7688 | 140.3581 | 140.9632 | 141.5843 | 142.2221 | 142.8769 | 143.5492 | 144.2394 | 144.948 | 145.6756 | Diversity/Losses: 0.236 | 75.37% | 76.57% | -23.73% | 10330 | [7 empty] | 35.1 | 102.4609
[6 empty] | 43840.566 |  |  |  | Aggregate | 32.5127 | 32.6381 | 32.7668 | 32.8989 | 33.0346 | 33.1739 | 33.3169 | 33.4637 | 33.6144 | 33.7692 | 33.9281 | 34.0912 | 34.2587 | 34.4307 |  | 103.6759 | 105.324 | -32.6492 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 80.1327 |  | 2019-09-02 13:41 | 2019-08-30 02:55 | 2019-12-15 21:27
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 134.8096 | 135.3294 | 135.8631 | 136.4109 | 136.9735 | 137.551 | 138.1439 | 138.7527 | 139.3777 | 140.0193 | 140.6782 | 141.3546 | 142.0491 | 142.7621
| 552 | BALALDIE | 33/11 | 1 x 4 |  | 2019-12-25 11:07 | 3.0002 | 1 | H | H | 3.0002 | 3.0806 | 3.1631 | 3.2479 | 3.3349 | 3.4242 | 3.5159 | 3.6101 | 3.7068 | 3.8061 | 3.9081 | 4.0128 | 4.1202 | 4.2306 |  | 87.91% | 60.84% | 0% | 80109 | [7 empty] | 2.98 | 0.020247
[6 empty] | 43824.4632 |  |  |  |  | Committed new connections: | [14 empty] | 2.6374 | 1.8253 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-29 20:06 | 2019-06-13 17:22 | 0
| 509 | BLACKSTAND | 33/11 | 1 x 6 |  | 2019-12-25 11:04 | 2.7951 | 1 | 0 | 0 | 2.7951 | 2.7952 | 2.7952 | 2.7953 | 2.7953 | 2.7954 | 2.7954 | 2.7955 | 2.7955 | 2.7956 | 2.7956 | 2.7957 | 2.7957 | 2.7958 |  | 84.43% | 68.51% | 0% | 80157 | [7 empty] | 2.65 | 0.14511
[6 empty] | 43824.4611 |  |  |  |  | Committed new connections: | [14 empty] | 2.3599 | 1.9149 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 20:04 | 2019-06-24 17:36 | 0
| 541 | CONTULLICH | 33/11 | 1 x 0.1 |  | No PI | 0.039332 | 1 | 0 | 0 | 0.039332 | 0.039332 | 0.039333 | 0.039334 | 0.039335 | 0.039335 | 0.039336 | 0.039337 | 0.039337 | 0.039338 | 0.039339 | 0.03934 | 0.03934 | 0.039341 |  | 0% | 0% | 0% | 80128 | [7 empty] | 0.039332 | 0
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 551 | CROSSHILLS | 33/11 | 2 x 15 |  | 2020-01-15 13:48 | 6.9127 | 1 | 0 | 0 | 6.9127 | 6.9128 | 6.9129 | 6.913 | 6.9132 | 6.9133 | 6.9134 | 6.9135 | 6.9137 | 6.9138 | 6.9139 | 6.914 | 6.9142 | 6.9143 |  | 98.1% | 81.87% | 0% | 80125 | [7 empty] | 6.54 | 0.37266
[6 empty] | 43845.575 |  |  |  |  | Committed new connections: | [14 empty] | 6.7815 | 5.6596 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-04 12:12 | 2019-06-06 12:10 | 0
| 522 | GLASTULLICH | 33/11 | 1 x 8 |  | 2020-01-16 08:30 | 1.4999 | 1 | 0 | 0 | 1.4999 | 1.5 | 1.5 | 1.5 | 1.5001 | 1.5001 | 1.5001 | 1.5001 | 1.5002 | 1.5002 | 1.5002 | 1.5002 | 1.5003 | 1.5003 |  | 0% | 0% | 2.01% | 80111 | [7 empty] | 1.35 | 0.14994
[6 empty] | 43846.3542 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 0.030142 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  |  |  | 2019-06-03 12:30
| 559 | INVERGORDON | 33/11 | 2 x 15 |  | 2020-01-28 16:30 | 5.7607 | 1 | 0 | 0 | 5.7607 | 5.7608 | 5.761 | 5.7611 | 5.7612 | 5.7613 | 5.7614 | 5.7615 | 5.7616 | 5.7617 | 5.7618 | 5.7619 | 5.762 | 5.7621 |  | 0% | 0% | 19.55% | 80138 | [7 empty] | 8.5 | -2.7393
[6 empty] | 43858.6875 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 1.1261 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 6.975 |  |  |  | 2019-07-21 01:30
| 576 | LEALTY | 33/11 | 1 x 0.5 |  | No PI | 0 | 1 | ? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 80150 | [7 empty] | 0 | 0
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 542 | MUIREND | 33/11 | 1 x 6 |  | 2019-12-25 11:04 | 2.6198 | 1 | 0 | 0 | 2.6198 | 2.6198 | 2.6199 | 2.6199 | 2.62 | 2.62 | 2.6201 | 2.6201 | 2.6202 | 2.6202 | 2.6203 | 2.6203 | 2.6204 | 2.6204 |  | 87.71% | 61.87% | 0% | 80160 | [7 empty] | 2.4282 | 0.19157
[6 empty] | 43824.4611 |  |  |  |  | Committed new connections: | [14 empty] | 2.2978 | 1.621 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-29 18:19 | 2019-06-05 18:14 | 0
| 554 | NIGG | 33/11 | 1 x 15 |  | 2019-04-03 13:54 | 1.6605 | 1 | H | H | 1.6605 | 1.705 | 1.7506 | 1.7975 | 1.8457 | 1.8951 | 1.9459 | 1.998 | 2.0515 | 2.1065 | 2.1629 | 2.2209 | 2.2804 | 2.3414 |  | 100% | 76.13% | 0% | 80117 | [7 empty] | 2.2138 | -0.55335
[6 empty] | 43558.5792 |  |  |  |  | Committed new connections: | [14 empty] | 1.6605 | 1.2642 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 13:54 | 2019-06-10 10:52 | 0
| 553 | PEDDIESTON | 33/11 | 2 x 2.5 |  | 2019-12-17 20:07 | 1.8654 | 1 | 0 | 0 | 1.8654 | 1.8654 | 1.8654 | 1.8655 | 1.8655 | 1.8656 | 1.8656 | 1.8656 | 1.8657 | 1.8657 | 1.8657 | 1.8658 | 1.8658 | 1.8658 |  | 81.13% | 58.12% | 0% | 80132 | [7 empty] | 1.7018 | 0.1636
[6 empty] | 43816.8382 |  |  |  |  | Committed new connections: | [14 empty] | 1.5134 | 1.0841 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-27 20:04 | 2019-08-23 18:47 | 0
| 546 | TAIN | 33/11 | 2 x 15 |  | 2019-11-19 20:26 | 6.359 | 1 | 0 | 0 | 6.359 | 6.3592 | 6.3593 | 6.3594 | 6.3595 | 6.3596 | 6.3597 | 6.3598 | 6.36 | 6.3601 | 6.3602 | 6.3603 | 6.3604 | 6.3605 |  | 82.27% | 61.11% | 0% | 80105 | [7 empty] | 6.48 | -0.12097
[6 empty] | 43788.8514 |  |  |  |  | Committed new connections: | [14 empty] | 5.2313 | 3.8858 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 12:08 | 2019-06-13 20:04 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
ARBROATH | 61 |  | 132/33 | 2 x 45 |  | 2019-12-23 12:11 | 31.5358 | 1 |  | Diverse | 31.5358 | 31.5364 | 31.5369 | 31.5375 | 31.5381 | 31.5387 | 31.5393 | 31.5398 | 31.5404 | 31.541 | 31.5416 | 31.5421 | 31.5427 | 31.5433 | Diversity/Losses: 1.081 | 95.86% | 74.79% | 24.74% | 10430 | [7 empty] | 30.9 | 0.6358
[6 empty] | 43822.5076 |  |  |  | Aggregate | 34.0896 | 34.0902 | 34.0908 | 34.0914 | 34.0921 | 34.0927 | 34.0933 | 34.0939 | 34.0946 | 34.0952 | 34.0958 | 34.0964 | 34.097 | 34.0977 |  | 30.2298 | 23.5863 | 7.8013 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 1.4918 |  | 2019-10-15 18:36 | 2019-06-24 17:01 | 2019-08-17 14:36
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 30.9051 | 30.9056 | 30.9062 | 30.9068 | 30.9073 | 30.9079 | 30.9085 | 30.909 | 30.9096 | 30.9102 | 30.9107 | 30.9113 | 30.9119 | 30.9124
| 64 | CARNOUSTIE | 33/11 | 2 x 15 |  | 2019-12-18 17:26 | 7.5459 | 1 | 0 | 0 | 7.5459 | 7.546 | 7.5461 | 7.5463 | 7.5464 | 7.5466 | 7.5467 | 7.5468 | 7.547 | 7.5471 | 7.5472 | 7.5474 | 7.5475 | 7.5477 |  | 92.53% | 74.4% | 0% | 80206 | [7 empty] | 7.64 | -0.094139
[6 empty] | 43817.7264 |  |  |  |  | Committed new connections: | [14 empty] | 6.982 | 5.6144 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-28 17:24 | 2019-06-24 17:38 | 0
| 62 | CHARLES AVENUE | 33/11 | 2 x 10 |  | 2019-11-19 17:16 | 9.4341 | 1 | 0 | 0 | 9.4341 | 9.4343 | 9.4344 | 9.4346 | 9.4348 | 9.4349 | 9.4351 | 9.4353 | 9.4355 | 9.4356 | 9.4358 | 9.436 | 9.4362 | 9.4363 |  | 90.36% | 79.77% | 0% | 80218 | [7 empty] | 9.18 | 0.25409
[6 empty] | 43788.7194 |  |  |  |  | Committed new connections: | [14 empty] | 8.5243 | 7.5252 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 17:15 | 2019-06-13 10:50 | 0
| 68 | ELLIOT DEPOT | 33/11 | 1 x 15 |  | 2019-12-10 14:33 | 5.4142 | 1 | 0 | 0 | 5.4142 | 5.4143 | 5.4144 | 5.4145 | 5.4146 | 5.4147 | 5.4148 | 5.4149 | 5.415 | 5.4151 | 5.4152 | 5.4153 | 5.4154 | 5.4155 |  | 94.85% | 92.89% | 0% | 80215 | [7 empty] | 5.04 | 0.37421
[6 empty] | 43809.6062 |  |  |  |  | Committed new connections: | [14 empty] | 5.1351 | 5.0291 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-17 09:42 | 2019-08-27 11:19 | 0
| 67 | HUME STREET | 33/11 | 2 x 24 |  | 2019-11-19 16:29 | 8.7981 | 1 | 0 | 0 | 8.7981 | 8.7982 | 8.7984 | 8.7985 | 8.7987 | 8.7989 | 8.799 | 8.7992 | 8.7993 | 8.7995 | 8.7997 | 8.7998 | 8.8 | 8.8001 |  | 93.02% | 73.47% | 0% | 80222 | [7 empty] | 9.01 | -0.21194
[6 empty] | 43788.6868 |  |  |  |  | Committed new connections: | [14 empty] | 8.1841 | 6.4635 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 11:49 | 2019-06-13 11:30 | 0
| 66 | REDFORD | 33/11 | 1 x 4/8 |  | 2019-11-06 17:30 | 2.8973 | 1 | 0 | 0 | 2.8973 | 2.8974 | 2.8975 | 2.8975 | 2.8976 | 2.8976 | 2.8977 | 2.8977 | 2.8978 | 2.8978 | 2.8979 | 2.8979 | 2.898 | 2.898 |  | 94.99% | 64.05% | 0% | 80202 | [7 empty] | 2.9069 | -0.0095123
[6 empty] | 43775.7292 |  |  |  |  | Committed new connections: | [14 empty] | 2.7523 | 1.8556 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.030399 |  | 2019-10-31 17:23 | 2019-06-03 12:01 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
BEAULY | 506 |  | 132/33 | 2 x 45 |  | 2019-11-20 07:23 | 24.9014 | 1 |  | Diverse | 24.9014 | 25.0456 | 25.1918 | 25.3398 | 25.4898 | 25.6418 | 25.7958 | 25.9518 | 26.11 | 26.2702 | 26.4325 | 26.597 | 26.7636 | 26.9325 | Diversity/Losses: 1.283 | 86.64% | 71.09% | 9.788% | 10630 | [7 empty] | 31.4 | -6.4986
[6 empty] | 43789.3076 |  |  |  | Aggregate | 31.9421 | 32.127 | 32.3144 | 32.5043 | 32.6968 | 32.8917 | 33.0893 | 33.2894 | 33.4923 | 33.6978 | 33.906 | 34.117 | 34.3308 | 34.5474 |  | 21.5755 | 17.7031 | 2.4373 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 0.18145 |  | 2019-10-30 17:46 | 2019-06-24 17:41 | 2020-02-02 02:17
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 24.4034 | 24.5447 | 24.6879 | 24.833 | 24.98 | 25.129 | 25.2799 | 25.4328 | 25.5878 | 25.7448 | 25.9038 | 26.065 | 26.2284 | 26.3939
| 501 | AIGAS | 33/11 | 1 x 0.5 |  | No PI | 0.19104 | 1 | 0 | 0 | 0.19104 | 0.19104 | 0.19105 | 0.19105 | 0.19105 | 0.19106 | 0.19106 | 0.19106 | 0.19107 | 0.19107 | 0.19107 | 0.19108 | 0.19108 | 0.19109 |  | 0% | 0% | 0% | 80336 | [7 empty] | 0.19104 | 0
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 562 | COMRIE | 33/11 | 1 x 0.05 |  | No PI | 0.028094 | 1 | 0 | 0 | 0.028094 | 0.028095 | 0.028095 | 0.028096 | 0.028096 | 0.028097 | 0.028097 | 0.028098 | 0.028098 | 0.028099 | 0.028099 | 0.0281 | 0.0281 | 0.028101 |  | 0% | 0% | 0% | 80341 | [7 empty] | 0.028094 | 0
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 513 | CONON BRIDGE | 33/11 | 2 x 6.25 |  | 2019-11-19 17:36 | 5.76 | 1 | 0 | 0 | 5.76 | 5.7601 | 5.7602 | 5.7603 | 5.7604 | 5.7605 | 5.7606 | 5.7607 | 5.7608 | 5.7609 | 5.7611 | 5.7612 | 5.7613 | 5.7614 |  | 0% | 59.17% | 0% | 80322 | [7 empty] | 2.99 | 2.77
[6 empty] | 43788.7333 |  |  |  |  | Committed new connections: | [14 empty] | #VALUE! | 3.408 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | #VALUE! | 2019-07-01 17:45 | 0
| 514 | CONON FALLS | 33/11 | 1 x 0.5 |  | No PI | 0.35679 | 1 | M | M | 0.35679 | 0.36165 | 0.36657 | 0.37156 | 0.37661 | 0.38174 | 0.38693 | 0.39219 | 0.39753 | 0.40294 | 0.40842 | 0.41397 | 0.41961 | 0.42532 |  | 0% | 0% | 0% | 80345 | [7 empty] | 0.35679 | 0
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | #VALUE! | No Data | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | #VALUE! | Missing Data | 0
| 515 | DINGWALL | 33/11 | 2 x 15 |  | 2019-11-19 11:00 | 8.8249 | 1 | 0 | 0 | 8.8249 | 8.825 | 8.8252 | 8.8254 | 8.8255 | 8.8257 | 8.8258 | 8.826 | 8.8262 | 8.8263 | 8.8265 | 8.8267 | 8.8268 | 8.827 |  | 0% | 0% | 3.265% | 80302 | [7 empty] | 9.45 | -0.62512
[6 empty] | 43788.4583 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 0.28814 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.16284 |  |  |  | 2019-07-23 04:30
| 520 | KILTARLITY | 33/11 | 1 x 6 |  | 2019-11-19 19:06 | 1.4349 | 1 | L | L | 1.4349 | 1.4428 | 1.4508 | 1.4589 | 1.4669 | 1.4751 | 1.4833 | 1.4915 | 1.4997 | 1.508 | 1.5164 | 1.5248 | 1.5333 | 1.5418 |  | 86.94% | 56.93% | 0% | 80361 | [7 empty] | 1.324 | 0.11087
[6 empty] | 43788.7958 |  |  |  |  | Committed new connections: | [14 empty] | 1.2474 | 0.81692 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 20:03 | 2019-08-19 19:02 | 0
| 538 | MARYBANK | 33/11 | 1 x 4 |  | 2019-12-25 12:10 | 1.3677 | 1 | 0 | 0 | 1.3677 | 1.3677 | 1.3678 | 1.3678 | 1.3678 | 1.3678 | 1.3679 | 1.3679 | 1.3679 | 1.3679 | 1.368 | 1.368 | 1.368 | 1.368 |  | 87.5% | 66.07% | 0% | 80316 | [7 empty] | 1.32 | 0.047704
[6 empty] | 43824.5069 |  |  |  |  | Committed new connections: | [14 empty] | 1.1967 | 0.90366 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-09 07:09 | 2019-06-06 08:10 | 0
| 547 | MUIR OF ORD | 33/11 | 2 x 12/24 |  | 2019-12-18 20:06 | 12.6313 | 1 | M | M | 12.6313 | 12.8032 | 12.9773 | 13.1539 | 13.3328 | 13.5142 | 13.6981 | 13.8845 | 14.0734 | 14.2648 | 14.4589 | 14.6556 | 14.855 | 15.0571 |  | 96.6% | 83.96% | 0% | 80327 | [7 empty] | 12.5677 | 0.06359
[6 empty] | 43817.8375 |  |  |  |  | Committed new connections: | [14 empty] | 12.2015 | 10.6052 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 20:17 | 2019-06-05 18:16 | 0
| 558 | NORTH KESSOCK | 33/11 | 1 x 4 |  | 2020-01-13 17:40 | 1.3474 | 1 | 0 | 0 | 1.3474 | 1.3474 | 1.3474 | 1.3474 | 1.3475 | 1.3475 | 1.3475 | 1.3475 | 1.3476 | 1.3476 | 1.3476 | 1.3476 | 1.3477 | 1.3477 |  | 87.33% | 69% | 0% | 80339 | [7 empty] | 1.2838 | 0.063607
[6 empty] | 43843.7361 |  |  |  |  | Committed new connections: | [14 empty] | 1.1767 | 0.92974 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 18:56 | 2019-06-05 18:19 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
BOAT OF GARTEN | 707 |  | 132/33 | 2 x 60 |  | 2019-11-19 11:07 | 27.9453 | 1 |  | Diverse | 27.9453 | 28.0919 | 28.2405 | 28.3911 | 28.5438 | 28.6985 | 28.8553 | 29.0143 | 29.1754 | 29.3387 | 29.5043 | 29.672 | 29.8421 | 30.0145 | Diversity/Losses: 1.046 | 82.14% | 57.4% | 13.95% | 10830 | [7 empty] | 27.9 | 0.045276
[6 empty] | 43788.4632 |  |  |  | Aggregate | 29.2293 | 29.3826 | 29.538 | 29.6956 | 29.8553 | 30.0171 | 30.1811 | 30.3474 | 30.5159 | 30.6868 | 30.8599 | 31.0354 | 31.2133 | 31.3935 |  | 22.955 | 16.0418 | 3.8984 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 0 |  | 2019-10-31 10:35 | 2019-07-05 17:41 | 2019-07-11 00:59
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 27.3864 | 27.53 | 27.6757 | 27.8233 | 27.9729 | 28.1245 | 28.2782 | 28.434 | 28.5919 | 28.752 | 28.9142 | 29.0786 | 29.2453 | 29.4142
| 704 | AVIEMORE | 33/11 | 2 x 24 |  | 2020-02-13 19:36 | 9.0437 | 1 | 0 | 0 | 9.0437 | 9.0438 | 9.044 | 9.0442 | 9.0443 | 9.0445 | 9.0447 | 9.0448 | 9.045 | 9.0452 | 9.0453 | 9.0455 | 9.0457 | 9.0458 |  | 90.22% | 65.52% | 0% | 80416 | [7 empty] | 9.48 | -0.43632
[6 empty] | 43874.8167 |  |  |  |  | Committed new connections: | [14 empty] | 8.1595 | 5.9257 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 10:32 | 2019-06-12 17:27 | 0
| 706 | BALLINDALLOCH | 33/11 | 2 x 5 |  | 2019-11-18 16:52 | 4.08 | 1 | M | M | 4.08 | 4.1355 | 4.1918 | 4.2488 | 4.3066 | 4.3652 | 4.4246 | 4.4848 | 4.5458 | 4.6076 | 4.6703 | 4.7339 | 4.7983 | 4.8635 |  | 94.12% | 61.57% | 0% | 80410 | [7 empty] | 3.95 | 0.13
[6 empty] | 43787.7028 |  |  |  |  | Committed new connections: | [14 empty] | 3.84 | 2.512 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-01 19:38 | 2019-06-13 09:39 | 0
| 708 | BOAT OF GARTEN 11 kV | 33/11 | 2 x 8 |  | 2020-02-18 11:06 | 3.4541 | 1 | 0 | 0 | 3.4541 | 3.4542 | 3.4543 | 3.4543 | 3.4544 | 3.4545 | 3.4545 | 3.4546 | 3.4546 | 3.4547 | 3.4548 | 3.4548 | 3.4549 | 3.455 |  | 88.48% | 72.01% | 0% | 80412 | [7 empty] | 3.43 | 0.02414
[6 empty] | 43879.4625 |  |  |  |  | Committed new connections: | [14 empty] | 3.0562 | 2.4875 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-02 06:55 | 2019-06-06 07:11 | 0
| 777 | DALWHINNIE | 33/11 | 1 x 1 |  | 2020-01-08 10:41 | 0.78813 | 1 | 0 | 0 | 0.78813 | 0.78815 | 0.78816 | 0.78818 | 0.78819 | 0.78821 | 0.78822 | 0.78823 | 0.78825 | 0.78826 | 0.78828 | 0.78829 | 0.78831 | 0.78832 |  | 87.49% | 71.43% | 0% | 80429 | [7 empty] | 0.75 | 0.038133
[6 empty] | 43838.4451 |  |  |  |  | Committed new connections: | [14 empty] | 0.6895 | 0.56295 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-11 07:11 | 2019-06-13 09:55 | 0
| 722 | GRANTOWN | 33/11 | 2 x 15 |  | 2019-12-23 03:33 | 6.2997 | 1 | M | M | 6.2997 | 6.3854 | 6.4723 | 6.5604 | 6.6496 | 6.7401 | 6.8318 | 6.9247 | 7.0189 | 7.1144 | 7.2112 | 7.3093 | 7.4088 | 7.5096 |  | 81.1% | 62.2% | 0% | 80405 | [7 empty] | 6.42 | -0.12027
[6 empty] | 43822.1479 |  |  |  |  | Committed new connections: | [14 empty] | 5.109 | 3.9183 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-31 03:37 | 2019-06-13 10:47 | 0
| 727 | KINGUSSIE | 33/11 | 2 x 7 |  | 2019-12-01 11:03 | 4.696 | 1 | 0 | 0 | 4.696 | 4.6961 | 4.6962 | 4.6963 | 4.6963 | 4.6964 | 4.6965 | 4.6966 | 4.6967 | 4.6968 | 4.6969 | 4.6969 | 4.697 | 4.6971 |  | 77.09% | 59.71% | 0% | 80422 | [7 empty] | 4.57 | 0.126
[6 empty] | 43800.4604 |  |  |  |  | Committed new connections: | [14 empty] | 3.62 | 2.804 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 19:33 | 2019-06-12 19:36 | 0
| 738 | TOMATIN | 33/11 | 1 x 2 |  | 2019-11-20 18:37 | 0.86759 | 1 | M | M | 0.86759 | 0.87939 | 0.89136 | 0.90348 | 0.91578 | 0.92824 | 0.94086 | 0.95366 | 0.96664 | 0.97979 | 0.99312 | 1.0066 | 1.0203 | 1.0342 |  | 87.1% | 64.52% | 0% | 80403 | [7 empty] | 0.77 | 0.09759
[6 empty] | 43789.7757 |  |  |  |  | Committed new connections: | [14 empty] | 0.75564 | 0.55974 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 08:40 | 2019-06-04 08:04 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
BRACO WEST | 290 |  | 275/33 | 2 x 120 |  | 2020-02-01 05:33 | 90.5813 | 1 |  | Diverse | 90.5813 | 90.5829 | 90.5846 | 90.5862 | 90.5879 | 90.5895 | 90.5912 | 90.5928 | 90.5945 | 90.5961 | 90.5978 | 90.5994 | 90.6011 | 90.6028 | Diversity/Losses: 0.442 | 81.26% | 70.56% | -59.76% | 10930 | [7 empty] | 42.4 | 48.1813
[6 empty] | 43862.2312 |  |  |  | Aggregate | 40.0238 | 40.0246 | 40.0253 | 40.026 | 40.0267 | 40.0275 | 40.0282 | 40.0289 | 40.0297 | 40.0304 | 40.0311 | 40.0319 | 40.0326 | 40.0333 |  | 73.606 | 63.9124 | -54.1327 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 36.1541 |  | 2019-09-03 16:41 | 2019-08-13 15:16 | 2019-11-27 23:35
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 88.7696 | 88.7713 | 88.7729 | 88.7745 | 88.7761 | 88.7777 | 88.7794 | 88.781 | 88.7826 | 88.7842 | 88.7858 | 88.7875 | 88.7891 | 88.7907
| 210 | CALLANDER | 33/11 | 1 x 5 |  | 2019-11-19 15:00 | 4.5924 | 1 | 0 | 0 | 4.5924 | 4.5925 | 4.5926 | 4.5927 | 4.5928 | 4.5929 | 4.5929 | 4.593 | 4.5931 | 4.5932 | 4.5933 | 4.5934 | 4.5934 | 4.5935 |  | 0% | 0% | 1.962% | 80524 | [7 empty] | 4.57 | 0.022433
|  |  |  | 1 x 8 |  | 43788.625 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 0.090126 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  |  |  | 2019-08-31 23:30
| 208 | CRIEFF | 33/11 | 2 x 15 |  | 2020-03-02 18:51 | 8.2143 | 1 | 0 | 0 | 8.2143 | 8.2144 | 8.2146 | 8.2147 | 8.2149 | 8.215 | 8.2152 | 8.2153 | 8.2155 | 8.2156 | 8.2158 | 8.2159 | 8.2161 | 8.2162 |  | 75.54% | 55.58% | 0% | 80509 | [7 empty] | 9.27 | -1.0557
[6 empty] | 43892.7854 |  |  |  |  | Committed new connections: | [14 empty] | 6.2049 | 4.5653 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-28 17:30 | 2019-06-03 17:26 | 0
| 209 | DUNBLANE | 33/11 | 2 x 12.5 |  | 2019-12-02 17:40 | 9.3825 | 1 | 0 | 0 | 9.3825 | 9.3826 | 9.3828 | 9.383 | 9.3832 | 9.3833 | 9.3835 | 9.3837 | 9.3838 | 9.384 | 9.3842 | 9.3844 | 9.3845 | 9.3847 |  | 91.53% | 70.48% | 0% | 80514 | [7 empty] | 8.93 | 0.45247
[6 empty] | 43801.7361 |  |  |  |  | Committed new connections: | [14 empty] | 8.5879 | 6.6126 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-31 17:50 | 2019-06-12 18:01 | 0
| 253 | FORTEVIOT | 33/11 | 1 x 6.25 |  | 2019-11-19 18:02 | 1.8505 | 1 | 0 | 0 | 1.8505 | 1.8505 | 1.8506 | 1.8506 | 1.8506 | 1.8507 | 1.8507 | 1.8507 | 1.8508 | 1.8508 | 1.8508 | 1.8509 | 1.8509 | 1.8509 |  | 84.95% | 66.67% | 0% | 80503 | [7 empty] | 1.72 | 0.13051
[6 empty] | 43788.7514 |  |  |  |  | Committed new connections: | [14 empty] | 1.5719 | 1.2337 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-28 17:39 | 2019-06-05 18:05 | 0
| 207 | GLENEAGLES | 33/11 | 2 x 15 |  | 2020-01-09 17:27 | 11.4052 | 1 | 0 | 0 | 11.4052 | 11.4054 | 11.4056 | 11.4058 | 11.406 | 11.4062 | 11.4064 | 11.4066 | 11.4068 | 11.407 | 11.4072 | 11.4074 | 11.4077 | 11.4079 |  | 89.07% | 77% | 0% | 80506 | [7 empty] | 11.06 | 0.34515
[6 empty] | 43839.7271 |  |  |  |  | Committed new connections: | [14 empty] | 10.1586 | 8.7818 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 17:25 | 2019-06-12 18:03 | 0
| 211 | KIPPEN | 33/11 | 2 x 8 |  | 2019-11-19 07:18 | 4.579 | 1 | 0 | 0 | 4.579 | 4.579 | 4.5791 | 4.5792 | 4.5793 | 4.5794 | 4.5795 | 4.5795 | 4.5796 | 4.5797 | 4.5798 | 4.5799 | 4.58 | 4.58 |  | 85.37% | 57.11% | 0% | 80520 | [7 empty] | 4.53 | 0.048958
[6 empty] | 43788.3042 |  |  |  |  | Committed new connections: | [14 empty] | 3.9091 | 2.6149 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 17:19 | 2019-06-12 17:22 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
BRIDGE OF DUN | 71 |  | 132/33 | 2 x 60 |  | 2019-11-30 16:54 | 25.1996 | 1 |  | Diverse | 25.1996 | 25.2542 | 25.31 | 25.3671 | 25.4255 | 25.4851 | 25.5462 | 25.6086 | 25.6724 | 25.7378 | 25.8046 | 25.8729 | 25.9428 | 26.0143 | Diversity/Losses: 1.059 | 84.01% | 76.24% | -48.73% | 11130 | [7 empty] | 26.5 | -1.3004
[6 empty] | 43799.7042 |  |  |  | Aggregate | 26.6849 | 26.7427 | 26.8018 | 26.8623 | 26.9241 | 26.9873 | 27.0519 | 27.118 | 27.1856 | 27.2548 | 27.3255 | 27.3979 | 27.4719 | 27.5476 |  | 21.1713 | 19.212 | -12.2808 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 0.35371 |  | 2019-09-30 17:33 | 2019-08-20 17:35 | 2020-01-24 02:18
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 24.6956 | 24.7491 | 24.8038 | 24.8597 | 24.9169 | 24.9754 | 25.0352 | 25.0964 | 25.159 | 25.223 | 25.2885 | 25.3554 | 25.4239 | 25.494
| 73 | BRECHIN | 33/11 | 2 x 10 |  | 2019-11-19 17:00 | 7.1433 | 1 | 0 | 0 | 7.1433 | 7.1435 | 7.1436 | 7.1437 | 7.1439 | 7.144 | 7.1441 | 7.1442 | 7.1444 | 7.1445 | 7.1446 | 7.1448 | 7.1449 | 7.145 |  | 88.89% | 67.53% | 0% | 80608 | [7 empty] | 7.14 | 0.0033301
[6 empty] | 43788.7083 |  |  |  |  | Committed new connections: | [14 empty] | 6.3497 | 4.8238 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.00093031 |  | 2019-10-30 16:59 | 2019-06-24 16:45 | 0
| 72 | BRIDGE OF DUN 11kV | 33/11 | 1 x 2.5 |  | 2019-09-09 18:07 | 0.75169 | 1 | 0 | 0 | 0.75169 | 0.7517 | 0.75172 | 0.75173 | 0.75174 | 0.75176 | 0.75177 | 0.75179 | 0.7518 | 0.75181 | 0.75183 | 0.75184 | 0.75185 | 0.75187 |  | 100% | 96.91% | 0% | 80606 | [7 empty] | 0.56 | 0.19169
[6 empty] | 43717.7549 |  |  |  |  | Committed new connections: | [14 empty] | 0.75169 | 0.72843 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-09-09 18:07 | 2019-08-30 14:49 | 0
| 5 | GLAXO (33kV Customer) | 33kV Customer |  |  | 2019-09-09 08:00 | 3.956 | 1 | ? | 0 | 3.956 | 3.9561 | 3.9561 | 3.9562 | 3.9563 | 3.9563 | 3.9564 | 3.9565 | 3.9566 | 3.9566 | 3.9567 | 3.9568 | 3.9568 | 3.9569 |  | 0% | 0% | 0% | 80617 | [7 empty] | 2.6817 | 1.2743
[6 empty] | 43717.3333 |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 76 | INCHBARE | 33/11 | 1 x 2.5 |  | 2019-11-19 15:53 | 1.1126 | 1 | 0 | 0 | 1.1126 | 1.1127 | 1.1127 | 1.1127 | 1.1127 | 1.1127 | 1.1128 | 1.1128 | 1.1128 | 1.1128 | 1.1128 | 1.1129 | 1.1129 | 1.1129 |  | 94.52% | 75.34% | 0% | 80605 | [7 empty] | 1.18 | -0.067363
[6 empty] | 43788.6618 |  |  |  |  | Committed new connections: | [14 empty] | 1.0517 | 0.83829 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-31 08:48 | 2019-06-24 09:48 | 0
| 77 | LOGIE PERT | 33/11 | 1 x 5 |  | 2019-10-01 17:11 | 1.48 | 1 | H | H | 1.48 | 1.5197 | 1.5604 | 1.6022 | 1.6451 | 1.6891 | 1.7344 | 1.7809 | 1.8286 | 1.8775 | 1.9278 | 1.9795 | 2.0325 | 2.087 |  | 100% | 95.94% | 0% | 80604 | [7 empty] | 1.37 | 0.11001
[6 empty] | 43739.716 |  |  |  |  | Committed new connections: | [14 empty] | 1.48 | 1.4199 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.14051 |  | 2019-10-01 17:11 | 2019-08-28 16:01 | 0
| 75 | MILL RD MONTROSE | 33/11 | 2 x 10 |  | 2020-02-24 12:44 | 6.5772 | 1 | 0 | 0 | 6.5772 | 6.5773 | 6.5775 | 6.5776 | 6.5777 | 6.5778 | 6.5779 | 6.5781 | 6.5782 | 6.5783 | 6.5784 | 6.5785 | 6.5787 | 6.5788 |  | 86.59% | 76.34% | 0% | 80613 | [7 empty] | 6.6595 | -0.082291
[6 empty] | 43885.5306 |  |  |  |  | Committed new connections: | [14 empty] | 5.6949 | 5.0211 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 16:51 | 2019-06-13 11:33 | 0
| 74 | MONTROSE NORTH | 33/11 | 2 x 15 |  | 2019-12-16 17:01 | 8.318 | 1 | 0 | 0 | 8.318 | 8.3182 | 8.3183 | 8.3185 | 8.3186 | 8.3188 | 8.319 | 8.3191 | 8.3193 | 8.3194 | 8.3196 | 8.3197 | 8.3199 | 8.32 |  | 89% | 71.4% | 0% | 80623 | [7 empty] | 8.0317 | 0.28633
[6 empty] | 43815.709 |  |  |  |  | Committed new connections: | [14 empty] | 7.4027 | 5.9389 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 17:18 | 2019-08-20 17:25 | 0
| 952 | ST CYRUS | 33/11 | 1 x 6 & 1 x 8 |  | 2019-12-25 15:00 | 1.302 | 1 | M | M | 1.302 | 1.3197 | 1.3377 | 1.3559 | 1.3743 | 1.393 | 1.412 | 1.4312 | 1.4507 | 1.4704 | 1.4904 | 1.5107 | 1.5312 | 1.5521 |  | 0% | 0% | 12.52% | 80629 | [7 empty] | 2.14 | -0.83798
[6 empty] | 43824.625 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 0.16303 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 3.4724 |  |  |  | 2019-08-25 03:00
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
BROADFORD | 627 |  | 132/33 | 1 x 30 |  | 2019-12-01 13:37 | 13.4588 | 1 |  | Diverse | 13.4588 | 13.4862 | 13.5144 | 13.5434 | 13.5731 | 13.6035 | 13.6348 | 13.6668 | 13.6997 | 13.7335 | 13.7681 | 13.8037 | 13.8402 | 13.8776 | Diversity/Losses: 0.997 | 85.39% | 75.62% | 21.43% | 11230 | [7 empty] | 12.2 | 1.2588
[6 empty] | 43800.5674 |  |  |  | Aggregate | 13.422 | 13.4494 | 13.4775 | 13.5063 | 13.5359 | 13.5663 | 13.5975 | 13.6295 | 13.6623 | 13.6959 | 13.7305 | 13.7659 | 13.8023 | 13.8396 |  | 11.492 | 10.1773 | 2.8843 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 0 |  | 2019-10-21 20:04 | 2019-08-14 18:40 | 2019-08-28 04:22
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 13.1896 | 13.2165 | 13.2442 | 13.2725 | 13.3016 | 13.3314 | 13.3621 | 13.3935 | 13.4257 | 13.4588 | 13.4928 | 13.5276 | 13.5634 | 13.6
| 624 | ACHINTEE | 33/11 | 1 x 1 |  | No PI | 0.084282 | 1 | M | M | 0.084282 | 0.085429 | 0.086591 | 0.087769 | 0.088963 | 0.090174 | 0.0914 | 0.092644 | 0.093904 | 0.095182 | 0.096477 | 0.097789 | 0.09912 | 0.10047 |  | 0% | 0% | 0% | 80716 | [7 empty] | 0.084282 | 0
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 637 | BROADFORD | 33/11 | 1 x 5 |  | 2020-03-16 15:04 | 1.638 | 1 | 0 | 0 | 1.638 | 1.638 | 1.6381 | 1.6381 | 1.6381 | 1.6381 | 1.6382 | 1.6382 | 1.6382 | 1.6383 | 1.6383 | 1.6383 | 1.6384 | 1.6384 |  | 94.52% | 75.24% | 0% | 80701 | [7 empty] | 1.59 | 0.048
[6 empty] | 43906.6278 |  |  |  |  | Committed new connections: | [14 empty] | 1.5483 | 1.2324 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 13:55 | 2019-06-06 18:58 | 0
| 629 | DRYNOCH | 33/11 | 1 x 2.5 |  | 2019-11-30 16:31 | 1.3437 | 1 | 0 | 0 | 1.3437 | 1.3437 | 1.3438 | 1.3438 | 1.3438 | 1.3438 | 1.3439 | 1.3439 | 1.3439 | 1.3439 | 1.344 | 1.344 | 1.344 | 1.344 |  | 94.64% | 77.11% | 0% | 80741 | [7 empty] | 1.24 | 0.10371
[6 empty] | 43799.6882 |  |  |  |  | Committed new connections: | [14 empty] | 1.2717 | 1.0362 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-11 08:06 | 2019-08-11 20:25 | 0
| 633 | KISHORNHILL | 33/11 | 1 x 2 |  | 2019-12-01 03:32 | 1.3152 | 1 | 0 | 0 | 1.3152 | 1.3153 | 1.3153 | 1.3153 | 1.3153 | 1.3153 | 1.3154 | 1.3154 | 1.3154 | 1.3154 | 1.3155 | 1.3155 | 1.3155 | 1.3155 |  | 78.72% | 57.45% | 0% | 80709 | [7 empty] | 1.28 | 0.035228
[6 empty] | 43800.1472 |  |  |  |  | Committed new connections: | [14 empty] | 1.0354 | 0.75556 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-21 12:04 | 2019-06-17 15:04 | 0
| 634 | KYLE | 33/11 | 2 x 5 |  | 2020-02-26 19:35 | 2.4963 | 1 | 0 | 0 | 2.4963 | 2.4964 | 2.4964 | 2.4965 | 2.4965 | 2.4965 | 2.4966 | 2.4966 | 2.4967 | 2.4967 | 2.4968 | 2.4968 | 2.4969 | 2.4969 |  | 87.2% | 76.8% | 0% | 80724 | 80725 | [6 empty] | 2.36 | 0.13631
[6 empty] | 43887.816 |  |  |  |  | Committed new connections: | [14 empty] | 2.1768 | 1.9172 | 0 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 18:54 | 2019-06-06 18:19 | 0
| 623 | LOWER OLLACH | 33/11 | 1 x 1 |  | 2020-02-12 19:04 | 0.97187 | 1 | H | H | 0.97187 | 0.99791 | 1.0246 | 1.0521 | 1.0803 | 1.1092 | 1.1389 | 1.1694 | 1.2008 | 1.2329 | 1.2659 | 1.2999 | 1.3347 | 1.3704 |  | 90.6% | 78.54% | 0% | 80740 | [7 empty] | 0.92779 | 0.04408
[6 empty] | 43873.7944 |  |  |  |  | Committed new connections: | [14 empty] | 0.88048 | 0.76327 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-28 20:07 | 2019-06-05 20:43 | 0
| 636 | NOSTIE BRIDGE | 33/11 | 1 x 4 |  | 2019-12-01 13:42 | 2.17 | 1 | 0 | 0 | 2.17 | 2.1701 | 2.1701 | 2.1702 | 2.1702 | 2.1702 | 2.1703 | 2.1703 | 2.1704 | 2.1704 | 2.1704 | 2.1705 | 2.1705 | 2.1706 |  | 88.3% | 42.02% | 0% | 80719 | [7 empty] | 2.1461 | 0.023951
[6 empty] | 43800.5708 |  |  |  |  | Committed new connections: | [14 empty] | 1.9162 | 0.91174 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-05-09 07:24 | 2019-07-01 19:06 | 0
| 641 | SHIELDAIG | 33/11 | 1 x 1 |  | 2020-02-17 12:59 | 0.72998 | 1 | 0 | 0 | 0.72998 | 0.72999 | 0.73 | 0.73002 | 0.73003 | 0.73004 | 0.73006 | 0.73007 | 0.73008 | 0.7301 | 0.73011 | 0.73012 | 0.73014 | 0.73015 |  | 99.52% | 96.18% | 0% | 80713 | [7 empty] | 0.73 | -2.301e-05
[6 empty] | 43878.541 |  |  |  |  | Committed new connections: | [14 empty] | 0.72649 | 0.70206 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-09-02 02:29 | 2019-08-31 02:40 | 0
| 639 | SKULAMUS | 33/11 | 1 x 4 |  | 2020-03-12 18:33 | 2.6725 | 1 | 0 | 0 | 2.6725 | 2.6726 | 2.6726 | 2.6727 | 2.6727 | 2.6728 | 2.6728 | 2.6729 | 2.6729 | 2.673 | 2.673 | 2.6731 | 2.6731 | 2.6732 |  | 92.71% | 69% | 0% | 80733 | [7 empty] | 2.6 | 0.072543
[6 empty] | 43902.7729 |  |  |  |  | Committed new connections: | [14 empty] | 2.4776 | 1.8439 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 20:04 | 2019-06-05 20:05 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
BRORA | 510 |  | 132/33 | 1 x 45 |  | 2019-12-18 07:15 | 8.4503 | 1 |  | Diverse | 8.4503 | 8.4505 | 8.4506 | 8.4508 | 8.4509 | 8.4511 | 8.4512 | 8.4514 | 8.4515 | 8.4517 | 8.4519 | 8.452 | 8.4522 | 8.4523 | Diversity/Losses: 1.102 | 94.5% | 67.69% | 20.38% | 11330 | [7 empty] | 8.8 | -0.34968
[6 empty] | 43817.3021 |  |  |  | Aggregate | 9.3106 | 9.3108 | 9.3109 | 9.3111 | 9.3113 | 9.3114 | 9.3116 | 9.3118 | 9.3119 | 9.3121 | 9.3123 | 9.3125 | 9.3126 | 9.3128 |  | 7.9859 | 5.7204 | 1.7218 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 0 |  | 2019-04-03 07:17 | 2019-06-13 12:05 | 2019-08-19 02:30
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 8.2813 | 8.2815 | 8.2816 | 8.2818 | 8.2819 | 8.2821 | 8.2822 | 8.2824 | 8.2825 | 8.2827 | 8.2828 | 8.283 | 8.2831 | 8.2833
| 550 | BRORA | 33/11 | 2 x 5 |  | 2019-12-25 11:32 | 2.1892 | 1 | 0 | 0 | 2.1892 | 2.1893 | 2.1893 | 2.1893 | 2.1894 | 2.1894 | 2.1895 | 2.1895 | 2.1895 | 2.1896 | 2.1896 | 2.1897 | 2.1897 | 2.1897 |  | 88.62% | 61.77% | 0% | 80805 | [7 empty] | 2.24 | -0.05078
[6 empty] | 43824.4806 |  |  |  |  | Committed new connections: | [14 empty] | 1.94 | 1.3522 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 07:22 | 2019-06-26 08:32 | 0
| 557 | DORNOCH | 33/11 | 1 x 8 |  | 2019-12-18 07:25 | 4.0885 | 1 | 0 | 0 | 4.0885 | 4.0886 | 4.0887 | 4.0887 | 4.0888 | 4.0889 | 4.089 | 4.089 | 4.0891 | 4.0892 | 4.0893 | 4.0893 | 4.0894 | 4.0895 |  | 92.55% | 68.8% | 0% | 80813 | [7 empty] | 3.77 | 0.31852
[6 empty] | 43817.309 |  |  |  |  | Committed new connections: | [14 empty] | 3.784 | 2.8131 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 12:40 | 2019-06-06 12:11 | 0
| 525 | GOLSPIE | 33/11 | 1 x 4 |  | 2020-01-13 11:36 | 2.0152 | 1 | 0 | 0 | 2.0152 | 2.0152 | 2.0153 | 2.0153 | 2.0153 | 2.0154 | 2.0154 | 2.0155 | 2.0155 | 2.0155 | 2.0156 | 2.0156 | 2.0156 | 2.0157 |  | 91.42% | 65.69% | 0% | 80810 | [7 empty] | 2.04 | -0.0248
[6 empty] | 43843.4833 |  |  |  |  | Committed new connections: | [14 empty] | 1.8423 | 1.3237 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 12:07 | 2019-06-13 12:29 | 0
| 560 | HELMSDALE | 33/11 | 1 x 4 |  | 2020-01-19 11:17 | 1.0176 | 1 | 0 | 0 | 1.0176 | 1.0177 | 1.0177 | 1.0177 | 1.0177 | 1.0177 | 1.0177 | 1.0178 | 1.0178 | 1.0178 | 1.0178 | 1.0178 | 1.0179 | 1.0179 |  | 86.61% | 71.65% | 0% | 80802 | [7 empty] | 1.02 | -0.0023617
[6 empty] | 43849.4701 |  |  |  |  | Committed new connections: | [14 empty] | 0.88142 | 0.72917 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-07 12:43 | 2019-07-18 19:47 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
BURGHMUIR | 245 |  | 132/33 | 2 x 90 |  | 2019-11-19 16:58 | 45.2098 | 1 |  | Diverse | 45.2098 | 45.2468 | 45.284 | 45.3214 | 45.3589 | 45.3967 | 45.4347 | 45.4729 | 45.5113 | 45.5499 | 45.5888 | 45.6278 | 45.6671 | 45.7065 | Diversity/Losses: 0.939 | 86.43% | 70.21% | 26.77% | 11430 | [7 empty] | 45 | 0.20982
[6 empty] | 43788.7069 |  |  |  | Aggregate | 42.4388 | 42.4735 | 42.5084 | 42.5435 | 42.5788 | 42.6143 | 42.6499 | 42.6858 | 42.7218 | 42.7581 | 42.7945 | 42.8312 | 42.868 | 42.9051 |  | 39.0764 | 31.7439 | 12.1038 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 0 |  | 2019-10-29 17:27 | 2019-06-05 12:34 | 2019-07-07 05:27
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 44.3056 | 44.3419 | 44.3783 | 44.4149 | 44.4518 | 44.4888 | 44.526 | 44.5635 | 44.6011 | 44.6389 | 44.677 | 44.7153 | 44.7537 | 44.7924
| 246 | BURGHMUIR | 33/11 | 2 x 12.5 |  | 2020-01-29 17:28 | 9.2454 | 1 | 0 | 0 | 9.2454 | 9.2456 | 9.2458 | 9.246 | 9.2461 | 9.2463 | 9.2465 | 9.2466 | 9.2468 | 9.247 | 9.2471 | 9.2473 | 9.2475 | 9.2476 |  | 93.48% | 70.29% | 0% | 80917 | [7 empty] | 8.92 | 0.32544
[6 empty] | 43859.7278 |  |  |  |  | Committed new connections: | [14 empty] | 8.6425 | 6.4986 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 17:19 | 2019-06-06 17:11 | 0
| 249 | GOODLYBURN | 33/11 | 2 x 12.5 |  | 2020-01-23 12:59 | 9.344 | 1 | 0 | 0 | 9.344 | 9.3442 | 9.3443 | 9.3445 | 9.3447 | 9.3449 | 9.345 | 9.3452 | 9.3454 | 9.3455 | 9.3457 | 9.3459 | 9.346 | 9.3462 |  | 84.59% | 69.52% | 0% | 80911 | [7 empty] | 8.89 | 0.454
[6 empty] | 43853.541 |  |  |  |  | Committed new connections: | [14 empty] | 7.904 | 6.496 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-29 17:53 | 2019-08-26 08:02 | 0
| 240 | INVERALMOND | 33/11 | 1 x 10 |  | 2019-11-25 13:48 | 6.144 | 1 | #N/A | L | 6.144 | 6.178 | 6.2123 | 6.2467 | 6.2813 | 6.3161 | 6.3511 | 6.3863 | 6.4217 | 6.4573 | 6.4931 | 6.5291 | 6.5653 | 6.6017 |  | 0% | 0% | 0% | 80908 | [7 empty] | 6.9188 | -0.77484
[6 empty] | 43794.575 |  |  |  |  | Committed new connections: | [14 empty] | #VALUE! | No Data | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | #VALUE! | Missing Data | 0
| 270 | REDGORTON | 33/11 | 2 x 15 |  | 2019-11-20 17:28 | 4.651 | 1 | 0 | 0 | 4.651 | 4.6511 | 4.6512 | 4.6513 | 4.6514 | 4.6514 | 4.6515 | 4.6516 | 4.6517 | 4.6518 | 4.6519 | 4.6519 | 4.652 | 4.6521 |  | 74.61% | 53.67% | 0% | 80904 | [7 empty] | 4.6119 | 0.039078
[6 empty] | 43789.7278 |  |  |  |  | Committed new connections: | [14 empty] | 3.4702 | 2.4963 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-30 17:27 | 2019-06-25 16:54 | 0
| 248 | THIMBLEROW | 33/11 | 2 x 21 |  | 2019-11-19 12:24 | 13.0543 | 1 | 0 | 0 | 13.0543 | 13.0546 | 13.0548 | 13.0551 | 13.0553 | 13.0555 | 13.0558 | 13.056 | 13.0563 | 13.0565 | 13.0567 | 13.057 | 13.0572 | 13.0574 |  | 87.71% | 72.66% | 0% | 80915 | [7 empty] | 16.42 | -3.3657
[6 empty] | 43788.5167 |  |  |  |  | Committed new connections: | [14 empty] | 11.45 | 9.4853 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 12:16 | 2019-06-05 12:30 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
CARRADALE | 302 |  | 132/33 | 2 x 60 |  | 2020-02-13 18:45 | 16.4678 | 1 |  | Diverse | 16.4678 | 16.5817 | 16.6973 | 16.8144 | 16.9331 | 17.0534 | 17.1753 | 17.2989 | 17.4242 | 17.5511 | 17.6798 | 17.8103 | 17.9425 | 18.0765 | Diversity/Losses: 1.218 | 54.95% | 44.92% | -371.7% | 11530 | [7 empty] | 23.7 | -7.2322
|  |  |  | 2 x 90 |  | 43874.7812 |  |  |  | Aggregate | 20.0568 | 20.1956 | 20.3363 | 20.4789 | 20.6235 | 20.77 | 20.9185 | 21.0691 | 21.2216 | 21.3763 | 21.533 | 21.6919 | 21.853 | 22.0162 |  | 9.0498 | 7.398 | -61.2073 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 0.3252 |  | 2019-05-11 03:04 | 2019-06-06 04:06 | 2020-03-01 15:57
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 16.1384 | 16.2501 | 16.3633 | 16.4781 | 16.5944 | 16.7123 | 16.8318 | 16.9529 | 17.0757 | 17.2001 | 17.3262 | 17.4541 | 17.5837 | 17.715
| 372 | BALLIEKINE | 33/11 | 1 x 1 |  | 2019-04-14 03:09 | 0.59831 | 1 | 0 | 0 | 0.59831 | 0.59832 | 0.59833 | 0.59834 | 0.59835 | 0.59837 | 0.59838 | 0.59839 | 0.5984 | 0.59841 | 0.59842 | 0.59843 | 0.59844 | 0.59845 |  | 100% | 85.38% | 0% | 81119 | [7 empty] | 0.64 | -0.041689
[6 empty] | 43569.1312 |  |  |  |  | Committed new connections: | [14 empty] | 0.59831 | 0.51084 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-14 03:09 | 2019-06-04 09:24 | 0
| 318 | BALLURE | 33/11 | 1 x 2.5 |  | 2020-02-24 13:30 | 1.3194 | 1 | 0 | 0 | 1.3194 | 1.3194 | 1.3195 | 1.3195 | 1.3195 | 1.3195 | 1.3196 | 1.3196 | 1.3196 | 1.3196 | 1.3196 | 1.3197 | 1.3197 | 1.3197 |  | 0% | 0% | 15.29% | 81137 | [7 empty] | 1.18 | 0.13941
[6 empty] | 43885.5625 |  |  |  |  | Committed new connections: | [14 empty] | Manual Calculation | Manual Calculation | 0.2018 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.3252 |  |  |  | 2019-07-26 01:30
| 370 | BRODICK | 33/11 | 2 x 4/8 |  | 2019-04-15 08:10 | 5.0759 | 1 | 0 | 0 | 5.0759 | 5.076 | 5.0761 | 5.0762 | 5.0763 | 5.0764 | 5.0765 | 5.0766 | 5.0767 | 5.0768 | 5.0769 | 5.077 | 5.0771 | 5.0771 |  | 100% | 66.23% | 0% | 81106 | [7 empty] | 5.65 | -0.57406
[6 empty] | 43570.3403 |  |  |  |  | Committed new connections: | [14 empty] | 5.0759 | 3.3618 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-15 08:10 | 2019-06-12 17:19 | 0
| 312 | CAMPBELTOWN | 33/11 | 2 x 15 |  | 2019-12-13 18:17 | 6.7971 | 1 | M | M | 6.7971 | 6.8896 | 6.9833 | 7.0783 | 7.1746 | 7.2722 | 7.3712 | 7.4714 | 7.5731 | 7.6761 | 7.7806 | 7.8864 | 7.9937 | 8.1025 |  | 87.05% | 73.62% | 0% | 81127 | [7 empty] | 8.82 | -2.0229
[6 empty] | 43812.7618 |  |  |  |  | Committed new connections: | [14 empty] | 5.9169 | 5.0041 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-04 09:49 | 2019-06-17 13:43 | 0
| 338 | CLAONAIG | 33/11 | 1 x 0.3 |  | No PI | 0.20228 | 1 | M | M | 0.20228 | 0.20503 | 0.20782 | 0.21065 | 0.21351 | 0.21642 | 0.21936 | 0.22235 | 0.22537 | 0.22844 | 0.23154 | 0.23469 | 0.23789 | 0.24112 |  | 0% | 0% | 0% | 81134 | [7 empty] | 0.20509 | -0.0028094
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 336 | DIPPEN | 33/11 | 1 x 1 |  | No PI | 0.94958 | 1 | M | M | 0.94958 | 0.9625 | 0.97559 | 0.98887 | 1.0023 | 1.016 | 1.0298 | 1.0438 | 1.058 | 1.0724 | 1.087 | 1.1018 | 1.1167 | 1.1319 |  | 0% | 0% | 0% | 81123 | [7 empty] | 0.94958 | 0
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 373 | MACHRIE | 33/11 | 1 x 2.5 |  | 2019-12-31 19:00 | 1.9066 | 1 | 0 | 0 | 1.9066 | 1.9066 | 1.9067 | 1.9067 | 1.9067 | 1.9068 | 1.9068 | 1.9068 | 1.9069 | 1.9069 | 1.9069 | 1.907 | 1.907 | 1.907 |  | 83.78% | 59.48% | 0% | 81114 | [7 empty] | 1.95 | -0.043406
[6 empty] | 43830.7917 |  |  |  |  | Committed new connections: | [14 empty] | 1.5974 | 1.134 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-01 18:38 | 2019-06-03 18:35 | 0
| 310 | TARBERT LOCH FYNE | 33/11 | 1 x 2.5 |  | 2019-12-08 14:00 | 2.3566 | 1 | 0 | 0 | 2.3566 | 2.3566 | 2.3566 | 2.3567 | 2.3567 | 2.3568 | 2.3568 | 2.3569 | 2.3569 | 2.3569 | 2.357 | 2.357 | 2.3571 | 2.3571 |  | 91.51% | 51.38% | 0% | 81140 | 84900 | [6 empty] | 2.53 | -0.17345
[6 empty] | 43807.5833 |  |  |  |  | Committed new connections: | [14 empty] | 2.1565 | 1.2109 | 0 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0.95655 |  | 2019-04-15 13:21 | 2019-07-05 21:25 | 0
| 349 | WESTPARK FERGUS | 33/11 | 1 x 8 |  | 2019-05-31 11:30 | 0.96601 | 1 | 0 | 0 | 0.96601 | 0.96602 | 0.96604 | 0.96606 | 0.96608 | 0.9661 | 0.96611 | 0.96613 | 0.96615 | 0.96617 | 0.96618 | 0.9662 | 0.96622 | 0.96624 |  | 100% | 94.04% | 0% | 81131 | [7 empty] | 0.73 | 0.23601
[6 empty] | 43616.4792 |  |  |  |  | Committed new connections: | [14 empty] | 0.96601 | 0.90844 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-05-31 11:30 | 2019-06-04 00:56 | 0
| 371 | WHITING BAY | 33/11 | 1 x 8 |  | 2020-02-17 18:36 | 2.2416 | 1 | M | M | 2.2416 | 2.2721 | 2.303 | 2.3343 | 2.3661 | 2.3983 | 2.4309 | 2.464 | 2.4975 | 2.5315 | 2.5659 | 2.6008 | 2.6362 | 2.6721 |  | 96.76% | 61.46% | 0% | 81111 | [7 empty] | 2.58 | -0.33843
[6 empty] | 43878.775 |  |  |  |  | Committed new connections: | [14 empty] | 2.169 | 1.3776 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-03 19:50 | 2019-06-05 08:12 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
CASSLEY | 512 |  | 132/33 | 1 x 30 |  | 2019-12-06 11:19 | 2.3593 | 1 |  | Diverse | 2.3593 | 2.3594 | 2.3594 | 2.3595 | 2.3595 | 2.3596 | 2.3596 | 2.3596 | 2.3597 | 2.3597 | 2.3598 | 2.3598 | 2.3599 | 2.3599 | Diversity/Losses: 0.789 | 92.07% | 91.02% | -374.9% | 11830 | [7 empty] | 1.9 | 0.45934
[6 empty] | 43805.4715 |  |  |  | Aggregate | 1.8607 | 1.8608 | 1.8608 | 1.8608 | 1.8609 | 1.8609 | 1.8609 | 1.861 | 1.861 | 1.861 | 1.8611 | 1.8611 | 1.8611 | 1.8612 |  | 2.1722 | 2.1476 | -8.8457 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 11.805 |  | 2019-10-12 12:10 | 2019-06-23 11:57 | 2019-11-28 16:44
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 2.3122 | 2.3122 | 2.3122 | 2.3123 | 2.3123 | 2.3124 | 2.3124 | 2.3125 | 2.3125 | 2.3125 | 2.3126 | 2.3126 | 2.3127 | 2.3127
| 563 | OVERSCAIG | 33/11 | 1 x 0.15 |  | No PI | 0.030903 | 1 | 0 | 0 | 0.030903 | 0.030904 | 0.030905 | 0.030905 | 0.030906 | 0.030906 | 0.030907 | 0.030907 | 0.030908 | 0.030909 | 0.030909 | 0.03091 | 0.03091 | 0.030911 |  | 0% | 0% | 0% | 81202 | [7 empty] | 0.030903 | 0
[6 empty] | No PI |  |  |  |  | Committed new connections: | [14 empty] | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak: |  | 0 | 0 | 0
| 544 | RHICONICH | 33/11 | 1 x 3.9 |  | 2020-03-07 02:44 | 1.8298 | 1 | 0 | 0 | 1.8298 | 1.8299 | 1.8299 | 1.8299 | 1.83 | 1.83 | 1.83 | 1.8301 | 1.8301 | 1.8301 | 1.8302 | 1.8302 | 1.8302 | 1.8303 |  | 90.31% | 78.03% | 0% | 81218 | [7 empty] | 1.9466 | -0.11675
[6 empty] | 43897.1139 |  |  |  |  | Committed new connections: | [14 empty] | 1.6526 | 1.4279 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-08 20:23 | 2019-06-12 18:34 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
CHARLESTON | 1 |  | 132/33 | 2 x 90 |  | 2019-12-02 11:49 | 21.6145 | 1 |  | Diverse | 21.6145 | 21.8153 | 22.0215 | 22.2332 | 22.4505 | 22.6737 | 22.9029 | 23.1381 | 23.3797 | 23.6277 | 23.8824 | 24.1439 | 24.4124 | 24.6881 | Diversity/Losses: 1.3 | 92.89% | 96.78% | 33.83% | 12030 | [7 empty] | 23.8 | -2.1855
[6 empty] | 43801.4924 |  |  |  | Aggregate | 28.1078 | 28.3689 | 28.6371 | 28.9123 | 29.195 | 29.4852 | 29.7832 | 30.0892 | 30.4033 | 30.7259 | 31.057 | 31.3971 | 31.7462 | 32.1047 |  | 20.0786 | 20.9195 | 7.3114 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [10 empty] | Generation at time of peak: 4.0614: Generation at time of BSP peak:; 0.026979 4.0615: 0 |  | 2019-09-12 11:39 | 2019-07-25 10:56 | 2019-07-07 05:09
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 21.1822 | 21.379 | 21.5811 | 21.7885 | 22.0015 | 22.2202 | 22.4448 | 22.6754 | 22.9121 | 23.1552 | 23.4048 | 23.661 | 23.9241 | 24.1943
| 2 | CHARLESTON | 33/11 | 2 x 15 |  | 2019-07-24 15:56 | 9.7357 | 1 | H | H | 9.7357 | 9.9965 | 10.2643 | 10.5393 | 10.8216 | 11.1115 | 11.4091 | 11.7148 | 12.0286 | 12.3508 | 12.6816 | 13.0213 | 13.3701 | 13.7283 |  | 92.32% | 100% | 0% | 81405 | [7 empty] | 9.43 | 0.30575
[6 empty] | 43670.6639 |  |  |  |  | Committed new connections: | [14 empty] | 8.9882 | 9.7357 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-09-03 12:26 | 2019-07-24 15:56 | 0
| 4 | GOURDIE | 33/11 | 1 x 6.3 |  | 2019-11-20 18:37 | 2.8044 | 1 | 0 | 0 | 2.8044 | 2.8045 | 2.8045 | 2.8046 | 2.8046 | 2.8047 | 2.8047 | 2.8048 | 2.8048 | 2.8049 | 2.8049 | 2.805 | 2.805 | 2.8051 |  | 95.18% | 69.3% | 0% | 81401 | [7 empty] | 2.57 | 0.2344
[6 empty] | 43789.7757 |  |  |  |  | Committed new connections: | [14 empty] | 2.6691 | 1.9434 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-10-28 18:35 | 2019-08-10 18:26 | 0
| 3 | MENZIESHILL | 33/11 | 2 x 21 |  | 2020-02-19 09:17 | 9.8185 | 1 | 0 | 0 | 9.8185 | 9.8187 | 9.8189 | 9.8191 | 9.8193 | 9.8194 | 9.8196 | 9.8198 | 9.82 | 9.8202 | 9.8203 | 9.8205 | 9.8207 | 9.8209 |  | 89.94% | 53.8% | 0% | 81410 | [7 empty] | 11.39 | -1.5715
[6 empty] | 43880.3868 |  |  |  |  | Committed new connections: | [14 empty] | 8.8306 | 5.2823 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-05-02 12:35 | 2019-06-12 17:17 | 0
| 6 | NINEWELLS | 33/11 | 2 x 15 |  | 2019-11-19 17:02 | 5.7491 | 1 | 0 | 0 | 5.7491 | 5.7492 | 5.7493 | 5.7494 | 5.7495 | 5.7496 | 5.7497 | 5.7498 | 5.75 | 5.7501 | 5.7502 | 5.7503 | 5.7504 | 5.7505 |  | 87.38% | 73.4% | 0% | 81420 | [7 empty] | 5.2096 | 0.53955
[6 empty] | 43788.7097 |  |  |  |  | Committed new connections: | [14 empty] | 5.0235 | 4.2197 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [11 empty] | Generation at time of peak: 4.0614: Generation at time of peak:; 0.026979 4.0615: 0 |  | 2019-04-04 09:40 | 2019-08-09 11:13 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
CLACHAN | 311 |  | 132/11 | 1 x 60 |  | 2020-02-08 19:18 | 53.2295 | 1 |  | Diverse | 53.2295 | 53.2305 | 53.2315 | 53.2324 | 53.2334 | 53.2344 | 53.2354 | 53.2363 | 53.2373 | 53.2383 | 53.2393 | 53.2402 | 53.2412 | 53.2422 | Diversity/Losses: 0.099 | 92.08% | 92.87% | -3.328% | 12151 | [7 empty] | 5.9 | 47.3295
[6 empty] | 43869.8042 |  |  |  | Aggregate | 5.2701 | 5.2702 | 5.2703 | 5.2704 | 5.2705 | 5.2706 | 5.2707 | 5.2708 | 5.2709 | 5.271 | 5.2711 | 5.2712 | 5.2713 | 5.2713 |  | 49.0133 | 49.4335 | -1.7717 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 5.2707: Generation at time of BSP peak:; 5.2708: 8.5274 |  | 2019-09-26 07:04 | 2019-08-19 02:52 | 2019-04-28 18:54
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 52.1649 | 52.1659 | 52.1668 | 52.1678 | 52.1688 | 52.1697 | 52.1707 | 52.1716 | 52.1726 | 52.1735 | 52.1745 | 52.1754 | 52.1764 | 52.1773
| 387 | BUTTERBRIDGE | 33/11 | 1 x 0.1 |  | No PI | 0.0084282 | 1 | 0 | 0 | 0.0084282 | 0.0084284 | 0.0084285 | 0.0084287 | 0.0084288 | 0.008429 | 0.0084291 | 0.0084293 | 0.0084295 | 0.0084296 | 0.0084298 | 0.0084299 | 0.0084301 | 0.0084302 |  | 0% | 0% | 0% | 81509 | [7 empty] | 0.0084282 | 0
[6 empty] | No PI |  |  |  |  | 5.2701: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 5.2707: Generation at time of peak: |  | 0 | 0 | 0
| 388 | DOUGLAS PIER | 33/11 | 1 x 2.5 |  | 2019-04-06 18:48 | 1.0425 | 1 | 0 | 0 | 1.0425 | 1.0425 | 1.0425 | 1.0425 | 1.0425 | 1.0426 | 1.0426 | 1.0426 | 1.0426 | 1.0426 | 1.0427 | 1.0427 | 1.0427 | 1.0427 |  | 100% | 55.25% | 0% | 81515 | [7 empty] | 1.13 | -0.087532
[6 empty] | 43561.7833 |  |  |  |  | 5.2701: Committed new connections: |  | 1.0425 | 0.57597 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 5.2707: Generation at time of peak:; 5.2708: 0 |  | 2019-04-06 18:48 | 2019-07-05 13:19 | 0
| 321 | INVERARAY | 33/11 | 1 x 2.5 |  | 2019-04-06 13:18 | 0.896 | 1 | 0 | 0 | 0.896 | 0.89602 | 0.89603 | 0.89605 | 0.89607 | 0.89608 | 0.8961 | 0.89611 | 0.89613 | 0.89615 | 0.89616 | 0.89618 | 0.8962 | 0.89621 |  | 100% | 74.11% | 0% | 81521 | [7 empty] | 0.89 | 0.006
[6 empty] | 43561.5542 |  |  |  |  | 5.2701: Committed new connections: |  | 0.896 | 0.664 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 5.2707: Generation at time of peak:; 5.2708: 0 |  | 2019-04-06 13:18 | 2019-06-01 13:46 | 0
| 369 | LOCHGOILHEAD | 33/11 | 1 x 2.5 |  | 2020-01-16 08:49 | 2.4153 | 1 | 0 | 0 | 2.4153 | 2.4153 | 2.4154 | 2.4154 | 2.4154 | 2.4155 | 2.4155 | 2.4156 | 2.4156 | 2.4157 | 2.4157 | 2.4158 | 2.4158 | 2.4158 |  | 71.66% | 75.49% | 0% | 81513 | [7 empty] | 0.41 | 2.0053
[6 empty] | 43846.3674 |  |  |  |  | 5.2701: Committed new connections: |  | 1.7308 | 1.8232 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 5.2707: Generation at time of peak:; 5.2708: 1.2745 |  | 2019-10-17 23:58 | 2019-08-20 00:06 | 0
| 382 | STRACHUR | 33/11 | 1 x 1 |  | 2019-12-01 03:33 | 0.90794 | 1 | 0 | 0 | 0.90794 | 0.90795 | 0.90797 | 0.90798 | 0.908 | 0.90802 | 0.90803 | 0.90805 | 0.90807 | 0.90808 | 0.9081 | 0.90812 | 0.90813 | 0.90815 |  | 79.48% | 47.5% | 0% | 81518 | [7 empty] | 0.84 | 0.067935
[6 empty] | 43800.1479 |  |  |  |  | 5.2701: Committed new connections: |  | 0.7216 | 0.43129 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 5.2707: Generation at time of peak:; 5.2708: 0 |  | 2019-10-30 03:34 | 2019-06-05 13:33 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
CLAYHILLS | 823 |  | 132/33 | 2 x 60 |  | 2019-12-17 14:17 | 31.7735 | 1 |  | Diverse | 31.7735 | 31.7741 | 31.7747 | 31.7752 | 31.7758 | 31.7764 | 31.777 | 31.7776 | 31.7781 | 31.7787 | 31.7793 | 31.7799 | 31.7805 | 31.781 | Diversity/Losses: 1.047 | 93.91% | 78.95% | 26.88% | 12230 | [7 empty] | 32.7 | -0.9265
[6 empty] | 43816.5951 |  |  |  | Aggregate | 33.2538 | 33.2544 | 33.255 | 33.2556 | 33.2562 | 33.2568 | 33.2574 | 33.258 | 33.2586 | 33.2592 | 33.2598 | 33.2604 | 33.261 | 33.2617 |  | 29.8375 | 25.0855 | 8.5415 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 5.2707: Generation at time of BSP peak:; 5.2708: 0 |  | 2019-04-03 11:33 | 2019-07-24 15:02 | 2019-07-06 04:39
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 31.138 | 31.1386 | 31.1392 | 31.1397 | 31.1403 | 31.1409 | 31.1414 | 31.142 | 31.1426 | 31.1431 | 31.1437 | 31.1443 | 31.1449 | 31.1454
| 808 | BALNAGASK | 33/11 | 1 x 23 |  | 2019-12-13 14:23 | 4.6516 | 1 | 0 | 0 | 4.6516 | 4.6517 | 4.6518 | 4.6519 | 4.6519 | 4.652 | 4.6521 | 4.6522 | 4.6523 | 4.6524 | 4.6524 | 4.6525 | 4.6526 | 4.6527 |  | 0% | 0% | 0% | 81607 | [7 empty] | 4.48 | 0.1716
[6 empty] | 43812.5993 |  |  |  |  | 5.2701: Committed new connections: |  | #VALUE! | No Data | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 5.2707: Generation at time of peak:; 5.2708: 0 |  | #VALUE! | Missing Data | 0
| 826 | CLAYHILLS | 33/11 | 2 x 24 |  | 2019-11-19 16:54 | 14.5012 | 1 | 0 | 0 | 14.5012 | 14.5014 | 14.5017 | 14.502 | 14.5022 | 14.5025 | 14.5028 | 14.503 | 14.5033 | 14.5035 | 14.5038 | 14.5041 | 14.5043 | 14.5046 |  | 89.84% | 79.06% | 0% | 81604 | [7 empty] | 14.79 | -0.28884
[6 empty] | 43788.7042 |  |  |  |  | 5.2701: Committed new connections: |  | 13.0276 | 11.4647 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 5.2707: Generation at time of peak:; 5.2708: 0 |  | 2019-04-03 11:33 | 2019-06-13 15:07 | 0
| 827 | COMMERCE STREET | 33/11 | 2 x 23 |  | 2019-12-11 15:06 | 14.101 | 1 | 0 | 0 | 14.101 | 14.1013 | 14.1015 | 14.1018 | 14.102 | 14.1023 | 14.1025 | 14.1028 | 14.1031 | 14.1033 | 14.1036 | 14.1038 | 14.1041 | 14.1043 |  | 91.12% | 84.67% | 0% | 81602 | [7 empty] | 14.47 | -0.369
[6 empty] | 43810.6292 |  |  |  |  | 5.2701: Committed new connections: |  | 12.8485 | 11.9394 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 5.2707: Generation at time of peak:; 5.2708: 0 |  | 2019-04-03 11:34 | 2019-06-12 11:39 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
COUPAR ANGUS | 243 |  | 132/33 | 2 x 120 |  | 2020-01-19 22:46 | 43.8551 | 1 |  | Diverse | 43.8551 | 43.8559 | 43.8567 | 43.8575 | 43.8583 | 43.8591 | 43.8599 | 43.8607 | 43.8615 | 43.8623 | 43.8631 | 43.8639 | 43.8647 | 43.8655 | Diversity/Losses: 0.593 | 67.53% | 52.21% | -25.53% | 12430 | [7 empty] | 25 | 18.8551
[6 empty] | 43849.9486 |  |  |  | Aggregate | 25.9952 | 25.9956 | 25.9961 | 25.9966 | 25.9971 | 25.9975 | 25.998 | 25.9985 | 25.999 | 25.9994 | 25.9999 | 26.0004 | 26.0009 | 26.0013 |  | 29.6135 | 22.8971 | -11.197 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 5.2707: Generation at time of BSP peak:; 5.2708: 43.5647 |  | 2019-10-12 01:24 | 2019-06-19 16:41 | 2020-01-30 04:44
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 42.978 | 42.9788 | 42.9796 | 42.9803 | 42.9811 | 42.9819 | 42.9827 | 42.9835 | 42.9843 | 42.9851 | 42.9858 | 42.9866 | 42.9874 | 42.9882
| 258 | ALYTH | 33/11 | 2 x 5 |  | 2019-12-31 17:22 | 2.8774 | 1 | 0 | 0 | 2.8774 | 2.8775 | 2.8775 | 2.8776 | 2.8776 | 2.8777 | 2.8777 | 2.8778 | 2.8778 | 2.8779 | 2.8779 | 2.878 | 2.8781 | 2.8781 |  | 96.9% | 73.16% | 0% | 81712 | [7 empty] | 2.81 | 0.067422
[6 empty] | 43830.7236 |  |  |  |  | 42.978: Committed new connections: |  | 2.7883 | 2.1052 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-10-29 17:20 | 2019-06-13 17:06 | 0
| 257 | BLAIRGOWRIE | 33/11 | 2 x 23 |  | 2020-01-10 17:45 | 7.3016 | 1 | 0 | 0 | 7.3016 | 7.3018 | 7.3019 | 7.302 | 7.3022 | 7.3023 | 7.3024 | 7.3026 | 7.3027 | 7.3028 | 7.303 | 7.3031 | 7.3032 | 7.3034 |  | 0% | 0% | 0% | 81708 | [7 empty] | 8.71 | -1.4084
[6 empty] | 43840.7396 |  |  |  |  | 42.978: Committed new connections: |  | #VALUE! | No Data | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0.32283 |  | #VALUE! | Missing Data | 0
| 256 | CAPUTH | 33/11 | 2 x 15 |  | 2020-02-14 12:15 | 5.256 | 1 | 0 | 0 | 5.256 | 5.2561 | 5.2562 | 5.2563 | 5.2564 | 5.2565 | 5.2566 | 5.2567 | 5.2568 | 5.2569 | 5.257 | 5.2571 | 5.2572 | 5.2572 |  | 81.74% | 59.36% | 0% | 81720 | [7 empty] | 5.46 | -0.204
[6 empty] | 43875.5104 |  |  |  |  | 42.978: Committed new connections: |  | 4.296 | 3.12 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-03 11:58 | 2019-08-30 08:33 | 0
| 244 | COUPAR ANGUS | 33/11 | 1 x 8 & 1 x 15 |  | 2019-11-27 17:00 | 5.6955 | 1 | 0 | 0 | 5.6955 | 5.6956 | 5.6957 | 5.6959 | 5.696 | 5.6961 | 5.6962 | 5.6963 | 5.6964 | 5.6965 | 5.6966 | 5.6967 | 5.6968 | 5.6969 |  | 99.71% | 98.29% | 0% | 81726 | [7 empty] | 6.1 | -0.40446
[6 empty] | 43796.7083 |  |  |  |  | 42.978: Committed new connections: |  | 5.6789 | 5.5983 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0.01954 |  | 2019-10-30 17:03 | 2019-08-30 19:10 | 0
| 259 | DALRULZION | 33/11 | 2 x 2.5 |  | 2020-01-16 11:52 | 2.0385 | 1 | 0 | 0 | 2.0385 | 2.0385 | 2.0386 | 2.0386 | 2.0386 | 2.0387 | 2.0387 | 2.0388 | 2.0388 | 2.0388 | 2.0389 | 2.0389 | 2.0389 | 2.039 |  | 92.07% | 77.84% | 0% | 81716 | [7 empty] | 1.96 | 0.07849
[6 empty] | 43846.4944 |  |  |  |  | 42.978: Committed new connections: |  | 1.8769 | 1.5867 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-10-25 00:20 | 2019-08-30 08:21 | 0
| 90 | LEOCH | 33/11 | 1 x 6.3 |  | 2019-12-22 17:35 | 2.8261 | 1 | 0 | 0 | 2.8261 | 2.8261 | 2.8262 | 2.8262 | 2.8263 | 2.8263 | 2.8264 | 2.8264 | 2.8265 | 2.8265 | 2.8266 | 2.8266 | 2.8267 | 2.8268 |  | 77.95% | 59.9% | 0% | 81705 | [7 empty] | 2.7 | 0.12608
[6 empty] | 43821.7326 |  |  |  |  | 42.978: Committed new connections: |  | 2.2029 | 1.6929 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0.002081 |  | 2019-10-30 17:50 | 2019-06-12 09:33 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
CRAIGIEBUCKLER | 829 |  | 132/33 | 2 x 30 |  | 2019-12-11 19:09 | 23.3276 | 1 |  | Diverse | 23.3276 | 23.4677 | 23.6115 | 23.7591 | 23.9107 | 24.0664 | 24.2262 | 24.3903 | 24.5588 | 24.7317 | 24.9093 | 25.0917 | 25.2789 | 25.4711 | Diversity/Losses: 1.109 | 92.99% | 73.38% | 31.92% | 12530 | [7 empty] | 23.4 | -0.072375
[6 empty] | 43810.7979 |  |  |  | Aggregate | 25.875 | 26.0304 | 26.1899 | 26.3537 | 26.5218 | 26.6945 | 26.8717 | 27.0537 | 27.2406 | 27.4325 | 27.6295 | 27.8317 | 28.0394 | 28.2526 |  | 21.6915 | 17.1185 | 7.4472 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 42.9827: Generation at time of BSP peak:; 43.5647 42.9835: 1.1622 |  | 2019-10-29 17:51 | 2019-06-10 17:46 | 2019-07-14 05:34
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 22.8611 | 22.9983 | 23.1393 | 23.284 | 23.4325 | 23.5851 | 23.7417 | 23.9025 | 24.0676 | 24.2371 | 24.4111 | 24.5898 | 24.7733 | 24.9617
| 830 | CRAIGIEBUCKLER | 33/11 | 2 x 24 |  | 2019-11-11 18:00 | 5.786 | 1 | H | H | 5.786 | 5.941 | 6.1002 | 6.2636 | 6.4314 | 6.6036 | 6.7805 | 6.9622 | 7.1487 | 7.3402 | 7.5368 | 7.7387 | 7.946 | 8.1588 |  | 0% | 0% | 0% | 81800 | [7 empty] | 5.9905 | -0.20446
[6 empty] | 43780.75 |  |  |  |  | 42.978: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak: |  | 0 | 0 | 0
| 834 | CRAIGTON | 33/11 | 2 x10 |  | 2019-11-08 20:00 | 5.9035 | 1 | 0 | 0 | 5.9035 | 5.9036 | 5.9037 | 5.9038 | 5.9039 | 5.9041 | 5.9042 | 5.9043 | 5.9044 | 5.9045 | 5.9046 | 5.9047 | 5.9048 | 5.9049 |  | 0% | 0% | 0% | 81813 | [7 empty] | 5.7065 | 0.19697
[6 empty] | 43777.8333 |  |  |  |  | 42.978: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak: |  | 0 | 0 | 0
| 836 | CULTER | 33/11 | 2 x 24 |  | 2019-11-19 17:42 | 5.6948 | 1 | 0 | 0 | 5.6948 | 5.6949 | 5.695 | 5.6951 | 5.6952 | 5.6953 | 5.6954 | 5.6955 | 5.6957 | 5.6958 | 5.6959 | 5.696 | 5.6961 | 5.6962 |  | 89.51% | 67.57% | 0% | 81817 | 83814 | [6 empty] | 5.57 | 0.12482
[6 empty] | 43788.7375 |  |  |  |  | 42.978: Committed new connections: |  | 5.0972 | 3.8477 | 0 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0.00864 |  | 2019-10-28 18:09 | 2019-06-12 18:24 | 0
| 939 | RUTHRIESTON | 33/11 | 2 x 23 |  | 2019-11-11 18:00 | 8.4907 | 1 | 0 | 0 | 8.4907 | 8.4908 | 8.491 | 8.4911 | 8.4913 | 8.4915 | 8.4916 | 8.4918 | 8.4919 | 8.4921 | 8.4922 | 8.4924 | 8.4925 | 8.4927 |  | 0% | 0% | 0% | 81821 | [7 empty] | 9.9583 | -1.4677
[6 empty] | 43780.75 |  |  |  |  | 42.978: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak: |  | 0 | 0 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
DOUNREAY | 598 |  | 132/33 | 2 x 90 |  | 2020-02-11 11:03 | 8.3247 | 1 |  | Diverse | 8.3247 | 8.3508 | 8.3775 | 8.4048 | 8.4328 | 8.4614 | 8.4907 | 8.5206 | 8.5512 | 8.5826 | 8.6147 | 8.6475 | 8.6811 | 8.7155 | Diversity/Losses: 1.041 | 85.37% | 71.07% | -68.08% | 13130 | [7 empty] | 8 | 0.32469
[6 empty] | 43872.4604 |  |  |  | Aggregate | 8.6633 | 8.6905 | 8.7183 | 8.7468 | 8.7758 | 8.8056 | 8.8361 | 8.8672 | 8.8991 | 8.9317 | 8.9651 | 8.9993 | 9.0343 | 9.0701 |  | 7.107 | 5.9162 | -5.6674 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 42.9827: Generation at time of BSP peak:; 43.5647 42.9835: 20.0735 |  | 2019-10-30 19:01 | 2019-06-19 15:00 | 2019-09-03 23:19
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 8.1582 | 8.1838 | 8.21 | 8.2367 | 8.2641 | 8.2922 | 8.3208 | 8.3502 | 8.3802 | 8.4109 | 8.4424 | 8.4746 | 8.5075 | 8.5412
| 591 | BETTYHILL | 33/11 | 1 x 2.5 |  | 2019-04-03 20:27 | 0.72998 | 1 | 0 | 0 | 0.72998 | 0.72999 | 0.73 | 0.73002 | 0.73003 | 0.73004 | 0.73006 | 0.73007 | 0.73008 | 0.7301 | 0.73011 | 0.73012 | 0.73014 | 0.73015 |  | 100% | 90.54% | 0% | 81909 | [7 empty] | 0.76 | -0.030023
[6 empty] | 43558.8521 |  |  |  |  | 42.978: Committed new connections: |  | 0.72998 | 0.66089 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-03 20:27 | 2019-06-13 20:14 | 0
| 581 | COLDBACKIE | 33/11 | 1 x 2.5 |  | 2020-02-16 11:35 | 0.87653 | 1 | L | L | 0.87653 | 0.88139 | 0.88627 | 0.89118 | 0.89612 | 0.90109 | 0.90608 | 0.9111 | 0.91615 | 0.92123 | 0.92634 | 0.93147 | 0.93663 | 0.94182 |  | 89.33% | 67.36% | 0% | 81911 | [7 empty] | 0.8 | 0.076531
[6 empty] | 43877.4826 |  |  |  |  | 42.978: Committed new connections: |  | 0.78302 | 0.5904 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-03 07:27 | 2019-06-06 12:26 | 0
| UNKNOWN | DSRL | 33/11 | 2 x 15 |  | 2019-11-19 10:36 | 5.5276 | 1 | #N/A | 0 | 5.5276 | 5.5277 | 5.5278 | 5.5279 | 5.528 | 5.5281 | 5.5282 | 5.5283 | 5.5284 | 5.5285 | 5.5286 | 5.5287 | 5.5288 | 5.5289 |  | 90.94% | 80.37% | 0% | 13185 | [7 empty] | 5.02 | 0.50762
[6 empty] | 43788.4417 |  |  |  |  | 42.978: Committed new connections: |  | 5.0269 | 4.4426 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-10-31 09:41 | 2019-06-13 10:10 | 0
| 583 | FORSS | 33/11 | 1 x 2.5 |  | 2019-12-09 17:00 | 0.82854 | 1 | H | H | 0.82854 | 0.85074 | 0.87353 | 0.89693 | 0.92095 | 0.94562 | 0.97095 | 0.99696 | 1.0237 | 1.0511 | 1.0792 | 1.1082 | 1.1378 | 1.1683 |  | 0% | 0% | 12.25% | 81920 | [7 empty] | 0.78 | 0.048544
[6 empty] | 43808.7083 |  |  |  |  | 42.978: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.10148 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 2.8055 |  |  |  | 2019-05-15 15:30
| 590 | MELVICH | 33/11 | 1 x 1 |  | 2019-04-03 20:02 | 0.70067 | 1 | 0 | 0 | 0.70067 | 0.70068 | 0.70069 | 0.7007 | 0.70072 | 0.70073 | 0.70074 | 0.70076 | 0.70077 | 0.70078 | 0.70079 | 0.70081 | 0.70082 | 0.70083 |  | 0% | 0% | 0% | 81904 | [7 empty] | 0.73 | -0.029334
[6 empty] | 43558.8347 |  |  |  |  | 42.978: Committed new connections: |  | #VALUE! | Unreliable Data | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | #VALUE! | Missing Data | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
DUDHOPE | 31 |  | 132/33 | 2 x 60 |  | 2019-11-19 12:20 | 44.2394 | 1 |  | Diverse | 44.2394 | 44.3164 | 44.3938 | 44.4717 | 44.55 | 44.6287 | 44.7079 | 44.7875 | 44.8675 | 44.948 | 45.0289 | 45.1103 | 45.1921 | 45.2743 | Diversity/Losses: 1.071 | 89.54% | 75.65% | 28.77% | 13330 | [7 empty] | 44.7 | -0.46062
[6 empty] | 43788.5139 |  |  |  | Aggregate | 47.3667 | 47.4492 | 47.5321 | 47.6155 | 47.6993 | 47.7836 | 47.8684 | 47.9536 | 48.0393 | 48.1254 | 48.2121 | 48.2992 | 48.3868 | 48.4749 |  | 39.6104 | 33.4652 | 12.7261 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 42.9827: Generation at time of BSP peak:; 43.5647 42.9835: 0 |  | 2019-04-16 11:40 | 2019-06-17 14:34 | 2019-08-04 05:56
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 43.3546 | 43.4301 | 43.506 | 43.5823 | 43.659 | 43.7362 | 43.8137 | 43.8917 | 43.9702 | 44.049 | 44.1283 | 44.2081 | 44.2882 | 44.3689
| 32 | CONSTABLE STREET | 33/11 | 2 x 15 |  | 2020-01-29 13:33 | 14.7727 | 1 | L | L | 14.7727 | 14.8545 | 14.9369 | 15.0196 | 15.1029 | 15.1866 | 15.2707 | 15.3554 | 15.4405 | 15.526 | 15.6121 | 15.6986 | 15.7856 | 15.8731 |  | 79.94% | 71.9% | 0% | 82002 | [7 empty] | 13.25 | 1.5227
[6 empty] | 43859.5646 |  |  |  |  | 42.978: Committed new connections: |  | 11.8093 | 10.6216 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-04 11:48 | 2019-06-24 16:05 | 0
| 24 | OVERGATE | 33/11 | 3 x 21 |  | 2020-02-03 15:05 | 15.4003 | 1 | 0 | 0 | 15.4003 | 15.4006 | 15.4009 | 15.4012 | 15.4014 | 15.4017 | 15.402 | 15.4023 | 15.4026 | 15.4029 | 15.4031 | 15.4034 | 15.4037 | 15.404 |  | 88.65% | 83.12% | 0% | 82010 | [7 empty] | 15.7734 | -0.37305
[6 empty] | 43864.6285 |  |  |  |  | 42.978: Committed new connections: |  | 13.6517 | 12.8015 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-05-09 09:43 | 2019-07-23 15:39 | 0
| 33 | ROSEBANK STREET | 33/11 | 3 x 23 |  | 2020-01-16 15:48 | 12.0946 | 1 | 0 | 0 | 12.0946 | 12.0948 | 12.095 | 12.0953 | 12.0955 | 12.0957 | 12.0959 | 12.0961 | 12.0964 | 12.0966 | 12.0968 | 12.097 | 12.0972 | 12.0975 |  | 82.48% | 66.58% | 0% | 82006 | [7 empty] | 11.475 | 0.61956
[6 empty] | 43846.6583 |  |  |  |  | 42.978: Committed new connections: |  | 9.9756 | 8.0522 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-10-29 18:32 | 2019-06-13 16:56 | 0
| 25 | WALTON | 33/11 | 2 x 24 |  | 2019-12-17 12:02 | 5.0991 | 1 | 0 | 0 | 5.0991 | 5.0992 | 5.0993 | 5.0994 | 5.0995 | 5.0996 | 5.0997 | 5.0998 | 5.0999 | 5.1 | 5.1001 | 5.1002 | 5.1003 | 5.1004 |  | 80.46% | 62.27% | 0% | 82021 | [7 empty] | 5.04 | 0.05914
[6 empty] | 43816.5014 |  |  |  |  | 42.978: Committed new connections: |  | 4.1028 | 3.1755 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-16 12:15 | 2019-06-13 12:23 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
HELENSBURGH (SP) |  |  | 132/33 | 2 x 60 |  | #N/A | #N/A | 1 |  | Diverse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0% | 0% | 0% | [9 empty] | #N/A
Substation was not found in SubstationLoad | [5 empty] | #N/A |  |  |  | Aggregate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 42.9827: Generation at time of BSP peak:; 43.5647 42.9835: #N/A |  | #N/A | #N/A | 0
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DUMFIN 11kV Circuit |  |  |  | #N/A | #N/A | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0%
|  | Substation was not found in SubstationLoad |  |  |  | #N/A |  |  |  |  | 42.978: Committed new connections: |  | #N/A | #N/A | #N/A | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: #N/A |  | #N/A | #N/A | #N/A
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
DUNOON | 380 |  | 132/33 | 2 x 45 |  | 2019-11-17 18:57 | 19.0127 | 1 |  | Diverse | 19.0127 | 19.0537 | 19.0957 | 19.1388 | 19.183 | 19.2283 | 19.2748 | 19.3225 | 19.3714 | 19.4216 | 19.473 | 19.5258 | 19.5799 | 19.6355 | Diversity/Losses: 1.174 | 79.7% | 60.72% | -42.47% | 42930 | [7 empty] | 23.2 | -4.1873
[6 empty] | 43786.7896 |  |  |  | Aggregate | 22.3276 | 22.3757 | 22.4251 | 22.4757 | 22.5276 | 22.5808 | 22.6354 | 22.6914 | 22.7488 | 22.8077 | 22.8682 | 22.9301 | 22.9937 | 23.0589 |  | 15.1525 | 11.5452 | -8.0747 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 42.9827: Generation at time of BSP peak:; 43.5647 42.9835: 0 |  | 2019-04-11 21:19 | 2019-07-08 17:05 | 2020-03-21 21:39
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 18.6325 | 18.6726 | 18.7138 | 18.756 | 18.7993 | 18.8438 | 18.8893 | 18.936 | 18.984 | 19.0331 | 19.0836 | 19.1353 | 19.1883 | 19.2427
| 365 | BRUCHAG | 33/11 | 2 x 10 |  | 2020-03-07 13:19 | 3.3611 | 1 | 0 | 0 | 3.3611 | 3.3611 | 3.3612 | 3.3612 | 3.3613 | 3.3614 | 3.3614 | 3.3615 | 3.3615 | 3.3616 | 3.3617 | 3.3617 | 3.3618 | 3.3618 |  | 90.48% | 54.29% | 0% | 82222 | [7 empty] | 3.56 | -0.19895
[6 empty] | 43897.5549 |  |  |  |  | 42.978: Committed new connections: |  | 3.0409 | 1.8246 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-06 18:34 | 2019-06-08 16:22 | 0
| 385 | COLINTRAIVE | 33/11 | 1 x 0.5 |  | No PI | 0.26689 | 1 | M | M | 0.26689 | 0.27052 | 0.27421 | 0.27794 | 0.28172 | 0.28555 | 0.28943 | 0.29337 | 0.29736 | 0.30141 | 0.30551 | 0.30967 | 0.31388 | 0.31815 |  | 0% | 0% | 0% | 82240 | [7 empty] | 0.26408 | 0.0028094
[6 empty] | No PI |  |  |  |  | 42.978: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak: |  | 0 | 0 | 0
| 363 | DUNOON | 33/11 | 2 x 24 |  | 2019-11-18 18:34 | 6.9258 | 1 | 0 | 0 | 6.9258 | 6.9259 | 6.9261 | 6.9262 | 6.9263 | 6.9264 | 6.9266 | 6.9267 | 6.9268 | 6.9269 | 6.9271 | 6.9272 | 6.9273 | 6.9275 |  | 87.78% | 66.05% | 0% | 82204 | [7 empty] | 6.93 | -0.0041881
[6 empty] | 43787.7736 |  |  |  |  | 42.978: Committed new connections: |  | 6.0792 | 4.5746 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-10-28 18:37 | 2019-08-30 17:21 | 0
| 383 | GLENDARUEL | 33/11 | 1 x 0.3 |  | No PI | 0.35679 | 1 | H | H | 0.35679 | 0.36635 | 0.37617 | 0.38624 | 0.39659 | 0.40721 | 0.41812 | 0.42932 | 0.44082 | 0.45263 | 0.46475 | 0.4772 | 0.48999 | 0.50311 |  | 0% | 0% | 0% | 82237 | [7 empty] | 0.3596 | -0.0028094
[6 empty] | No PI |  |  |  |  | 42.978: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak: |  | 0 | 0 | 0
| 379 | INNELLAN | 33/11 | 1 x 6.25 |  | 2019-04-03 18:51 | 0.86792 | 1 | 0 | 0 | 0.86792 | 0.86794 | 0.86795 | 0.86797 | 0.86798 | 0.868 | 0.86801 | 0.86803 | 0.86805 | 0.86806 | 0.86808 | 0.86809 | 0.86811 | 0.86813 |  | 0% | 74.92% | 0% | 82209 | [7 empty] | 0.95 | -0.082081
[6 empty] | 43558.7854 |  |  |  |  | 42.978: Committed new connections: |  | #VALUE! | 0.65024 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | #VALUE! | 2019-08-21 17:23 | 0
| 366 | KAMES | 33/11 | 1 x 2.5 |  | 2019-11-30 18:41 | 0.59738 | 1 | 0 | 0 | 0.59738 | 0.59739 | 0.5974 | 0.59741 | 0.59742 | 0.59744 | 0.59745 | 0.59746 | 0.59747 | 0.59748 | 0.59749 | 0.5975 | 0.59751 | 0.59752 |  | 82.24% | 45.33% | 0% | 82245 | [7 empty] | 0.58 | 0.017381
[6 empty] | 43799.7785 |  |  |  |  | 42.978: Committed new connections: |  | 0.4913 | 0.27078 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-05 03:42 | 2019-08-15 18:29 | 0
| 384 | NEWTON | 33/11 | 1 x 0.3 |  | No PI | 0.27813 | 1 | 0 | 0 | 0.27813 | 0.27814 | 0.27814 | 0.27815 | 0.27815 | 0.27816 | 0.27816 | 0.27817 | 0.27817 | 0.27818 | 0.27818 | 0.27819 | 0.27819 | 0.2782 |  | 0% | 0% | 0% | 82233 | [7 empty] | 0.27251 | 0.0056188
[6 empty] | No PI |  |  |  |  | 42.978: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak: |  | 0 | 0 | 0
| 375 | OTTER FERRY | 33/11 | 1 x 2.5 |  | 2020-01-01 14:08 | 1.2897 | 1 | H | H | 1.2897 | 1.3242 | 1.3597 | 1.3961 | 1.4335 | 1.4719 | 1.5113 | 1.5518 | 1.5934 | 1.6361 | 1.6799 | 1.7249 | 1.7711 | 1.8186 |  | 86.47% | 70.35% | 0% | 82249 | [7 empty] | 1.5492 | -0.25954
[6 empty] | 43831.5889 |  |  |  |  | 42.978: Committed new connections: |  | 1.1152 | 0.90724 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-07 18:57 | 2019-06-18 18:17 | 0
| 362 | ROTHESAY | 33/11 | 2 x 24 |  | 2020-02-11 17:16 | 4.8336 | 1 | 0 | 0 | 4.8336 | 4.8336 | 4.8337 | 4.8338 | 4.8339 | 4.834 | 4.8341 | 4.8342 | 4.8343 | 4.8344 | 4.8344 | 4.8345 | 4.8346 | 4.8347 |  | 84.7% | 64.09% | 0% | 82218 | [7 empty] | 4.5228 | 0.31074
[6 empty] | 43872.7194 |  |  |  |  | 42.978: Committed new connections: |  | 4.094 | 3.0977 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-10-30 17:50 | 2019-08-30 17:49 | 0
| 364 | SANDBANK | 33/11 | 2 x 8 |  | 2019-11-30 18:38 | 3.5504 | 1 | 0 | 0 | 3.5504 | 3.5505 | 3.5506 | 3.5506 | 3.5507 | 3.5507 | 3.5508 | 3.5509 | 3.5509 | 3.551 | 3.5511 | 3.5511 | 3.5512 | 3.5513 |  | 87.76% | 55.8% | 0% | 82228 | [7 empty] | 3.49 | 0.060423
[6 empty] | 43799.7764 |  |  |  |  | 42.978: Committed new connections: |  | 3.1157 | 1.9813 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-06 18:40 | 2019-07-11 16:47 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
DUNVEGAN | 638 |  | 132/33 | 1 x 60 |  | 2019-09-14 02:19 | 54.2932 | 1 |  | Diverse | 54.2932 | 54.4976 | 54.7048 | 54.9148 | 55.1277 | 55.3434 | 55.562 | 55.7837 | 56.0083 | 56.2359 | 56.4667 | 56.7006 | 56.9376 | 57.1779 | Diversity/Losses: 0.15 | 100% | 94.8% | -67.58% | 82301 | [7 empty] | 8.6 | 45.6932
[6 empty] | 43722.0965 |  |  |  | Aggregate | 8.1319 | 8.1625 | 8.1935 | 8.225 | 8.2569 | 8.2892 | 8.3219 | 8.3551 | 8.3887 | 8.4228 | 8.4574 | 8.4924 | 8.5279 | 8.5639 |  | 54.2932 | 51.4697 | -36.6916 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 42.9827: Generation at time of BSP peak:; 43.5647 42.9835: 27.696 |  | 2019-09-14 02:19 | 2019-08-30 00:27 | 2019-09-30 14:38
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 53.2074 | 53.4077 | 53.6107 | 53.8165 | 54.0251 | 54.2365 | 54.4508 | 54.668 | 54.8881 | 55.1112 | 55.3374 | 55.5666 | 55.7989 | 56.0344
| 638 | DUNVEGAN | 33/11 | 1 x 4 |  | 2020-03-15 11:40 | 2.2425 | 1 | M | M | 2.2425 | 2.273 | 2.3039 | 2.3353 | 2.3671 | 2.3993 | 2.4319 | 2.465 | 2.4985 | 2.5325 | 2.567 | 2.6019 | 2.6373 | 2.6732 |  | 95.68% | 78.76% | 0% | 82311 | [7 empty] | 2.44
[6 empty] | 43905.4861 |  |  |  |  | 42.978: Committed new connections: |  | 2.1457 | 1.7661 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-03 20:05 | 2019-06-06 18:42 | 0
| 632 | PORTREE | 33/11 | 1 x 8 & 1 x 7.5 |  | 2019-11-14 12:25 | 4.525 | 1 | 0 | 0 | 4.525 | 4.5251 | 4.5252 | 4.5253 | 4.5254 | 4.5254 | 4.5255 | 4.5256 | 4.5257 | 4.5258 | 4.5259 | 4.5259 | 4.526 | 4.5261 |  | 87.05% | 77.92% | 0% | 82304 | [7 empty] | 4.6273 | -0.10226
[6 empty] | 43783.5174 |  |  |  |  | 42.978: Committed new connections: |  | 3.9389 | 3.5259 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-10-30 20:18 | 2019-06-06 11:36 | 0
| 640 | UIG | 33/11 | 1 x 2.5 |  | 2019-04-03 18:36 | 1.3643 | 1 | 0 | 0 | 1.3643 | 1.3644 | 1.3644 | 1.3644 | 1.3644 | 1.3645 | 1.3645 | 1.3645 | 1.3645 | 1.3646 | 1.3646 | 1.3646 | 1.3646 | 1.3647 |  | 100% | 84.71% | 0% | 82309 | [7 empty] | 1.21 | 0.15435
[6 empty] | 43558.775 |  |  |  |  | 42.978: Committed new connections: |  | 1.3643 | 1.1557 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 42.9827: Generation at time of peak:; 43.5647 42.9835: 0 |  | 2019-04-03 18:36 | 2019-06-06 18:30 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
DYCE | 843 |  | 132/33 | 2 x 60 |  | 2020-02-13 09:03 | 38.3709 | 1 |  | Diverse | 38.3709 | 38.3716 | 38.3723 | 38.373 | 38.3737 | 38.3744 | 38.3751 | 38.3758 | 38.3765 | 38.3772 | 38.3779 | 38.3786 | 38.3793 | 38.38 | Diversity/Losses: 1.137 | 84.11% | 70.06% | -13.25% | 13530 | [7 empty] | 43.5 | -5.1291
[6 empty] | 43874.3771 |  |  |  | Aggregate | 43.6159 | 43.6167 | 43.6175 | 43.6183 | 43.6191 | 43.6199 | 43.6207 | 43.6215 | 43.6223 | 43.6231 | 43.6239 | 43.6247 | 43.6255 | 43.6262 |  | 32.2744 | 26.8828 | -5.0854 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 43.6207: Generation at time of BSP peak:; 43.6215: 0.72225 |  | 2019-10-30 17:00 | 2019-06-25 10:43 | 2019-11-23 22:17
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 37.6035 | 37.6042 | 37.6049 | 37.6055 | 37.6062 | 37.6069 | 37.6076 | 37.6083 | 37.609 | 37.6097 | 37.6103 | 37.611 | 37.6117 | 37.6124
| 807 | BALMEDIE | 33/11 | 1 x 8 |  | 2020-01-29 17:00 | 3.6439 | 1 | 0 | 0 | 3.6439 | 3.6439 | 3.644 | 3.6441 | 3.6441 | 3.6442 | 3.6443 | 3.6443 | 3.6444 | 3.6444 | 3.6445 | 3.6446 | 3.6446 | 3.6447 |  | 0% | 0% | 20.05% | 82416 | [7 empty] | 3.58 | 0.063851
[6 empty] | 43859.7083 |  |  |  |  | 43.6159: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.73072 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 43.6207: Generation at time of peak:; 43.6215: 0.10324 |  |  |  | 2019-07-26 04:00
| 844 | DYCE NORTH | 33/11 | 2 x 24 |  | 2019-12-12 09:15 | 16.1486 | 1 | 0 | 0 | 16.1486 | 16.1489 | 16.1492 | 16.1495 | 16.1498 | 16.1501 | 16.1504 | 16.1507 | 16.151 | 16.1513 | 16.1515 | 16.1518 | 16.1521 | 16.1524 |  | 87.72% | 79.54% | 0% | 82406 | [7 empty] | 15.46 | 0.6886
[6 empty] | 43811.3854 |  |  |  |  | 43.6159: Committed new connections: |  | 14.1662 | 12.8439 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 43.6207: Generation at time of peak:; 43.6215: 0.2624 |  | 2019-10-30 09:11 | 2019-06-12 12:14 | 0
| 849 | ELLON 11 kV | 33/11 | 2 x 12.5 |  | 2019-11-19 17:19 | 10.8753 | 1 | 0 | 0 | 10.8753 | 10.8755 | 10.8757 | 10.8759 | 10.8761 | 10.8763 | 10.8765 | 10.8767 | 10.8769 | 10.8771 | 10.8773 | 10.8775 | 10.8777 | 10.8779 |  | 84.43% | 75.84% | 0% | 82427 | [7 empty] | 10.96 | -0.084664
[6 empty] | 2019-11-19 17:19: 43788.7215; 10.8753: Committed new connections: |  | 9.1818 | 8.2476 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-31 16:59 | 2019-06-12 17:18 | 0
| 991 | HARVEST AVENUE | 33/11 | 2 x 24 |  | 2020-01-23 09:02 | 3.456 | 1 | ? | 0 | 3.456 | 3.4561 | 3.4561 | 3.4562 | 3.4563 | 3.4563 | 3.4564 | 3.4564 | 3.4565 | 3.4566 | 3.4566 | 3.4567 | 3.4568 | 3.4568 |  | 89.12% | 70.37% | 0% | 82440 | [7 empty] | 0.64 | 2.816
[6 empty] | 2019-11-19 17:19: 43853.3764; 10.8753: Committed new connections: |  | 3.08 | 2.432 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[6 empty] | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-30 09:15 | 2019-08-21 14:21 | 0
| 884 | KINGSEAT | 33/11 | 2 x 5 |  | 2019-12-25 15:07 | 3.6877 | 1 | 0 | 0 | 3.6877 | 3.6878 | 3.6879 | 3.6879 | 3.688 | 3.6881 | 3.6881 | 3.6882 | 3.6883 | 3.6884 | 3.6884 | 3.6885 | 3.6886 | 3.6886 |  | 87.13% | 62.12% | 0% | 82409 | [7 empty] | 3.61 | 0.077745
[6 empty] | 2019-11-19 17:19: 43824.6299; 10.8753: Committed new connections: |  | 3.2133 | 2.2908 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-28 17:34 | 2019-06-24 17:52 | 0
| 947 | STONEYWOOD T3 | 33/11 | 1 x 24 |  | 2020-03-10 11:02 | 5.8044 | 1 | 0 | 0 | 5.8044 | 5.8045 | 5.8046 | 5.8047 | 5.8048 | 5.8049 | 5.805 | 5.8051 | 5.8052 | 5.8053 | 5.8054 | 5.8055 | 5.8056 | 5.8057 |  | 92.85% | 80.11% | 0% | 82403 | [7 empty] | 7.087 | -1.2826
[6 empty] | 2019-11-19 17:19: 43900.4597; 10.8753: Committed new connections: |  | 5.3894 | 4.6497 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 4.1884 |  | 2019-04-14 15:31 | 2019-08-16 00:18 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
ELGIN | 456 |  | 132/33 | 2 x 90 |  | 2019-11-19 16:48 | 47.1701 | 1 |  | Diverse | 47.1701 | 47.171 | 47.1718 | 47.1727 | 47.1736 | 47.1744 | 47.1753 | 47.1761 | 47.177 | 47.1779 | 47.1787 | 47.1796 | 47.1804 | 47.1813 | Diversity/Losses: 1.116 | 87.32% | 75.35% | 27.46% | 13630 | [7 empty] | 47.7 | -0.52989
[6 empty] | 43788.7 |  |  |  | Aggregate | 52.6538 | 52.6548 | 52.6557 | 52.6567 | 52.6576 | 52.6586 | 52.6596 | 52.6605 | 52.6615 | 52.6624 | 52.6634 | 52.6644 | 52.6653 | 52.6663 |  | 41.1908 | 35.5437 | 12.9552 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: |  |  | Generation at time of peak: 10.8765: Generation at time of BSP peak:; 0.2624 10.8767: 0 |  | 2019-10-30 17:01 | 2019-06-13 12:04 | 2019-06-23 04:49
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 46.2267 | 46.2276 | 46.2284 | 46.2292 | 46.2301 | 46.2309 | 46.2318 | 46.2326 | 46.2335 | 46.2343 | 46.2352 | 46.236 | 46.2368 | 46.2377
| 458 | ASHGROVE | 33/11 | 1 x 10 |  | 2019-11-19 16:42 | 7.4309 | 1 | 0 | 0 | 7.4309 | 7.4311 | 7.4312 | 7.4313 | 7.4315 | 7.4316 | 7.4317 | 7.4319 | 7.432 | 7.4321 | 7.4323 | 7.4324 | 7.4326 | 7.4327 |  | 83.98% | 73.11% | 0% | 82513 | [7 empty] | 6.73 | 0.70093
[6 empty] | 2019-11-19 17:19: 43788.6958; 10.8753: Committed new connections: |  | 6.2402 | 5.4327 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-31 16:53 | 2019-07-27 09:52 | 0
| 499 | BILBOHALL | 33/11 | 1 x 24 |  | 2019-11-18 14:26 | 4.0579 | 1 | 0 | 0 | 4.0579 | 4.0579 | 4.058 | 4.0581 | 4.0582 | 4.0582 | 4.0583 | 4.0584 | 4.0585 | 4.0585 | 4.0586 | 4.0587 | 4.0588 | 4.0588 |  | 94.09% | 91.88% | 0% | 82502 | [7 empty] | 3.57 | 0.48787
[6 empty] | 2019-11-19 17:19: 43787.6014; 10.8753: Committed new connections: |  | 3.8179 | 3.7286 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-09-18 12:53 | 2019-06-04 15:05 | 0
| 454 | BURGHEAD | 33/11 | 2 x 15 |  | 2020-01-14 16:56 | 6.9821 | 1 | 0 | 0 | 6.9821 | 6.9823 | 6.9824 | 6.9825 | 6.9827 | 6.9828 | 6.9829 | 6.983 | 6.9832 | 6.9833 | 6.9834 | 6.9836 | 6.9837 | 6.9838 |  | 89.63% | 75.08% | 0% | 82534 | [7 empty] | 6.71 | 0.27215
[6 empty] | 2019-11-19 17:19: 43844.7056; 10.8753: Committed new connections: |  | 6.2582 | 5.2421 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-24 18:47 | 2019-08-09 17:44 | 0
| 457 | CUMMING STREET | 33/11 | 2 x 24 |  | 2019-04-03 12:17 | 11.7213 | 1 | 0 | 0 | 11.7213 | 11.7215 | 11.7217 | 11.7219 | 11.7222 | 11.7224 | 11.7226 | 11.7228 | 11.723 | 11.7232 | 11.7234 | 11.7236 | 11.7239 | 11.7241 |  | 0% | 92.48% | 0% | 82518 | [7 empty] | 12.4 | -0.6787
[6 empty] | 2019-11-19 17:19: 43558.5118; 10.8753: Committed new connections: |  | #VALUE! | 10.8394 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | #VALUE! | 2019-07-05 12:22 | 0
| 482 | ELGIN | 33/11 | 2 x 10 |  | 2020-01-12 17:23 | 4.5139 | 1 | 0 | 0 | 4.5139 | 4.5139 | 4.514 | 4.5141 | 4.5142 | 4.5143 | 4.5144 | 4.5144 | 4.5145 | 4.5146 | 4.5147 | 4.5148 | 4.5148 | 4.5149 |  | 83.7% | 71.54% | 0% | 82535 | [7 empty] | 4.24 | 0.27386
[6 empty] | 2019-11-19 17:19: 43842.7243; 10.8753: Committed new connections: |  | 3.778 | 3.2291 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-31 17:03 | 2019-06-12 17:32 | 0
| 487 | FOCHABERS | 33/11 | 2 x 15 |  | 2019-11-19 11:04 | 6.4182 | 1 | 0 | 0 | 6.4182 | 6.4183 | 6.4184 | 6.4185 | 6.4186 | 6.4188 | 6.4189 | 6.419 | 6.4191 | 6.4192 | 6.4193 | 6.4195 | 6.4196 | 6.4197 |  | 91.04% | 84.31% | 0% | 82505 | 83661 | [6 empty] | 6.03 | 0.38817
[6 empty] | 2019-11-19 17:19: 43788.4611; 10.8753: Committed new connections: |  | 5.8433 | 5.4114 | 0 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-30 07:46 | 2019-06-06 09:00 | 0
| 453 | KINLOSS | 33/11 | 2 x 15 |  | 2020-02-25 07:13 | 3.148 | 1 | 0 | 0 | 3.148 | 3.1481 | 3.1481 | 3.1482 | 3.1482 | 3.1483 | 3.1483 | 3.1484 | 3.1485 | 3.1485 | 3.1486 | 3.1486 | 3.1487 | 3.1488 |  | 84.87% | 63.48% | 0% | 82506 | 84542 | [6 empty] | 2.76 | 0.388
[6 empty] | 2019-11-19 17:19: 43886.3007; 10.8753: Committed new connections: |  | 2.6717 | 1.9982 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-28 17:41 | 2019-08-08 14:29 | 0
| 488 | LHANBRYDE | 33/11 | 2 x 5 |  | 2019-12-25 11:54 | 1.3845 | 1 | 0 | 0 | 1.3845 | 1.3845 | 1.3845 | 1.3846 | 1.3846 | 1.3846 | 1.3846 | 1.3847 | 1.3847 | 1.3847 | 1.3847 | 1.3848 | 1.3848 | 1.3848 |  | 86.56% | 62.36% | 0% | 82523 | [7 empty] | 1.38 | 0.004476
[6 empty] | 2019-11-19 17:19: 43824.4958; 10.8753: Committed new connections: |  | 1.1984 | 0.86329 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-27 17:24 | 2019-06-13 18:11 | 0
| 455 | LOSSIEMOUTH | 33/11 | 2 x 15 |  | 2019-12-16 16:49 | 6.997 | 1 | 0 | 0 | 6.997 | 6.9972 | 6.9973 | 6.9974 | 6.9975 | 6.9977 | 6.9978 | 6.9979 | 6.9981 | 6.9982 | 6.9983 | 6.9984 | 6.9986 | 6.9987 |  | 83.14% | 70.53% | 0% | 82526 | [7 empty] | 6.52 | 0.47703
[6 empty] | 2019-11-19 17:19: 43815.7007; 10.8753: Committed new connections: |  | 5.817 | 4.9351 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 10.8765: Generation at time of peak:; 0.2624 10.8767: 0 |  | 2019-10-30 17:07 | 2019-06-13 17:35 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
FASNAKYLE | 521 |  | 275/33 | 2 x 120 |  | 2020-02-09 14:24 | 98.7678 | 1 |  | Diverse | 98.7678 | 98.7696 | 98.7714 | 98.7732 | 98.775 | 98.7768 | 98.7786 | 98.7804 | 98.7822 | 98.784 | 98.7858 | 98.7876 | 98.7894 | 98.7912 | Diversity/Losses: 0.005 | 95.16% | 84.76% | -63% | 13830 | [7 empty] | 0.63 | 98.1378
[6 empty] | 43870.6 |  |  |  | Aggregate | 0.51977 | 0.51978 | 0.51979 | 0.5198 | 0.51981 | 0.51982 | 0.51983 | 0.51984 | 0.51985 | 0.51986 | 0.51987 | 0.51988 | 0.51989 | 0.5199 |  | 93.9851 | 83.7172 | -62.2215 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 15.8317 |  | 2019-04-06 18:13 | 2019-08-17 22:51 | 2019-12-22 19:50
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 96.7924 | 96.7942 | 96.7959 | 96.7977 | 96.7995 | 96.8012 | 96.803 | 96.8048 | 96.8065 | 96.8083 | 96.8101 | 96.8118 | 96.8136 | 96.8154
| 519 | FASNAKYLE PRIMARY | 33/11 | 1 x 1 |  | 2019-04-16 08:10 | 0.51977 | 1 | 0 | 0 | 0.51977 | 0.51978 | 0.51979 | 0.5198 | 0.51981 | 0.51982 | 0.51983 | 0.51984 | 0.51985 | 0.51986 | 0.51987 | 0.51988 | 0.51989 | 0.5199 |  | 100% | 69.66% | 0% | 82606 | [7 empty] | 0.63 | -0.11023
[6 empty] | 43571.3403 |  |  |  |  | 0.51977: Committed new connections: |  | 0.51977 | 0.3621 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-16 08:10 | 2019-07-04 19:21 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
FIDDES | 851 |  | 132/33 | 2 x 90 |  | 2020-01-16 21:45 | 110.0853 | 1 |  | Diverse | 110.0853 | 110.0873 | 110.0893 | 110.0913 | 110.0933 | 110.0953 | 110.0974 | 110.0994 | 110.1014 | 110.1034 | 110.1054 | 110.1074 | 110.1094 | 110.1114 | Diversity/Losses: 0.181 | 86.74% | 72.75% | -64.59% | 14030 | [7 empty] | 19.8 | 90.2853
[6 empty] | 43846.9062 |  |  |  | Aggregate | 19.9351 | 19.9354 | 19.9358 | 19.9362 | 19.9365 | 19.9369 | 19.9373 | 19.9376 | 19.938 | 19.9384 | 19.9387 | 19.9391 | 19.9394 | 19.9398 |  | 95.4908 | 80.0896 | -71.1041 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 5.0503 |  | 2019-10-10 01:19 | 2019-08-28 13:17 | 2020-02-20 14:52
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 107.8836 | 107.8856 | 107.8875 | 107.8895 | 107.8915 | 107.8934 | 107.8954 | 107.8974 | 107.8993 | 107.9013 | 107.9033 | 107.9053 | 107.9072 | 107.9092
| 847 | EDZELL | 33/11 | 1 x 8 |  | 2019-11-19 15:00 | 2.4908 | 1 | 0 | 0 | 2.4908 | 2.4909 | 2.4909 | 2.491 | 2.491 | 2.4911 | 2.4911 | 2.4912 | 2.4912 | 2.4912 | 2.4913 | 2.4913 | 2.4914 | 2.4914 |  | 0% | 0% | 21.61% | 82706 | [7 empty] | 2.52 | -0.029168
[6 empty] | 43788.625 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.53824 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  |  |  | 2019-08-06 03:30
| 873 | INVERBERVIE | 33/11 | 2 x 8 |  | 2019-12-24 17:43 | 3.4527 | 1 | 0 | 0 | 3.4527 | 3.4527 | 3.4528 | 3.4529 | 3.4529 | 3.453 | 3.4531 | 3.4531 | 3.4532 | 3.4532 | 3.4533 | 3.4534 | 3.4534 | 3.4535 |  | 91.88% | 69.27% | 0% | 82714 | [7 empty] | 3.01 | 0.44268
[6 empty] | 43823.7382 |  |  |  |  | 0.51977: Committed new connections: |  | 3.1724 | 2.3915 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0.7432 |  | 2019-10-29 17:36 | 2019-08-20 19:29 | 0
| 890 | LAURENCEKIRK | 33/11 | 2 x 5 |  | 2019-11-19 16:21 | 5.0509 | 1 | 0 | 0 | 5.0509 | 5.051 | 5.0511 | 5.0512 | 5.0513 | 5.0514 | 5.0515 | 5.0516 | 5.0517 | 5.0517 | 5.0518 | 5.0519 | 5.052 | 5.0521 |  | 86.71% | 66.09% | 0% | 82710 | [7 empty] | 5.01 | 0.04092
[6 empty] | 43788.6813 |  |  |  |  | 0.51977: Committed new connections: |  | 4.3796 | 3.3384 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-31 17:34 | 2019-07-04 17:55 | 0
| 945 | STONEHAVEN | 33/11 | 2 x 24 |  | 2019-11-13 17:00 | 8.9406 | 1 | 0 | 0 | 8.9406 | 8.9408 | 8.941 | 8.9411 | 8.9413 | 8.9415 | 8.9416 | 8.9418 | 8.942 | 8.9421 | 8.9423 | 8.9424 | 8.9426 | 8.9428 |  | 0% | 0% | 19.27% | 82703 | [7 empty] | 9.69 | -0.74935
[6 empty] | 43782.7083 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 1.7226 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 2.0473 |  |  |  | 2019-06-03 03:00
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
FORT AUGUSTUS | 716 |  | 132/33 | 1 x 15 |  | 2020-01-21 02:40 | 9.9761 | 1 |  | Diverse | 9.9761 | 9.9813 | 9.9866 | 9.9921 | 9.9977 | 10.0034 | 10.0093 | 10.0153 | 10.0215 | 10.0279 | 10.0344 | 10.0411 | 10.048 | 10.0551 | Diversity/Losses: 0.451 | 72.57% | 70.79% | -40.59% | 13930 | [7 empty] | 5 | 4.9761
[6 empty] | 43851.1111 |  |  |  | Aggregate | 4.5 | 4.5023 | 4.5047 | 4.5072 | 4.5097 | 4.5123 | 4.515 | 4.5177 | 4.5205 | 4.5234 | 4.5263 | 4.5293 | 4.5324 | 4.5356 |  | 7.2399 | 7.0625 | -4.0496 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 6.4697 |  | 2019-10-27 02:53 | 2019-08-11 23:45 | 2020-03-12 16:40
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 9.7766 | 9.7817 | 9.7869 | 9.7922 | 9.7977 | 9.8033 | 9.8091 | 9.815 | 9.8211 | 9.8273 | 9.8337 | 9.8403 | 9.847 | 9.854
| 710 | ABERCHALDER | 33/11 | 1 x 0.2 |  | No PI | 0.084282 | 1 | H | H | 0.084282 | 0.08654 | 0.088858 | 0.091238 | 0.093682 | 0.096192 | 0.098769 | 0.10141 | 0.10413 | 0.10692 | 0.10978 | 0.11273 | 0.11575 | 0.11885 |  | 0% | 0% | 0% | 82807 | [7 empty] | 0.078663 | 0.0056188
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 894 | ARDOCHY | 33/11 | 0.1 |  | No PI | 0.022475 | 1 | ? | 0 | 0.022475 | 0.022476 | 0.022476 | 0.022476 | 0.022477 | 0.022477 | 0.022478 | 0.022478 | 0.022479 | 0.022479 | 0.022479 | 0.02248 | 0.02248 | 0.022481 |  | 0% | 0% | 0% | [8 empty] | 0.022475
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 745 | BUNOICH | 33/11 | 1 x 2 |  | 2020-01-03 18:39 | 0.19315 | 1 | 0 | 0 | 0.19315 | 0.19316 | 0.19316 | 0.19316 | 0.19317 | 0.19317 | 0.19317 | 0.19318 | 0.19318 | 0.19318 | 0.19319 | 0.19319 | 0.1932 | 0.1932 |  | 98.07% | 78.1% | 0% | 82816 | [7 empty] | 0.18 | 0.013153
[6 empty] | 43833.7771 |  |  |  |  | 0.51977: Committed new connections: |  | 0.18943 | 0.15085 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-03 13:49 | 2019-06-02 13:51 | 0
| 517 | DRUMNADROCHIT | 33/11 | 1 x 6 |  | 2019-12-30 02:00 | 2.8469 | 1 | 0 | 0 | 2.8469 | 2.847 | 2.8471 | 2.8471 | 2.8472 | 2.8472 | 2.8473 | 2.8473 | 2.8474 | 2.8474 | 2.8475 | 2.8475 | 2.8476 | 2.8476 |  | 0% | 0% | 17.87% | 82814 | [7 empty] | 2.39 | 0.45695
[6 empty] | 43829.0833 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.50861 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 1.942 |  |  |  | 2019-08-26 02:30
| 396 | GLEN LAOGH | 33/11 | 1 x 0.1 |  | No PI | 0.0084282 | 1 | 0 | 0 | 0.0084282 | 0.0084284 | 0.0084285 | 0.0084287 | 0.0084288 | 0.008429 | 0.0084291 | 0.0084293 | 0.0084295 | 0.0084296 | 0.0084298 | 0.0084299 | 0.0084301 | 0.0084302 |  | 0% | 0% | 0% | [8 empty] | 0.0084282 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 781 | GLENDOE PRIMARY | 33/11 | 1 x 15 |  | 2019-12-31 18:34 | 0.83059 | 1 | 0 | 0 | 0.83059 | 0.83061 | 0.83062 | 0.83064 | 0.83065 | 0.83067 | 0.83068 | 0.8307 | 0.83071 | 0.83073 | 0.83074 | 0.83076 | 0.83077 | 0.83079 |  | 99.42% | 86.68% | 0% | 82823 | [7 empty] | 0.95 | -0.11941
[6 empty] | 43830.7736 |  |  |  |  | 0.51977: Committed new connections: |  | 0.82578 | 0.71993 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-05 19:08 | 2019-06-05 18:00 | 0
| 766 | INVERGARRY | 33/11 | 1 x 1 |  | No PI | 0.4776 | 1 | 0 | 0 | 0.4776 | 0.47761 | 0.47762 | 0.47763 | 0.47763 | 0.47764 | 0.47765 | 0.47766 | 0.47767 | 0.47768 | 0.47769 | 0.4777 | 0.4777 | 0.47771 |  | 0% | 0% | 0% | 82810 | [7 empty] | 0.4776 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 763 | WESTER DRUMMOND | 33/11 | 1 x 0.1 |  | No PI | 0.036522 | 1 | 0 | 0 | 0.036522 | 0.036523 | 0.036524 | 0.036524 | 0.036525 | 0.036526 | 0.036526 | 0.036527 | 0.036528 | 0.036528 | 0.036529 | 0.03653 | 0.03653 | 0.036531 |  | 0% | 0% | 0% | 82831 | [7 empty] | 0.036522 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
FORT WILLIAM | 715 |  | 132/33 | 2 x 120 |  | 2019-08-16 22:32 | 61.2745 | 1 |  | Diverse | 61.2745 | 61.7917 | 62.3227 | 62.868 | 63.4278 | 64.0026 | 64.5927 | 65.1987 | 65.8209 | 66.4597 | 67.1156 | 67.789 | 68.4805 | 69.1905 | Diversity/Losses: 0.575 | 92.27% | 100% | -31.08% | 14430 | [7 empty] | 65.7 | -4.4255
[6 empty] | 43693.9389 |  |  |  | Aggregate | 35.2634 | 35.5611 | 35.8667 | 36.1805 | 36.5026 | 36.8334 | 37.1731 | 37.5218 | 37.8798 | 38.2475 | 38.625 | 39.0125 | 39.4105 | 39.8191 |  | 56.5362 | 61.2745 | -19.047 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 30.3448 |  | 2019-09-01 13:32 | 2019-08-16 22:32 | 2020-01-09 02:54
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 60.049 | 60.5559 | 61.0763 | 61.6106 | 62.1592 | 62.7225 | 63.3009 | 63.8947 | 64.5045 | 65.1305 | 65.7733 | 66.4333 | 67.1109 | 67.8067
| 702 | ANNAT | 33/11 | 1 x 15 |  | 2019-12-02 13:20 | 2.7856 | 1 | 0 | 0 | 2.7856 | 2.7856 | 2.7857 | 2.7857 | 2.7858 | 2.7858 | 2.7859 | 2.7859 | 2.786 | 2.786 | 2.7861 | 2.7861 | 2.7862 | 2.7862 |  | 87.36% | 71.26% | 0% | 82961 | [7 empty] | 2.68 | 0.10557
[6 empty] | 43801.5556 |  |  |  |  | 0.51977: Committed new connections: |  | 2.4334 | 1.9851 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-31 08:11 | 2019-06-14 07:30 | 0
| 740 | ARISAIG | 33/11 | 1 x 2.5 |  | 2019-04-06 13:50 | 0.71044 | 1 | 0 | 0 | 0.71044 | 0.71045 | 0.71046 | 0.71048 | 0.71049 | 0.7105 | 0.71051 | 0.71053 | 0.71054 | 0.71055 | 0.71057 | 0.71058 | 0.71059 | 0.71061 |  | 100% | 78.88% | 0% | 82966 | [7 empty] | 0.65 | 0.060437
[6 empty] | 43561.5764 |  |  |  |  | 0.51977: Committed new connections: |  | 0.71044 | 0.56039 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-06 13:50 | 2019-07-22 17:44 | 0
| 744 | CORRAN | 33/11 | 1 x 2.5 |  | 2020-02-16 18:38 | 1.3234 | 1 | 0 | 0 | 1.3234 | 1.3235 | 1.3235 | 1.3235 | 1.3235 | 1.3235 | 1.3236 | 1.3236 | 1.3236 | 1.3236 | 1.3237 | 1.3237 | 1.3237 | 1.3237 |  | 96.97% | 72.96% | 0% | 82931 | [7 empty] | 1.33 | -0.0065719
[6 empty] | 43877.7764 |  |  |  |  | 0.51977: Committed new connections: |  | 1.2834 | 0.96558 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-16 18:47 | 2019-06-15 08:15 | 0
| 714 | GLENSANDA | 33/11 | 2 x 15 |  | 2019-09-27 15:25 | 6.253 | 1 | H | H | 6.253 | 6.4205 | 6.5924 | 6.769 | 6.9504 | 7.1365 | 7.3277 | 7.524 | 7.7256 | 7.9325 | 8.145 | 8.3632 | 8.5872 | 8.8172 |  | 100% | 99.64% | 0% | 82927 | [7 empty] | 6.6 | -0.34704
[6 empty] | 43735.6424 |  |  |  |  | 0.51977: Committed new connections: |  | 6.253 | 6.2306 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-09-27 15:25 | 2019-06-06 13:19 | 0
| 756 | GLENUIG | 33/11 | 1 x 0.1 |  | No PI | 0.078663 | 1 | H | H | 0.078663 | 0.080771 | 0.082934 | 0.085156 | 0.087437 | 0.089779 | 0.092184 | 0.094653 | 0.097189 | 0.099792 | 0.10247 | 0.10521 | 0.10803 | 0.11092 |  | 0% | 0% | 0% | [8 empty] | 0.078663 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 724 | INVERLOCHY | 33/11 | 2 x 15 |  | 2019-11-20 13:56 | 10.068 | 1 | 0 | 0 | 10.068 | 10.0682 | 10.0684 | 10.0686 | 10.0688 | 10.0689 | 10.0691 | 10.0693 | 10.0695 | 10.0697 | 10.0699 | 10.07 | 10.0702 | 10.0704 |  | 77.72% | 65.53% | 0% | 82956 | [7 empty] | 9.1 | 0.96803
[6 empty] | 43789.5806 |  |  |  |  | 0.51977: Committed new connections: |  | 7.8252 | 6.5972 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0.15818 |  | 2019-04-16 13:25 | 2019-06-02 13:26 | 0
| 771 | KINGAIRLOCH | 33/11 | 1 x 0.1 |  | No PI | 0.081473 | 1 | H | H | 0.081473 | 0.083655 | 0.085896 | 0.088197 | 0.09056 | 0.092986 | 0.095476 | 0.098034 | 0.10066 | 0.10336 | 0.10613 | 0.10897 | 0.11189 | 0.11488 |  | 0% | 0% | 0% | [8 empty] | 0.081473 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 754 | KINLOCHMOIDART | 33/11 | 1 x 2 |  | No PI | 0.070235 | 1 | 0 | 0 | 0.070235 | 0.070236 | 0.070238 | 0.070239 | 0.07024 | 0.070242 | 0.070243 | 0.070244 | 0.070245 | 0.070247 | 0.070248 | 0.070249 | 0.070251 | 0.070252 |  | 0% | 0% | 0% | 82974 | [7 empty] | 0.070235 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 721 | LIDDESDALE | 33/11 | 1 x 0.1 |  | 2020-02-18 20:15 | 0.82466 | 1 | H | H | 0.82466 | 0.84675 | 0.86944 | 0.89273 | 0.91664 | 0.94119 | 0.96641 | 0.99229 | 1.0189 | 1.0462 | 1.0742 | 1.103 | 1.1325 | 1.1628 |  | 84.26% | 70.05% | 0% | [8 empty] | 0.77 | 0.054663
[6 empty] | 43879.8438 |  |  |  |  | 0.51977: Committed new connections: |  | 0.69489 | 0.57768 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-28 20:05 | 2019-06-24 17:57 | 0
| 747 | LOCHALINE | 33/11 | 1 x 5 |  | 2019-04-03 14:20 | 1 | 1 | H | H | 1 | 1.0268 | 1.0543 | 1.0825 | 1.1115 | 1.1413 | 1.1719 | 1.2033 | 1.2355 | 1.2686 | 1.3026 | 1.3375 | 1.3733 | 1.4101 |  | 100% | 62.5% | 0% | 82980 | [7 empty] | 0.86 | 0.14
[6 empty] | 43558.5972 |  |  |  |  | 0.51977: Committed new connections: |  | 1 | 0.625 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-03 14:20 | 2019-08-20 10:15 | 0
| 731 | MALLAIG | 33/11 | 1 x 6.3 |  | 2019-12-08 03:44 | 1.7052 | 1 | 0 | 0 | 1.7052 | 1.7052 | 1.7052 | 1.7052 | 1.7053 | 1.7053 | 1.7053 | 1.7054 | 1.7054 | 1.7054 | 1.7055 | 1.7055 | 1.7055 | 1.7056 |  | 75.42% | 77.65% | 0% | 82971 | [7 empty] | 1.5616 | 0.14358
[6 empty] | 43807.1556 |  |  |  |  | 0.51977: Committed new connections: |  | 1.286 | 1.3241 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-05-08 18:37 | 2019-06-18 18:37 | 0
| 734 | PINEGROVE | 33/11 | 2 x 10 |  | 2019-12-01 13:21 | 6.4709 | 1 | 0 | 0 | 6.4709 | 6.471 | 6.4711 | 6.4713 | 6.4714 | 6.4715 | 6.4716 | 6.4717 | 6.4718 | 6.472 | 6.4721 | 6.4722 | 6.4723 | 6.4724 |  | 87.92% | 70.27% | 0% | 82935 | [7 empty] | 6.3474 | 0.12352
[6 empty] | 43800.5563 |  |  |  |  | 0.51977: Committed new connections: |  | 5.6895 | 4.5471 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-31 13:19 | 2019-06-03 13:19 | 0
| 753 | POOR HOUSE | 33/11 | 1 x 0.1 |  | No PI | 0.019666 | 1 | 0 | 0 | 0.019666 | 0.019666 | 0.019667 | 0.019667 | 0.019667 | 0.019668 | 0.019668 | 0.019668 | 0.019669 | 0.019669 | 0.019669 | 0.01967 | 0.01967 | 0.019671 |  | 0% | 0% | 0% | [8 empty] | 0.019666 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 732 | RAHOY | 33/11 | 1 x 1 |  | No PI | 0.042141 | 1 | 0 | 0 | 0.042141 | 0.042142 | 0.042143 | 0.042143 | 0.042144 | 0.042145 | 0.042146 | 0.042147 | 0.042147 | 0.042148 | 0.042149 | 0.04215 | 0.04215 | 0.042151 |  | 0% | 0% | 0% | 82905 | [7 empty] | 0.042141 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 749 | SALEN 2 | 33/11 | 1 x 2.5 |  | 2019-04-06 13:25 | 2.8571 | 1 | H | H | 2.8571 | 2.9336 | 3.0122 | 3.0929 | 3.1758 | 3.2608 | 3.3482 | 3.4379 | 3.53 | 3.6245 | 3.7216 | 3.8213 | 3.9237 | 4.0288 |  | 100% | 65.66% | 0% | 82921 | [7 empty] | 3.3679 | -0.51085
[6 empty] | 43561.559 |  |  |  |  | 0.51977: Committed new connections: |  | 2.8571 | 1.8759 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-06 13:25 | 2019-07-03 21:19 | 0
| 755 | SHONA BEAG | 33/11 | 1 x 0.1 |  | No PI | 0.028094 | 1 | 0 | 0 | 0.028094 | 0.028095 | 0.028095 | 0.028096 | 0.028096 | 0.028097 | 0.028097 | 0.028098 | 0.028098 | 0.028099 | 0.028099 | 0.0281 | 0.0281 | 0.028101 |  | 0% | 0% | 0% | [8 empty] | 0.028094 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 751 | STRONTIAN | 33/11 | 1 x 2.5 |  | 2019-11-19 13:24 | 0.94492 | 1 | 0 | 0 | 0.94492 | 0.94494 | 0.94496 | 0.94497 | 0.94499 | 0.94501 | 0.94503 | 0.94504 | 0.94506 | 0.94508 | 0.94509 | 0.94511 | 0.94513 | 0.94515 |  | 83.16% | 55.47% | 0% | 82919 | [7 empty] | 0.83 | 0.11492
[6 empty] | 43788.5583 |  |  |  |  | 0.51977: Committed new connections: |  | 0.78581 | 0.5241 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-03 13:55 | 2019-06-06 13:20 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
FRASERBURGH | 853 |  | 132/33 | 2 x 45 |  | 2019-12-17 11:44 | 17.9867 | 1 |  | Diverse | 17.9867 | 17.987 | 17.9874 | 17.9877 | 17.988 | 17.9884 | 17.9887 | 17.989 | 17.9893 | 17.9897 | 17.99 | 17.9903 | 17.9907 | 17.991 | Diversity/Losses: 0.984 | 92.05% | 77.37% | 17.18% | 14330 | [7 empty] | 19.4 | -1.4133
[6 empty] | 43816.4889 |  |  |  | Aggregate | 17.696 | 17.6963 | 17.6966 | 17.697 | 17.6973 | 17.6976 | 17.6979 | 17.6983 | 17.6986 | 17.6989 | 17.6992 | 17.6996 | 17.6999 | 17.7002 |  | 16.5562 | 13.9166 | 3.0908 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 0 |  | 2019-10-29 16:57 | 2019-06-06 11:32 | 2019-10-07 00:47
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 17.627 | 17.6273 | 17.6276 | 17.6279 | 17.6283 | 17.6286 | 17.6289 | 17.6292 | 17.6296 | 17.6299 | 17.6302 | 17.6305 | 17.6308 | 17.6312
| 854 | FRASERBURGH | 33/11 | 2 x 40 |  | 2019-12-17 11:42 | 17.696 | 1 | 0 | 0 | 17.696 | 17.6963 | 17.6966 | 17.697 | 17.6973 | 17.6976 | 17.6979 | 17.6983 | 17.6986 | 17.6989 | 17.6992 | 17.6996 | 17.6999 | 17.7002 |  | 92.09% | 78.46% | 0% | 83000 | [7 empty] | 19.09 | -1.394
[6 empty] | 43816.4875 |  |  |  |  | 0.51977: Committed new connections: |  | 16.2958 | 13.8851 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-29 17:01 | 2019-06-06 11:00 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
GRUDIE BRIDGE | 526 |  | 132/33 | 2 x 90 |  | 2019-06-15 20:08 | 12.82 | 1 |  | Diverse | 12.82 | 12.8529 | 12.8868 | 12.9215 | 12.9572 | 12.9939 | 13.0315 | 13.0701 | 13.1097 | 13.1504 | 13.1922 | 13.2351 | 13.2791 | 13.3243 | Diversity/Losses: 0.761 | 58.81% | 100% | -215.2% | 14830 | [7 empty] | 9.9 | 2.92
[6 empty] | 43631.8389 |  |  |  | Aggregate | 9.7589 | 9.784 | 9.8097 | 9.8362 | 9.8634 | 9.8912 | 9.9199 | 9.9493 | 9.9794 | 10.0104 | 10.0422 | 10.0749 | 10.1084 | 10.1428 |  | 7.54 | 12.82 | -27.5823 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 0.07444 |  | 2019-05-08 20:12 | 2019-06-15 20:08 | 2020-03-22 02:27
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 12.5636 | 12.5959 | 12.6291 | 12.6631 | 12.6981 | 12.734 | 12.7708 | 12.8087 | 12.8475 | 12.8874 | 12.9283 | 12.9704 | 13.0135 | 13.0578
| 505 | ACHILTIBUIE | 33/11 | 1 x 1 |  | 2020-02-14 16:52 | 0.91987 | 1 | H | H | 0.91987 | 0.94451 | 0.96981 | 0.99579 | 1.0225 | 1.0499 | 1.078 | 1.1069 | 1.1365 | 1.167 | 1.1982 | 1.2303 | 1.2633 | 1.2971 |  | 88.54% | 88.34% | 0% | 83335 | [7 empty] | 0.81 | 0.10987
[6 empty] | 43875.7028 |  |  |  |  | 0.51977: Committed new connections: |  | 0.81448 | 0.81262 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0.86071 |  | 2019-04-03 21:24 | 2019-08-19 10:00 | 0
| 504 | AULTBEA | 33/11 | 1 x 6 |  | 2019-04-03 11:11 | 1.6506 | 1 | 0 | 0 | 1.6506 | 1.6506 | 1.6507 | 1.6507 | 1.6507 | 1.6508 | 1.6508 | 1.6508 | 1.6508 | 1.6509 | 1.6509 | 1.6509 | 1.651 | 1.651 |  | 100% | 76.97% | 0% | 83310 | [7 empty] | 1.69 | -0.0394
[6 empty] | 43558.466 |  |  |  |  | 0.51977: Committed new connections: |  | 1.6506 | 1.2705 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-03 11:11 | 2019-06-13 20:08 | 0
| 535 | BIDEN CLAN RAONAILD | 33/11 | 1 x 0.1 |  | No PI | 0.0028094 | 1 | 0 | 0 | 0.0028094 | 0.0028095 | 0.0028095 | 0.0028096 | 0.0028096 | 0.0028097 | 0.0028097 | 0.0028098 | 0.0028098 | 0.0028099 | 0.0028099 | 0.00281 | 0.00281 | 0.0028101 |  | 0% | 0% | 0% | [8 empty] | 0.0028094 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 518 | DRUMRUNIE | 33/11 | 1 x 0.2 |  | No PI | 0.32589 | 1 | 0 | 0 | 0.32589 | 0.3259 | 0.3259 | 0.32591 | 0.32592 | 0.32592 | 0.32593 | 0.32593 | 0.32594 | 0.32594 | 0.32595 | 0.32596 | 0.32596 | 0.32597 |  | 0% | 0% | 0% | 83332 | [7 empty] | 0.32589 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 567 | GARBAT FOREST | 33/11 | 1 x 0.1 |  | No PI | 0.0056188 | 1 | 0 | 0 | 0.0056188 | 0.0056189 | 0.005619 | 0.0056191 | 0.0056192 | 0.0056193 | 0.0056194 | 0.0056195 | 0.0056196 | 0.0056197 | 0.0056198 | 0.0056199 | 0.00562 | 0.0056202 |  | 0% | 0% | 0% | [8 empty] | 0.0056188 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 527 | INVERBROOM | 33/11 | 1 x 0.2 |  | No PI | 0.22194 | 1 | 0 | 0 | 0.22194 | 0.22195 | 0.22195 | 0.22196 | 0.22196 | 0.22196 | 0.22197 | 0.22197 | 0.22198 | 0.22198 | 0.22198 | 0.22199 | 0.22199 | 0.222 |  | 0% | 0% | 0% | 83321 | [7 empty] | 0.21913 | 0.0028094
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 531 | KERRY FALLS | 33/11 | 1 x 6 |  | 2019-05-05 20:00 | 1.8126 | 1 | 0 | 0 | 1.8126 | 1.8127 | 1.8127 | 1.8127 | 1.8128 | 1.8128 | 1.8128 | 1.8129 | 1.8129 | 1.8129 | 1.813 | 1.813 | 1.813 | 1.8131 |  | 0% | 0% | 11.05% | 83308 | [7 empty] | 2.12 | -0.30736
[6 empty] | 43590.8333 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.20033 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 1.4925 |  |  |  | 2019-04-26 08:00
| 532 | KINLOCHEWE | 33/11 | 1 x 1 |  | No PI | 0.9243 | 1 | 0 | 0 | 0.9243 | 0.92431 | 0.92433 | 0.92435 | 0.92436 | 0.92438 | 0.9244 | 0.92441 | 0.92443 | 0.92445 | 0.92446 | 0.92448 | 0.9245 | 0.92451 |  | 0% | 0% | 0% | 83347 | [7 empty] | 0.9243 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 507 | LETTEREWE | 33/11 | 1 x 0.1 |  | No PI | 0.011238 | 1 | H | H | 0.011238 | 0.011539 | 0.011848 | 0.012165 | 0.012491 | 0.012826 | 0.013169 | 0.013522 | 0.013884 | 0.014256 | 0.014638 | 0.01503 | 0.015433 | 0.015846 |  | 0% | 0% | 0% | 83367 | [7 empty] | 0.011238 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 568 | LOCH GLASCARNOCH | 33/11 | 1 x 0.5 |  | No PI | 0.0028094 | 1 | 0 | 0 | 0.0028094 | 0.0028095 | 0.0028095 | 0.0028096 | 0.0028096 | 0.0028097 | 0.0028097 | 0.0028098 | 0.0028098 | 0.0028099 | 0.0028099 | 0.00281 | 0.00281 | 0.0028101 |  | 0% | 0% | 0% | [8 empty] | 0.0028094 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 556 | LOCHINVER | 33/11 | 1 x 2.5 |  | 2019-04-07 20:09 | 1.5167 | 1 | 0 | 0 | 1.5167 | 1.5167 | 1.5168 | 1.5168 | 1.5168 | 1.5169 | 1.5169 | 1.5169 | 1.5169 | 1.517 | 1.517 | 1.517 | 1.517 | 1.5171 |  | 100% | 74.23% | 0% | 83340 | [7 empty] | 1.56 | -0.043286
[6 empty] | 43562.8396 |  |  |  |  | 0.51977: Committed new connections: |  | 1.5167 | 1.1259 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-07 20:09 | 2019-07-01 20:09 | 0
| 564 | MINOR GRUDIE | 33/11 | 1 x 0.1 |  | No PI | 0.0056188 | 1 | 0 | 0 | 0.0056188 | 0.0056189 | 0.005619 | 0.0056191 | 0.0056192 | 0.0056193 | 0.0056194 | 0.0056195 | 0.0056196 | 0.0056197 | 0.0056198 | 0.0056199 | 0.00562 | 0.0056202 |  | 0% | 0% | 0% | 83364 | [7 empty] | 0.0028094 | 0.0028094
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 549 | ULLAPOOL | 33/11 | 1 x 2.5 |  | 2019-04-07 11:07 | 2.3588 | 1 | 0 | 0 | 2.3588 | 2.3589 | 2.3589 | 2.3589 | 2.359 | 2.359 | 2.3591 | 2.3591 | 2.3592 | 2.3592 | 2.3592 | 2.3593 | 2.3593 | 2.3594 |  | 100% | 78.28% | 0% | 83324 | [7 empty] | 2.33 | 0.028817
[6 empty] | 43562.4632 |  |  |  |  | 0.51977: Committed new connections: |  | 2.3588 | 1.8466 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-07 11:07 | 2019-06-06 17:36 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
HARRIS | 647 |  | 132/33 | 1 x 60 |  | #N/A | #N/A | 1 |  | Diverse | #N/A | 1.6008 | 1.6061 | 1.6114 | 1.6167 | 1.622 | 1.6274 | 1.6328 | 1.6383 | 1.6438 | 1.6493 | 1.6548 | 1.6604 | 1.666 | #N/A | 0% | 0% | 0% | 85652 | [7 empty] | 1.44 | #N/A
Substation was not found in SubstationLoad | [5 empty] | #N/A |  |  |  | Aggregate | 1.5955 | 1.6008 | 1.6061 | 1.6114 | 1.6167 | 1.622 | 1.6274 | 1.6328 | 1.6383 | 1.6438 | 1.6493 | 1.6548 | 1.6604 | 1.666 |  | #N/A | #N/A | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: #N/A |  | #N/A | #N/A | 0
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | #N/A | 1.5688 | 1.5739 | 1.5791 | 1.5843 | 1.5896 | 1.5949 | 1.6002 | 1.6055 | 1.6109 | 1.6163 | 1.6217 | 1.6272 | 1.6327
| 658 | STOCKINISH | 33/11 | 1 x 1 |  | 2019-12-17 20:36 | 0.65201 | 1 | 0 | 0 | 0.65201 | 0.65203 | 0.65204 | 0.65205 | 0.65206 | 0.65207 | 0.65209 | 0.6521 | 0.65211 | 0.65212 | 0.65213 | 0.65214 | 0.65216 | 0.65217 |  | 94.38% | 92.13% | 0% | 85637 | [7 empty] | 0.79 | -0.13799
[6 empty] | 43816.8583 |  |  |  |  | 0.51977: Committed new connections: |  | 0.61538 | 0.60073 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-05-29 19:16 | 2019-06-06 19:19 | 0
| 662 | TARBERT | 33/11 | 2 x 2.5 |  | 2020-02-12 18:44 | 0.94353 | 1 | L | L | 0.94353 | 0.94876 | 0.95401 | 0.9593 | 0.96462 | 0.96996 | 0.97534 | 0.98074 | 0.98618 | 0.99164 | 0.99714 | 1.0027 | 1.0082 | 1.0138 |  | 86.17% | 72.56% | 0% | 85639 | [7 empty] | 1.86 | -0.91647
[6 empty] | 43873.7806 |  |  |  |  | 0.51977: Committed new connections: |  | 0.81302 | 0.68462 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-03 21:04 | 2019-06-13 08:58 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
INVERNESS | 725 |  | 132/33 | 2 x 60 |  | 2019-11-19 16:52 | 63.2434 | 1 |  | Diverse | 63.2434 | 63.2445 | 63.2457 | 63.2468 | 63.248 | 63.2491 | 63.2503 | 63.2515 | 63.2526 | 63.2538 | 63.2549 | 63.2561 | 63.2572 | 63.2584 | Diversity/Losses: 1.121 | 94.15% | 69.67% | 16.62% | 15130 | [7 empty] | 63.2 | 0.043368
|  |  |  | 1 x 90 |  | 43788.7028 |  |  |  | Aggregate | 70.8737 | 70.875 | 70.8763 | 70.8776 | 70.8789 | 70.8802 | 70.8815 | 70.8828 | 70.8841 | 70.8854 | 70.8867 | 70.888 | 70.8893 | 70.8905 |  | 59.5442 | 44.0603 | 10.5116 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 25.5466 |  | 2019-10-31 17:27 | 2019-07-26 11:35 | 2019-09-06 04:53
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 61.9785 | 61.9796 | 61.9808 | 61.9819 | 61.983 | 61.9842 | 61.9853 | 61.9864 | 61.9876 | 61.9887 | 61.9898 | 61.9909 | 61.9921 | 61.9932
| 712 | CULLODEN | 33/11 | 2 x 15 |  | 2019-11-13 17:35 | 9.7425 | 1 | 0 | 0 | 9.7425 | 9.7426 | 9.7428 | 9.743 | 9.7432 | 9.7434 | 9.7435 | 9.7437 | 9.7439 | 9.7441 | 9.7442 | 9.7444 | 9.7446 | 9.7448 |  | 91.23% | 73.96% | 0% | 83504 | [7 empty] | 9.34 | 0.40246
[6 empty] | 43782.7326 |  |  |  |  | 0.51977: Committed new connections: |  | 8.8885 | 7.2057 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-28 17:45 | 2019-06-05 18:01 | 0
| 713 | DALNEIGH | 33/11 | 1 x 24 |  | 2019-12-16 17:36 | 8.9488 | 1 | 0 | 0 | 8.9488 | 8.949 | 8.9492 | 8.9493 | 8.9495 | 8.9497 | 8.9498 | 8.95 | 8.9502 | 8.9503 | 8.9505 | 8.9506 | 8.9508 | 8.951 |  | 90.32% | 74.91% | 0% | 83517 | [7 empty] | 8.88 | 0.068846
[6 empty] | 43815.7333 |  |  |  |  | 0.51977: Committed new connections: |  | 8.083 | 6.7033 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-28 17:39 | 2019-06-05 17:47 | 0
| 761 | ERROGIE | 33/11 | 1 x 1.5 |  | No PI | 0.20228 | 1 | 0 | 0 | 0.20228 | 0.20228 | 0.20228 | 0.20229 | 0.20229 | 0.2023 | 0.2023 | 0.2023 | 0.20231 | 0.20231 | 0.20231 | 0.20232 | 0.20232 | 0.20233 |  | 0% | 0% | 0% | 83532 | [7 empty] | 0.19947 | 0.0028094
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 718 | FOYERS | 33/11 | 1 x 2.5 |  | 2020-01-03 17:07 | 0.37467 | 1 | 0 | 0 | 0.37467 | 0.37467 | 0.37468 | 0.37469 | 0.37469 | 0.3747 | 0.37471 | 0.37471 | 0.37472 | 0.37473 | 0.37474 | 0.37474 | 0.37475 | 0.37476 |  | 80.88% | 76.29% | 0% | 83535 | [7 empty] | 0.36 | 0.014667
[6 empty] | 43833.7132 |  |  |  |  | 0.51977: Committed new connections: |  | 0.30304 | 0.28583 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-30 17:40 | 2019-06-12 18:59 | 0
| 750 | HILTON | 33/11 | 2 x 24 |  | 2019-12-16 17:22 | 11.4281 | 1 | 0 | 0 | 11.4281 | 11.4283 | 11.4285 | 11.4287 | 11.4289 | 11.4291 | 11.4293 | 11.4295 | 11.4297 | 11.4299 | 11.4302 | 11.4304 | 11.4306 | 11.4308 |  | 88.99% | 72.6% | 0% | 83513 | [7 empty] | 11.11 | 0.31807
[6 empty] | 43815.7236 |  |  |  |  | 0.51977: Committed new connections: |  | 10.1694 | 8.2969 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-28 17:28 | 2019-06-05 17:57 | 0
| 757 | INVERARNIE | 33/11 | 1 x 2.5 |  | 2019-09-26 07:30 | 0.6902 | 1 | 0 | 0 | 0.6902 | 0.69021 | 0.69022 | 0.69024 | 0.69025 | 0.69026 | 0.69027 | 0.69029 | 0.6903 | 0.69031 | 0.69032 | 0.69034 | 0.69035 | 0.69036 |  | 100% | 89.59% | 0% | 83528 | [7 empty] | 0.63 | 0.060198
[6 empty] | 43734.3125 |  |  |  |  | 0.51977: Committed new connections: |  | 0.6902 | 0.61832 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-09-26 07:30 | 2019-07-03 13:39 | 0
| 726 | INVERNESS 11 kV | 33/11 | 2 x 10 |  | 2019-11-26 15:05 | 8.389 | 1 | 0 | 0 | 8.389 | 8.3891 | 8.3893 | 8.3895 | 8.3896 | 8.3898 | 8.3899 | 8.3901 | 8.3902 | 8.3904 | 8.3905 | 8.3907 | 8.3908 | 8.391 |  | 82.74% | 66.64% | 0% | 83523 | [7 empty] | 7.32 | 1.069
[6 empty] | 43795.6285 |  |  |  |  | 0.51977: Committed new connections: |  | 6.9414 | 5.5902 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-31 17:21 | 2019-06-12 17:21 | 0
| 735 | RAIGMORE | 33/11 | 2 x 24 |  | 2019-10-31 13:04 | 14.4928 | 1 | 0 | 0 | 14.4928 | 14.493 | 14.4933 | 14.4936 | 14.4938 | 14.4941 | 14.4943 | 14.4946 | 14.4949 | 14.4951 | 14.4954 | 14.4957 | 14.4959 | 14.4962 |  | 100% | 87.36% | 0% | 83508 | [7 empty] | 14.6977 | -0.20492
[6 empty] | 43769.5444 |  |  |  |  | 0.51977: Committed new connections: |  | 14.4928 | 12.661 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-31 13:04 | 2019-06-06 10:21 | 0
| 741 | WATERLOO PLACE | 33/11 | 2 x 23 |  | 2019-11-26 12:21 | 16.6055 | 1 | 0 | 0 | 16.6055 | 16.6058 | 16.6061 | 16.6064 | 16.6067 | 16.607 | 16.6073 | 16.6076 | 16.6079 | 16.6082 | 16.6085 | 16.6088 | 16.6091 | 16.6094 |  | 84.3% | 72.77% | 0% | 83519 | [7 empty] | 14.52 | 2.0855
| ` |  |  |  |  | 43795.5146 |  |  |  |  | 0.51977: Committed new connections: |  | 13.9988 | 12.0843 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-31 11:02 | 2019-06-06 12:20 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
KEITH | 463 |  | 132/33 | 2 x 90 |  | 2020-01-09 17:04 | 38.9798 | 1 |  | Diverse | 38.9798 | 39.0184 | 39.0572 | 39.0962 | 39.1354 | 39.1748 | 39.2144 | 39.2543 | 39.2944 | 39.3347 | 39.3752 | 39.4159 | 39.4569 | 39.498 | Diversity/Losses: 1.379 | 91.56% | 64.88% | -350.2% | [8 empty] | 50.5 | -11.5202
|  |  |  | 2 x 90 |  | 43839.7111 |  |  |  | Aggregate | 53.7349 | 53.788 | 53.8415 | 53.8953 | 53.9493 | 54.0036 | 54.0583 | 54.1132 | 54.1685 | 54.224 | 54.2799 | 54.336 | 54.3925 | 54.4492 |  | 35.6893 | 25.291 | -136.5143 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 13.0068 |  | 2019-04-04 09:03 | 2019-07-02 02:50 | 2020-01-12 23:47
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 38.2002 | 38.238 | 38.276 | 38.3143 | 38.3527 | 38.3913 | 38.4302 | 38.4692 | 38.5085 | 38.548 | 38.5877 | 38.6276 | 38.6677 | 38.7081
| 460 | ABERLOUR | 33/11 | 2 x 5 |  | 2019-11-19 10:38 | 5.0234 | 1 | 0 | 0 | 5.0234 | 5.0235 | 5.0236 | 5.0237 | 5.0238 | 5.0239 | 5.024 | 5.0241 | 5.0241 | 5.0242 | 5.0243 | 5.0244 | 5.0245 | 5.0246 |  | 89.33% | 87.56% | 0% | 83612 | [7 empty] | 4.56 | 0.46341
[6 empty] | 43788.4431 |  |  |  |  | 0.51977: Committed new connections: |  | 4.4876 | 4.3983 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-29 08:45 | 2019-06-13 12:46 | 0
| 462 | BUCKIE | 33/11 | 2 x 24 |  | 2019-11-14 16:30 | 13.081 | 1 | 0 | 0 | 13.081 | 13.0813 | 13.0815 | 13.0817 | 13.082 | 13.0822 | 13.0825 | 13.0827 | 13.0829 | 13.0832 | 13.0834 | 13.0837 | 13.0839 | 13.0841 |  | 0% | 0% | 44.61% | 83645 | [7 empty] | 10.46 | 2.621
[6 empty] | 43783.6875 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 5.8352 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 3.2486 |  |  |  | 2019-06-24 04:00
| 469 | CULLEN | 33/11 | 1 x 15 |  | 2019-12-16 17:04 | 2.6047 | 1 | 0 | 0 | 2.6047 | 2.6047 | 2.6048 | 2.6048 | 2.6049 | 2.6049 | 2.605 | 2.605 | 2.6051 | 2.6051 | 2.6052 | 2.6052 | 2.6053 | 2.6053 |  | 86.18% | 71.66% | 0% | 83641 | [7 empty] | 2.4 | 0.2047
[6 empty] | 43815.7111 |  |  |  |  | 0.51977: Committed new connections: |  | 2.2448 | 1.8666 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-29 17:31 | 2019-06-24 16:57 | 0
| 461 | DUFFTOWN | 33/11 | 2 x 5 |  | 2020-02-28 13:36 | 4.6004 | 1 | 0 | 0 | 4.6004 | 4.6005 | 4.6006 | 4.6006 | 4.6007 | 4.6008 | 4.6009 | 4.601 | 4.6011 | 4.6011 | 4.6012 | 4.6013 | 4.6014 | 4.6015 |  | 94.66% | 88.43% | 0% | 83618 | [7 empty] | 4.72 | -0.11961
[6 empty] | 43889.5667 |  |  |  |  | 0.51977: Committed new connections: |  | 4.3547 | 4.0681 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-05-10 15:50 | 2019-08-20 13:45 | 0
| 869 | HUNTLY | 33/11 | 2 x 15 |  | 2019-12-16 16:30 | 5.9826 | 1 | 0 | 0 | 5.9826 | 5.9827 | 5.9828 | 5.9829 | 5.983 | 5.9831 | 5.9832 | 5.9833 | 5.9834 | 5.9835 | 5.9837 | 5.9838 | 5.9839 | 5.984 |  | 0% | 0% | 20.46% | 83625 | [7 empty] | 5.97 | 0.012565
[6 empty] | 43815.6875 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 1.2241 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0.49223 |  |  |  | 2019-07-01 04:00
| 871 | INSCH | 33/11 | 2 x 7 |  | 2020-01-09 17:30 | 6.2616 | 1 | 0 | 0 | 6.2616 | 6.2617 | 6.2619 | 6.262 | 6.2621 | 6.2622 | 6.2623 | 6.2624 | 6.2625 | 6.2627 | 6.2628 | 6.2629 | 6.263 | 6.2631 |  | 0% | 0% | 3.226% | 83630 | [7 empty] | 6.23 | 0.031622
[6 empty] | 43839.7292 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.20197 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 2 |  |  |  | 2019-07-25 14:30
| 464 | KEITH | 33/11 | 2 x 15 |  | 2019-12-16 16:49 | 6.6533 | 1 | L | L | 6.6533 | 6.6902 | 6.7273 | 6.7646 | 6.8021 | 6.8398 | 6.8777 | 6.9158 | 6.9541 | 6.9926 | 7.0314 | 7.0704 | 7.1095 | 7.1489 |  | 87.92% | 78.94% | 0% | 83602 | [7 empty] | 6.74 | -0.086656
[6 empty] | 43815.7007 |  |  |  |  | 0.51977: Committed new connections: |  | 5.8496 | 5.2523 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-09-30 16:58 | 2019-06-19 20:13 | 0
| 465 | LIMEHILLOCKS | 33/11 | 1 x 2.5 |  | 2019-12-25 12:30 | 1.426 | 1 | 0 | 0 | 1.426 | 1.4261 | 1.4261 | 1.4261 | 1.4262 | 1.4262 | 1.4262 | 1.4262 | 1.4263 | 1.4263 | 1.4263 | 1.4263 | 1.4264 | 1.4264 |  | 0% | 0% | 14.38% | 83651 | [7 empty] | 1.39 | 0.036048
[6 empty] | 43824.5208 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.20506 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0.025123 |  |  |  | 2019-07-25 14:00
| 401 | MARNOCH | 33/11 | 1 x 5 |  | 2020-03-12 11:30 | 2.796 | 1 | L | L | 2.796 | 2.8115 | 2.8271 | 2.8428 | 2.8585 | 2.8744 | 2.8903 | 2.9063 | 2.9224 | 2.9386 | 2.9549 | 2.9713 | 2.9878 | 3.0043 |  | 0% | 0% | 17.88% | 83653 | [7 empty] | 2.7909 | 0.005186
|  |  |  | 1 x 6 |  | 43902.4792 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.49995 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 3.4836 |  |  |  | 2019-08-26 01:30
| 459 | ROTHES | 33/11 | 2 x 5 |  | 2019-11-13 20:21 | 5.3057 | 1 | 0 | 0 | 5.3057 | 5.3058 | 5.3059 | 5.306 | 5.3061 | 5.3062 | 5.3063 | 5.3064 | 5.3065 | 5.3066 | 5.3067 | 5.3068 | 5.3069 | 5.307 |  | 92.49% | 76.53% | 0% | 83605 | [7 empty] | 4.092 | 1.2137
[6 empty] | 43782.8479 |  |  |  |  | 0.51977: Committed new connections: |  | 4.9075 | 4.0607 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-04-04 11:37 | 2019-06-13 08:42 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
KILLIN | 214 |  | 132/33 | 2 x 45 |  | 2020-02-22 16:10 | 31.5833 | 1 |  | Diverse | 31.5833 | 32.1248 | 32.6785 | 33.2447 | 33.8238 | 34.4159 | 35.0216 | 35.6409 | 36.2744 | 36.9224 | 37.5851 | 38.2631 | 38.9565 | 39.6659 | Diversity/Losses: 0.097 | 87.94% | 85.25% | -40.64% | 15630 | [7 empty] | 4 | 27.5833
[6 empty] | 43883.6736 |  |  |  | Aggregate | 3.0577 | 3.1101 | 3.1637 | 3.2185 | 3.2746 | 3.3319 | 3.3905 | 3.4505 | 3.5118 | 3.5746 | 3.6387 | 3.7043 | 3.7715 | 3.8402 |  | 27.7736 | 26.9261 | -12.8357 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 6.3497 |  | 2019-09-02 22:12 | 2019-08-22 23:26 | 2020-02-27 12:00
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 30.9516 | 31.4823 | 32.0249 | 32.5798 | 33.1473 | 33.7276 | 34.3211 | 34.9281 | 35.5489 | 36.1839 | 36.8334 | 37.4978 | 38.1774 | 38.8726
| 269 | CASHLIE | 33/11 | 1 x 1 |  | No PI | 0.20509 | 1 | 0 | 0 | 0.20509 | 0.20509 | 0.20509 | 0.2051 | 0.2051 | 0.20511 | 0.20511 | 0.20511 | 0.20512 | 0.20512 | 0.20512 | 0.20513 | 0.20513 | 0.20514 |  | 0% | 0% | 0% | 83724 | [7 empty] | 0.20509 | 0
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 140 | CHAORACH | 33/11 | 1 x 4 |  | 2019-12-10 08:30 | 0.26588 | 1 | ? | 0 | 0.26588 | 0.26588 | 0.26589 | 0.26589 | 0.2659 | 0.2659 | 0.26591 | 0.26591 | 0.26592 | 0.26592 | 0.26593 | 0.26593 | 0.26594 | 0.26594 |  | 39.23% | 19.3% | 0% | 83751 | [7 empty] | 0.12826 | 0.13762
[6 empty] | 43809.3542 |  |  |  |  | 0.51977: Committed new connections: |  | 0.10431 | 0.051301 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0.26588 |  | 2019-05-25 12:24 | 2019-06-09 19:22 | 0
| 219 | KILLIN TOWN | 33/11 | 1 x 2.5 |  | 2019-11-19 03:02 | 1.2345 | 1 | M | M | 1.2345 | 1.2513 | 1.2684 | 1.2856 | 1.3031 | 1.3208 | 1.3388 | 1.357 | 1.3755 | 1.3942 | 1.4132 | 1.4324 | 1.4519 | 1.4716 |  | 80.84% | 48.5% | 0% | 83715 | [7 empty] | 1.21 | 0.02454
[6 empty] | 43788.1264 |  |  |  |  | 0.51977: Committed new connections: |  | 0.99796 | 0.59878 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 0 |  | 2019-10-29 15:58 | 2019-07-05 15:13 | 0
| 221 | LUBNAIG | 33/11 | 1 x 0.2 |  | No PI | 0.022475 | 1 | 0 | 0 | 0.022475 | 0.022476 | 0.022476 | 0.022476 | 0.022477 | 0.022477 | 0.022478 | 0.022478 | 0.022479 | 0.022479 | 0.022479 | 0.02248 | 0.02248 | 0.022481 |  | 0% | 0% | 0% | 83706 | [7 empty] | 0.019666 | 0.0028094
[6 empty] | No PI |  |  |  |  | 0.51977: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak: |  | 0 | 0 | 0
| 217 | LOCHEARNHEAD | 33/11 | 1 x 4 |  | 2019-12-01 09:00 | 1.3297 | 1 | H | H | 1.3297 | 1.3653 | 1.4019 | 1.4394 | 1.478 | 1.5176 | 1.5582 | 1.6 | 1.6428 | 1.6868 | 1.732 | 1.7784 | 1.8261 | 1.875 |  | 0% | 0% | 24.6% | 83712 | [7 empty] | 1.7 | -0.37031
[6 empty] | 43800.375 |  |  |  |  | 0.51977: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.32716 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 0.51983: Generation at time of peak:; 0.51984: 1.7269 |  |  |  | 2019-07-01 01:30
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
KINLOCHLEVEN | 729 |  | 132/33 | 1 x 45 |  | 2020-02-29 02:14 | 33.6174 | 1 |  | Diverse | 33.6174 | 33.618 | 33.6187 | 33.6193 | 33.6199 | 33.6205 | 33.6211 | 33.6217 | 33.6223 | 33.623 | 33.6236 | 33.6242 | 33.6248 | 33.6254 | Diversity/Losses: 0.096 | 98.34% | 98.45% | 54.11% | 21630 | [7 empty] | 3.4 | 30.2174
[6 empty] | 43890.0931 |  |  |  | Aggregate | 3.239 | 3.2391 | 3.2391 | 3.2392 | 3.2392 | 3.2393 | 3.2394 | 3.2394 | 3.2395 | 3.2395 | 3.2396 | 3.2397 | 3.2397 | 3.2398 |  | 33.0585 | 33.0953 | 18.1888 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 0.51983: Generation at time of BSP peak:; 0.51984: 6.7873 |  | 2019-09-04 05:55 | 2019-08-23 00:14 | 2019-10-30 13:20
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 32.9451 | 32.9457 | 32.9463 | 32.9469 | 32.9475 | 32.9481 | 32.9487 | 32.9493 | 32.9499 | 32.9505 | 32.9511 | 32.9517 | 32.9523 | 32.9529
| 330 | GLENCOE | 33/11 | 1 x 6.9 |  | 2020-02-29 18:50 | 2.0151 | 1 | 0 | 0 | 2.0151 | 2.0152 | 2.0152 | 2.0153 | 2.0153 | 2.0153 | 2.0154 | 2.0154 | 2.0154 | 2.0155 | 2.0155 | 2.0156 | 2.0156 | 2.0156 |  | 90.23% | 67.67% | 0% | 86607 | [7 empty] | 2.11 | -0.09485
[6 empty] | 43890.7847 |  |  |  |  | 32.9451: Committed new connections: |  | 1.8182 | 1.3636 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0 |  | 2019-10-28 18:42 | 2019-08-31 18:53 | 0
| 729 | KINLOCHLEVEN | 33/11 | 2 x 2.5 |  | 2020-02-13 03:06 | 1.2239 | 1 | 0 | 0 | 1.2239 | 1.2239 | 1.2239 | 1.2239 | 1.2239 | 1.224 | 1.224 | 1.224 | 1.224 | 1.2241 | 1.2241 | 1.2241 | 1.2241 | 1.2241 |  | 90.19% | 72.65% | 0% | 86601 | 86602 | [6 empty] | 1.31 | -0.086149
[6 empty] | 43874.1292 |  |  |  |  | 32.9451: Committed new connections: |  | 1.1038 | 0.88907 | 0 | 66.6% | 33.3% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0.29962 |  | 2019-10-29 03:36 | 2019-06-18 16:26 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
KINTORE | 887 |  | 132/33 | 2 x 60 |  | 2019-11-13 17:20 | 65.1126 | 1 |  | Diverse | 65.1126 | 65.4901 | 65.5037 | 65.5174 | 65.5311 | 65.5449 | 65.5588 | 65.5727 | 65.5867 | 65.6008 | 65.6149 | 65.6292 | 65.6435 | 65.6578 | Diversity/Losses: 1.003 | 94.06% | 70.37% | -32.84% | 15830 | [7 empty] | 67.2 | -2.0874
|  |  |  | 1 x 90 |  | 43782.7222 |  |  |  | Aggregate | 65.3379 | 65.7167 | 65.7303 | 65.744 | 65.7578 | 65.7717 | 65.7856 | 65.7996 | 65.8136 | 65.8277 | 65.8419 | 65.8562 | 65.8706 | 65.885 |  | 61.2419 | 45.8177 | -21.3819 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 32.9487: Generation at time of BSP peak:; 6.7873 32.9493: 3.1477 |  | 2019-10-29 17:38 | 2019-06-10 17:31 | 2020-02-19 08:08
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 63.8103 | 64.1803 | 64.1936 | 64.207 | 64.2205 | 64.234 | 64.2476 | 64.2612 | 64.275 | 64.2888 | 64.3026 | 64.3166 | 64.3306 | 64.3447
| 810 | BANCHORY | 33/11 | 2 x 14 |  | 2019-11-19 16:40 | 9.2841 | 1 | 0 | 0 | 9.2841 | 9.2843 | 9.2845 | 9.2846 | 9.2848 | 9.285 | 9.2851 | 9.2853 | 9.2855 | 9.2856 | 9.2858 | 9.286 | 9.2862 | 9.2863 |  | 88.16% | 73.48% | 0% | 83818 | [7 empty] | 9.44 | -0.15588
[6 empty] | 43788.6944 |  |  |  |  | 32.9451: Committed new connections: |  | 8.1852 | 6.8216 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0 |  | 2019-10-30 17:44 | 2019-06-13 16:47 | 0
| 856 | FYVIE | 33/11 | 1 x 6 |  | 2019-10-31 07:13 | 4.3666 | 1 | 0 | 0 | 4.3666 | 4.3667 | 4.3668 | 4.3669 | 4.367 | 4.367 | 4.3671 | 4.3672 | 4.3673 | 4.3674 | 4.3674 | 4.3675 | 4.3676 | 4.3677 |  | 100% | 85.52% | 0% | 83852 | [7 empty] | 3.9 | 0.46665
|  |  |  | 1 x 8 |  | 43769.3007 |  |  |  |  | 32.9451: Committed new connections: |  | 4.3666 | 3.7344 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 1.3898 |  | 2019-10-31 07:13 | 2019-08-14 07:41 | 0
| 875 | INVERURIE | 33/11 | 2 x 15 |  | 2019-12-16 16:54 | 13.6242 | 1 | 0 | 0 | 13.6242 | 13.6245 | 13.6247 | 13.625 | 13.6252 | 13.6255 | 13.6257 | 13.6259 | 13.6262 | 13.6264 | 13.6267 | 13.6269 | 13.6272 | 13.6274 |  | 82.84% | 73.26% | 0% | 83837 | [7 empty] | 13.77 | -0.14579
|  |  |  | 1 x 17 |  | 43815.7042 |  |  |  |  | 32.9451: Committed new connections: |  | 11.2862 | 9.9812 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0.0092796 |  | 2019-04-02 09:09 | 2019-06-29 21:48 | 0
| 881 | KEMNAY | 33/11 | 2 x 15 |  | 2020-01-13 17:17 | 3.803 | 1 | 0 | 0 | 3.803 | 3.8031 | 3.8031 | 3.8032 | 3.8033 | 3.8034 | 3.8034 | 3.8035 | 3.8036 | 3.8036 | 3.8037 | 3.8038 | 3.8038 | 3.8039 |  | 83.56% | 71.82% | 0% | 83830 | [7 empty] | 2.12 | 1.683
[6 empty] | 43843.7201 |  |  |  |  | 32.9451: Committed new connections: |  | 3.1779 | 2.7313 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0 |  | 2019-10-31 16:54 | 2019-08-28 17:41 | 0
| 903 | METHLICK | 33/11 | 1 x 5 |  | 2019-12-24 16:30 | 1.976 | 1 | 0 | 0 | 1.976 | 2.3413 | 2.3413 | 2.3413 | 2.3414 | 2.3414 | 2.3414 | 2.3415 | 2.3415 | 2.3415 | 2.3416 | 2.3416 | 2.3417 | 2.3417 |  | 0% | 0% | 14.04% | 83849 | [7 empty] | 1.907 | 0.068929
|  |  |  | 1 x 6.3 |  | 43823.6875 |  |  |  |  | 32.9451: Committed new connections:; 32.9457: 0.425 |  | Manual Calculation | Manual Calculation | 0.27741 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 2.651 |  |  |  | 2019-08-06 02:30
| 907 | MIDMAR | 33/11 | 1 x 5 |  | 2020-03-23 12:29 | 2.6134 | 1 | 0 | 0 | 2.6134 | 2.6134 | 2.6135 | 2.6135 | 2.6136 | 2.6136 | 2.6137 | 2.6137 | 2.6138 | 2.6138 | 2.6138 | 2.6139 | 2.6139 | 2.614 |  | 85.44% | 77.07% | 0% | 83825 | [7 empty] | 2.5991 | 0.014303
[6 empty] | 43913.5201 |  |  |  |  | 32.9451: Committed new connections: |  | 2.233 | 2.0141 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0.42617 |  | 2019-04-04 11:40 | 2019-06-13 15:26 | 0
| 921 | OLDMELDRUM | 33/11 | 2 x 8 |  | 2020-01-13 18:30 | 4.5255 | 1 | 0 | 0 | 4.5255 | 4.5256 | 4.5257 | 4.5258 | 4.5258 | 4.5259 | 4.526 | 4.5261 | 4.5262 | 4.5262 | 4.5263 | 4.5264 | 4.5265 | 4.5266 |  | 0% | 0% | 17.91% | 83845 | [7 empty] | 4.516 | 0.0094702
[6 empty] | 43843.7708 |  |  |  |  | 32.9451: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.81053 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 2.6728 |  |  |  | 2019-04-22 03:00
| 923 | PARK | 33/11 | 1 x 6 |  | 2019-11-11 08:03 | 2.2405 | 1 | L | L | 2.2405 | 2.2529 | 2.2654 | 2.278 | 2.2906 | 2.3033 | 2.3161 | 2.3289 | 2.3418 | 2.3548 | 2.3678 | 2.3809 | 2.3941 | 2.4074 |  | 85.71% | 67.35% | 0% | 85103 | [7 empty] | 2.3678 | -0.1273
[6 empty] | 43780.3354 |  |  |  |  | 32.9451: Committed new connections: |  | 1.9204 | 1.5089 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0 |  | 2019-04-03 09:03 | 2019-06-24 15:10 | 0
| 941 | SKENE | 33/11 | 2 x 30 |  | 2020-01-10 08:12 | 13.52 | 1 | 0 | 0 | 13.52 | 13.5202 | 13.5205 | 13.5207 | 13.521 | 13.5212 | 13.5215 | 13.5217 | 13.522 | 13.5222 | 13.5225 | 13.5227 | 13.523 | 13.5232 |  | 86.51% | 74.44% | 0% | 83836 | [7 empty] | 13.77 | -0.25
[6 empty] | 43840.3417 |  |  |  |  | 32.9451: Committed new connections: |  | 11.696 | 10.064 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0 |  | 2019-10-30 08:47 | 2019-06-13 12:07 | 0
| 962 | TORRYBURN | 33/11 | 2 x 24 |  | 2019-11-19 16:30 | 9.3845 | 1 | 0 | 0 | 9.3845 | 9.3847 | 9.3849 | 9.385 | 9.3852 | 9.3854 | 9.3856 | 9.3857 | 9.3859 | 9.3861 | 9.3862 | 9.3864 | 9.3866 | 9.3868 |  | 0% | 0% | 25.31% | 83801 | 83807 | [6 empty] | 9.07 | 0.31452
[6 empty] | 43788.6875 |  |  |  |  | 32.9451: Committed new connections: |  | Manual Calculation | Manual Calculation | 2.375 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 32.9487: Generation at time of peak:; 6.7873 32.9493: 0.020469 |  |  |  | 2019-07-07 04:30
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
LAIRG | 534 |  | 132/33 | 1 x 90 |  | 2019-08-14 09:06 | 5.2609 | 1 |  | Diverse | 5.2609 | 5.261 | 5.2611 | 5.2612 | 5.2613 | 5.2614 | 5.2615 | 5.2616 | 5.2617 | 5.2618 | 5.2619 | 5.262 | 5.2621 | 5.2622 | Diversity/Losses: 0.366 | 88.99% | 100% | -981.9% | 16230 | [7 empty] | 1.9 | 3.3609
[6 empty] | 43691.3792 |  |  |  | Aggregate | 1.9236 | 1.9237 | 1.9237 | 1.9237 | 1.9238 | 1.9238 | 1.9238 | 1.9239 | 1.9239 | 1.9239 | 1.924 | 1.924 | 1.924 | 1.9241 |  | 4.6819 | 5.2609 | -51.6585 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 32.9487: Generation at time of BSP peak:; 6.7873 32.9493: 0 |  | 2019-09-26 18:31 | 2019-08-14 09:06 | 2019-12-13 08:44
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 5.1557 | 5.1558 | 5.1559 | 5.156 | 5.1561 | 5.1562 | 5.1563 | 5.1564 | 5.1565 | 5.1566 | 5.1567 | 5.1568 | 5.1569 | 5.157
| 534 | LAIRG | 33/11 | 1 x 2.5 |  | 2019-12-24 20:06 | 1.2241 | 1 | ? | 0 | 1.2241 | 1.2241 | 1.2241 | 1.2241 | 1.2242 | 1.2242 | 1.2242 | 1.2242 | 1.2243 | 1.2243 | 1.2243 | 1.2243 | 1.2243 | 1.2244 |  | 86.49% | 63.4% | 0% | 83909 | [7 empty] | 1.13
[6 empty] | 43823.8375 |  |  |  |  | 5.1557: Committed new connections: |  | 1.0587 | 0.77604 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0 |  | 2019-10-31 20:04 | 2019-06-04 20:15 | 0
| 540 | TORBOLL | 33/11 | 1 x 0.1 |  | No PI | 0.016856 | 1 | 0 | 0 | 0.016856 | 0.016857 | 0.016857 | 0.016857 | 0.016858 | 0.016858 | 0.016858 | 0.016859 | 0.016859 | 0.016859 | 0.01686 | 0.01686 | 0.01686 | 0.01686 |  | 0% | 0% | 0% | 83902 | [7 empty] | 0.016856 | 0
[6 empty] | No PI |  |  |  |  | 5.1557: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak: |  | 0 | 0 | 0
| 548 | TRESSADY | 33/11 | 1 x 0.5 |  | No PI | 0.68269 | 1 | 0 | 0 | 0.68269 | 0.6827 | 0.68271 | 0.68272 | 0.68274 | 0.68275 | 0.68276 | 0.68277 | 0.68279 | 0.6828 | 0.68281 | 0.68282 | 0.68284 | 0.68285 |  | 0% | 0% | 0% | 83905 | [7 empty] | 0.6855 | -0.0028094
[6 empty] | No PI |  |  |  |  | 5.1557: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak: |  | 0 | 0 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
ARDMORE | 665 |  | 33 |  |  | 2019-12-11 13:22 | 32.2136 | 1 |  | Diverse | 32.2136 | 32.2568 | 32.3003 | 32.344 | 32.388 | 32.4322 | 32.4766 | 32.5213 | 32.5663 | 32.6114 | 32.6569 | 32.7025 | 32.7485 | 32.7947 | Diversity/Losses: 0.278 | 89.9% | 78.51% | -70.56% | 84001 | [7 empty] | 6.87 | 25.3436
[6 empty] | 43810.5569 |  |  |  | Aggregate | 8.9685 | 8.9805 | 8.9927 | 9.0048 | 9.0171 | 9.0294 | 9.0417 | 9.0542 | 9.0667 | 9.0793 | 9.0919 | 9.1046 | 9.1174 | 9.1303 |  | 28.9588 | 25.2914 | -22.7299 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.1563: Generation at time of BSP peak:; 0 5.1564: 37.594 |  | 2019-09-02 11:02 | 2019-07-16 16:20 | 2019-11-24 00:29
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 31.5693 | 31.6117 | 31.6543 | 31.6972 | 31.7402 | 31.7836 | 31.8271 | 31.8709 | 31.9149 | 31.9592 | 32.0037 | 32.0485 | 32.0935 | 32.1388
| 671 | AIRD | 33/11 | 2 x 8 |  | 2020-01-14 13:09 | 2.4928 | 1 | 0 | 0 | 2.4928 | 2.4929 | 2.4929 | 2.4929 | 2.493 | 2.493 | 2.4931 | 2.4931 | 2.4932 | 2.4932 | 2.4933 | 2.4933 | 2.4934 | 2.4934 |  | 86.06% | 71.67% | 0% | 84009 | 84010 | [6 empty] | 2.58 | -0.087191
[6 empty] | 43844.5479 |  |  |  |  | 5.1557: Committed new connections: |  | 2.1453 | 1.7866 | 0 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0 |  | 2019-04-09 07:38 | 2019-06-13 07:22 | 0
| 653 | CLACHAN | 33/11 | 1 x 2.5 |  | 2020-02-24 18:52 | 2.1501 | 1 | L | L | 2.1501 | 2.162 | 2.174 | 2.186 | 2.1981 | 2.2103 | 2.2225 | 2.2349 | 2.2472 | 2.2597 | 2.2722 | 2.2848 | 2.2975 | 2.3102 |  | 90.37% | 75.41% | 0% | 84013 | [7 empty] | 2.16 | -0.0099451
[6 empty] | 43885.7861 |  |  |  |  | 5.1557: Committed new connections: |  | 1.943 | 1.6213 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0 |  | 2019-04-01 18:43 | 2019-06-14 08:36 | 0
| 644 | DRIMORE | 33/11 | 1 x 2.5 |  | 2020-03-05 19:07 | 1.0403 | 1 | 0 | 0 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0403 | 1.0404 | 1.0404 | 1.0404 | 1.0404 | 1.0404 | 1.0405 | 1.0405 | 1.0405 |  | 87.42% | 72.08% | 0% | 84005 | [7 empty] | 1.07 | -0.02975
[6 empty] | 43895.7965 |  |  |  |  | 5.1557: Committed new connections: |  | 0.90936 | 0.74981 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0 |  | 2019-04-04 12:47 | 2019-08-30 09:32 | 0
| 665 | LOCH CARNAN | 33/11 | 3 x 6.5 |  | No PI | 0.50569 | 1 | 0 | 0 | 0.50569 | 0.5057 | 0.50571 | 0.50572 | 0.50573 | 0.50574 | 0.50575 | 0.50576 | 0.50577 | 0.50578 | 0.50579 | 0.5058 | 0.5058 | 0.50581 |  | 0% | 0% | 0% | 84018 | [7 empty] | 0.50288 | 0.0028094
[6 empty] | No PI |  |  |  |  | 5.1557: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak: |  | 0 | 0 | 0
| 660 | POLLACHAR | 33/11 | 2 x 3.9 |  | 2020-02-16 21:08 | 2.7797 | 1 | 0 | 0 | 2.7797 | 2.7798 | 2.7798 | 2.7799 | 2.7799 | 2.78 | 2.78 | 2.7801 | 2.7801 | 2.7802 | 2.7802 | 2.7803 | 2.7803 | 2.7804 |  | 94.59% | 73% | 0% | 84017 | [7 empty] | 2.3493 | 0.43036
[6 empty] | 43877.8806 |  |  |  |  | 5.1557: Committed new connections: |  | 2.6292 | 2.0293 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0.8757 |  | 2019-04-07 20:05 | 2019-06-06 18:47 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
LUNANHEAD | 81 |  | 132/33 | 1 x 90 |  | 2019-11-19 16:41 | 31.4618 | 1 |  | Diverse | 31.4618 | 31.5454 | 31.6313 | 31.7194 | 31.81 | 31.9029 | 31.9983 | 32.0962 | 32.1968 | 32.3 | 32.406 | 32.5148 | 32.6265 | 32.7412 | Diversity/Losses: 1.026 | 90.91% | 72.2% | 27.69% | 17130 | [7 empty] | 62.2 | -30.7382
|  |  |  | 1 x 120 |  | 43788.6951 |  |  |  | Aggregate | 32.2655 | 32.3513 | 32.4393 | 32.5298 | 32.6226 | 32.7179 | 32.8157 | 32.9161 | 33.0193 | 33.1251 | 33.2338 | 33.3454 | 33.46 | 33.5776 |  | 28.602 | 22.7161 | 8.7107 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.1563: Generation at time of BSP peak:; 0 5.1564: 0.045434 |  | 2019-10-30 17:14 | 2019-06-24 16:52 | 2019-06-30 03:19
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 30.8325 | 30.9145 | 30.9987 | 31.0851 | 31.1738 | 31.2648 | 31.3583 | 31.4543 | 31.5528 | 31.654 | 31.7579 | 31.8645 | 31.974 | 32.0863
| 89 | FRIOCKHEIM | 33/11 | 1 x 5 |  | 2019-12-18 18:12 | 3.1827 | 1 | H | H | 3.1827 | 3.2679 | 3.3555 | 3.4454 | 3.5377 | 3.6324 | 3.7297 | 3.8296 | 3.9322 | 4.0376 | 4.1457 | 4.2568 | 4.3708 | 4.4879 |  | 89.74% | 73.57% | 0% | 84113 | [7 empty] | 4.403 | -1.2203
[6 empty] | 43817.7583 |  |  |  |  | 5.1557: Committed new connections: |  | 2.856 | 2.3415 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0.95909 |  | 2019-10-30 17:07 | 2019-08-22 17:46 | 0
| 87 | INVERARITY | 33/11 | 1 x 2.5 |  | 2020-03-05 18:12 | 0.6 | 1 | 0 | 0 | 0.6 | 0.60001 | 0.60002 | 0.60003 | 0.60004 | 0.60005 | 0.60007 | 0.60008 | 0.60009 | 0.6001 | 0.60011 | 0.60012 | 0.60013 | 0.60014 |  | 93.33% | 60% | 0% | 84112 | [7 empty] | 0.65 | -0.05
[6 empty] | 43895.7583 |  |  |  |  | 5.1557: Committed new connections: |  | 0.56 | 0.36 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0 |  | 2019-04-16 18:07 | 2019-06-05 18:02 | 0
| 83 | LOCHSIDE | 33/11 | 2 x 24 |  | 2019-11-19 16:36 | 14.9459 | 1 | 0 | 0 | 14.9459 | 14.9462 | 14.9465 | 14.9467 | 14.947 | 14.9473 | 14.9475 | 14.9478 | 14.9481 | 14.9484 | 14.9486 | 14.9489 | 14.9492 | 14.9495 |  | 96.04% | 82.51% | 0% | 84105 | [7 empty] | 14.24 | 0.70591
[6 empty] | 43788.6917 |  |  |  |  | 5.1557: Committed new connections: |  | 14.3542 | 12.3315 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0 |  | 2019-04-03 16:49 | 2019-06-24 16:32 | 0
| 82 | LUNANHEAD | 33/11 | 2 x 15 |  | 2019-12-09 16:30 | 7.2255 | 1 | 0 | 0 | 7.2255 | 7.2257 | 7.2258 | 7.2259 | 7.2261 | 7.2262 | 7.2263 | 7.2265 | 7.2266 | 7.2267 | 7.2269 | 7.227 | 7.2271 | 7.2273 |  | 0% | 0% | 15.91% | 84101 | [7 empty] | 7.22 | 0.0055454
[6 empty] | 43808.6875 |  |  |  |  | 5.1557: Committed new connections: |  | Manual Calculation | Manual Calculation | 1.1496 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 2.9537 |  |  |  | 2019-07-24 03:30
| 84 | MARYTON | 33/11 | 2 x 15 |  | 2019-11-19 17:00 | 6.3113 | 1 | 0 | 0 | 6.3113 | 6.3114 | 6.3116 | 6.3117 | 6.3118 | 6.3119 | 6.312 | 6.3121 | 6.3122 | 6.3124 | 6.3125 | 6.3126 | 6.3127 | 6.3128 |  | 0% | 0% | 15.54% | 84109 | [7 empty] | 6.3 | 0.011327
[6 empty] | 43788.7083 |  |  |  |  | 5.1557: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.98049 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.1563: Generation at time of peak:; 0 5.1564: 0.013027 |  |  |  | 2019-08-11 04:00
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
LYNDHURST | 11 |  | 132/33 | 2 x 60 |  | 2019-11-19 16:28 | 22.7396 | 1 |  | Diverse | 22.7396 | 22.74 | 22.7404 | 22.7408 | 22.7413 | 22.7417 | 22.7421 | 22.7425 | 22.7429 | 22.7433 | 22.7438 | 22.7442 | 22.7446 | 22.745 | Diversity/Losses: 1.106 | 86.53% | 71.69% | 0% | 17230 | [7 empty] | 25 | -2.2604
[6 empty] | 43788.6861 |  |  |  | Aggregate | 25.1398 | 25.1402 | 25.1407 | 25.1412 | 25.1416 | 25.1421 | 25.1425 | 25.143 | 25.1435 | 25.1439 | 25.1444 | 25.1448 | 25.1453 | 25.1457 |  | 19.6758 | 16.3021 |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.1563: Generation at time of BSP peak:; 0 5.1564: 0 |  | 2019-10-28 16:58 | 2019-08-27 17:13
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 22.2848 | 22.2852 | 22.2856 | 22.286 | 22.2864 | 22.2868 | 22.2873 | 22.2877 | 22.2881 | 22.2885 | 22.2889 | 22.2893 | 22.2897 | 22.2901
| 13 | LOCHEE | 33/11 | 2 x 23 |  | 2020-01-27 16:59 | 6.3366 | 1 | 0 | 0 | 6.3366 | 6.3367 | 6.3368 | 6.3369 | 6.3371 | 6.3372 | 6.3373 | 6.3374 | 6.3375 | 6.3376 | 6.3377 | 6.3379 | 6.338 | 6.3381 |  | 72.91% | 60% | 0% | 84218 | [7 empty] | 5.36 | 0.97659
[6 empty] | 43857.7076 |  |  |  |  | 22.2848: Committed new connections: |  | 4.6201 | 3.802 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-10-29 17:10 | 2019-06-13 12:00 | 0
| 12 | LYNDHURST | 33/11 | 2 x 10 |  | 2020-01-15 16:47 | 4.563 | 1 | 0 | 0 | 4.563 | 4.563 | 4.5631 | 4.5632 | 4.5633 | 4.5634 | 4.5635 | 4.5635 | 4.5636 | 4.5637 | 4.5638 | 4.5639 | 4.564 | 4.564 |  | 92.38% | 81.63% | 0% | 84203 | [7 empty] | 5.27 | -0.70705
[6 empty] | 43845.6993 |  |  |  |  | 22.2848: Committed new connections: |  | 4.2153 | 3.7247 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-04-04 12:14 | 2019-07-09 11:35 | 0
| 14 | MACALPINE ROAD | 33/11 | 1 x 15 & 1 x 21 |  | 2020-01-13 16:59 | 6.8448 | 1 | 0 | 0 | 6.8448 | 6.8449 | 6.8451 | 6.8452 | 6.8453 | 6.8454 | 6.8456 | 6.8457 | 6.8458 | 6.8459 | 6.8461 | 6.8462 | 6.8463 | 6.8464 |  | 87.59% | 75.41% | 0% | 84207 | [7 empty] | 7.19 | -0.34519
[6 empty] | 43843.7076 |  |  |  |  | 22.2848: Committed new connections: |  | 5.9952 | 5.1617 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-10-28 17:25 | 2019-06-05 12:04 | 0
| 15 | WEST KIRKTON | 33/11 | 2 x 23 |  | 2019-12-18 17:01 | 7.3954 | 1 | 0 | 0 | 7.3954 | 7.3956 | 7.3957 | 7.3958 | 7.396 | 7.3961 | 7.3962 | 7.3964 | 7.3965 | 7.3966 | 7.3968 | 7.3969 | 7.397 | 7.3972 |  | 89.61% | 70.82% | 0% | 84214 | [7 empty] | 7.46 | -0.064572
[6 empty] | 43817.709 |  |  |  |  | 22.2848: Committed new connections: |  | 6.6272 | 5.2373 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-10-30 17:05 | 2019-06-24 17:28 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
MACDUFF | 405 |  | 132/33 | 2 x 90 |  | 2019-11-27 17:33 | 24.7291 | 1 |  | Diverse | 24.7291 | 25.0161 | 25.3108 | 25.6133 | 25.924 | 26.243 | 26.5705 | 26.9068 | 27.2521 | 27.6066 | 27.9707 | 28.3444 | 28.7282 | 29.1222 | Diversity/Losses: 0.957 | 94.76% | 92.21% | -99.02% | 17330 | [7 empty] | 21.8 | 2.9291
[6 empty] | 43796.7312 |  |  |  | Aggregate | 23.6713 | 23.9461 | 24.2281 | 24.5178 | 24.8152 | 25.1205 | 25.434 | 25.7559 | 26.0864 | 26.4258 | 26.7743 | 27.132 | 27.4994 | 27.8766 |  | 23.4327 | 22.8024 | -24.4862 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 22.2873: Generation at time of BSP peak:; 0 22.2877: 8.571 |  | 2019-09-04 12:09 | 2019-08-13 17:52 | 2020-03-02 23:34
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 24.2345 | 24.5158 | 24.8046 | 25.1011 | 25.4055 | 25.7181 | 26.0391 | 26.3687 | 26.7071 | 27.0545 | 27.4112 | 27.7775 | 28.1536 | 28.5398
| 406 | MACDUFF NEW | 33/11 | 2 x 12.5 |  | 2020-03-25 17:00 | 7.3738 | 1 | H | H | 7.3738 | 7.5713 | 7.7741 | 7.9824 | 8.1962 | 8.4157 | 8.6412 | 8.8727 | 9.1103 | 9.3544 | 9.605 | 9.8622 | 10.1264 | 10.3977 |  | 0% | 0% | 20% | 83207 | [7 empty] | 13.064 | -5.6902
[6 empty] | 43915.7083 |  |  |  |  | 22.2848: Committed new connections: |  | Manual Calculation | Manual Calculation | 1.4748 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak: |  |  |  | No PI, assumed 20% of max
| 435 | PORTSOY | 33/11 | 1 x 5 |  | 2019-09-11 12:30 | 2.8729 | 1 | H | H | 2.8729 | 2.9499 | 3.0289 | 3.11 | 3.1933 | 3.2789 | 3.3667 | 3.4569 | 3.5495 | 3.6446 | 3.7422 | 3.8424 | 3.9454 | 4.0511 |  | 0% | 0% | 13.84% | 83211 | [7 empty] | 2.5796 | 0.29332
[6 empty] | 43719.5208 |  |  |  |  | 22.2848: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.39765 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0.98447 |  |  |  | 2019-08-10 02:30
| 964 | TURRIFF | 33/11 | 2 x 15 |  | 2019-12-17 12:14 | 13.4247 | 1 | 0 | 0 | 13.4247 | 13.4249 | 13.4251 | 13.4254 | 13.4256 | 13.4259 | 13.4261 | 13.4264 | 13.4266 | 13.4269 | 13.4271 | 13.4273 | 13.4276 | 13.4278 |  | 91.35% | 80.13% | 0% | 83214 | [7 empty] | 10.02 | 3.4047
[6 empty] | 43816.5097 |  |  |  |  | 22.2848: Committed new connections: |  | 12.2641 | 10.7577 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 4.6065 |  | 2019-10-30 17:42 | 2019-08-26 08:05 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
MILTON OF CRAIGIE | 51 |  | 132/33 | 2 x 60 |  | 2019-11-21 17:17 | 45.5121 | 1 |  | Diverse | 45.5121 | 45.513 | 45.5138 | 45.5146 | 45.5155 | 45.5163 | 45.5171 | 45.518 | 45.5188 | 45.5196 | 45.5205 | 45.5213 | 45.5221 | 45.5229 | Diversity/Losses: 1.029 | 94.87% | 78.63% | 17.64% | 17430 | [7 empty] | 47.9 | -2.3879
[6 empty] | 43790.7201 |  |  |  | Aggregate | 46.8108 | 46.8116 | 46.8125 | 46.8133 | 46.8142 | 46.815 | 46.8159 | 46.8168 | 46.8176 | 46.8185 | 46.8193 | 46.8202 | 46.821 | 46.8219 |  | 43.178 | 35.787 | 8.0301 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 22.2873: Generation at time of BSP peak:; 0 22.2877: 0.13996 |  | 2019-10-21 17:35 | 2019-08-09 17:06 | 2019-07-13 05:23
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 44.6019 | 44.6027 | 44.6035 | 44.6043 | 44.6052 | 44.606 | 44.6068 | 44.6076 | 44.6084 | 44.6092 | 44.61 | 44.6109 | 44.6117 | 44.6125
| 55 | ASHLUDIE | 33/11 | 2 x 10 |  | 2019-04-03 17:52 | 7.0845 | 1 | 0 | 0 | 7.0845 | 7.0846 | 7.0848 | 7.0849 | 7.085 | 7.0851 | 7.0853 | 7.0854 | 7.0855 | 7.0857 | 7.0858 | 7.0859 | 7.0861 | 7.0862 |  | 0% | 82.81% | 0% | 84331 | [7 empty] | 9.12 | -2.0355
[6 empty] | 43558.7444 |  |  |  |  | 22.2848: Committed new connections: |  | #VALUE! | 5.867 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | #VALUE! | 2019-06-24 17:21 | 0
| 56 | BALDOVIE | 33/11 | 2 x 24 |  | 2019-11-19 16:55 | 11.9461 | 1 | 0 | 0 | 11.9461 | 11.9464 | 11.9466 | 11.9468 | 11.947 | 11.9472 | 11.9474 | 11.9477 | 11.9479 | 11.9481 | 11.9483 | 11.9485 | 11.9488 | 11.949 |  | 97.49% | 86.28% | 0% | 84318 | [7 empty] | 11.98 | -0.033861
[6 empty] | 43788.7049 |  |  |  |  | 22.2848: Committed new connections: |  | 11.6468 | 10.3071 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-10-28 17:15 | 2019-07-09 13:26 | 0
| 57 | BROUGHTY FERRY | 33/11 | 2 x 10 |  | 2019-12-05 17:24 | 7.0873 | 1 | 0 | 0 | 7.0873 | 7.0874 | 7.0875 | 7.0877 | 7.0878 | 7.0879 | 7.0881 | 7.0882 | 7.0883 | 7.0884 | 7.0886 | 7.0887 | 7.0888 | 7.089 |  | 87.9% | 72.84% | 0% | 84327 | [7 empty] | 7.16 | -0.07272
[6 empty] | 43804.725 |  |  |  |  | 22.2848: Committed new connections: |  | 6.23 | 5.1621 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-10-30 18:21 | 2019-06-13 16:54 | 0
| 58 | EDZELL STREET | 33/11 | 1 x 10 |  | 2019-12-01 17:25 | 2.8251 | 1 | 0 | 0 | 2.8251 | 2.8251 | 2.8252 | 2.8252 | 2.8253 | 2.8253 | 2.8254 | 2.8254 | 2.8255 | 2.8255 | 2.8256 | 2.8256 | 2.8257 | 2.8257 |  | 88.44% | 69.92% | 0% | 84322 | [7 empty] | 2.86 | -0.034922
[6 empty] | 43800.7257 |  |  |  |  | 22.2848: Committed new connections: |  | 2.4985 | 1.9753 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-10-28 17:35 | 2019-06-13 17:44 | 0
| 54 | LONGHAUGH | 33/11 | 2 x 23 |  | 2019-11-19 17:00 | 8.062 | 1 | 0 | 0 | 8.062 | 8.0621 | 8.0623 | 8.0624 | 8.0626 | 8.0627 | 8.0629 | 8.063 | 8.0632 | 8.0633 | 8.0635 | 8.0636 | 8.0637 | 8.0639 |  | 0% | 0% | 25.9% | 84304 | [7 empty] | 8.34 | -0.27802
[6 empty] | 43788.7083 |  |  |  |  | 22.2848: Committed new connections: |  | Manual Calculation | Manual Calculation | 2.0882 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0.4957 |  |  |  | 2019-06-30 05:30
| 52 | MILTON OF CRAIGIE | 33/11 | 1 x 24 |  | 2020-01-28 23:39 | 3.4468 | 1 | 0 | 0 | 3.4468 | 3.4468 | 3.4469 | 3.4469 | 3.447 | 3.4471 | 3.4471 | 3.4472 | 3.4473 | 3.4473 | 3.4474 | 3.4474 | 3.4475 | 3.4476 |  | 36.93% | 45.99% | 0% | 84314 | [7 empty] | 7.8601 | -4.4133
|  |  |  | 1 x 15 |  | 43858.9854 |  |  |  |  | 22.2848: Committed new connections: |  | 1.273 | 1.5853 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-04-01 12:32 | 2019-06-26 03:41 | 0
| 53 | OLD CRAIGIE ROAD | 33/11 | 2 x 10 |  | 2019-12-18 18:31 | 6.359 | 1 | 0 | 0 | 6.359 | 6.3592 | 6.3593 | 6.3594 | 6.3595 | 6.3596 | 6.3597 | 6.3598 | 6.36 | 6.3601 | 6.3602 | 6.3603 | 6.3604 | 6.3605 |  | 91.83% | 77.96% | 0% | 84310 | [7 empty] | 6.2738 | 0.085249
[6 empty] | 43817.7715 |  |  |  |  | 22.2848: Committed new connections: |  | 5.8398 | 4.9577 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 22.2873: Generation at time of peak:; 0 22.2877: 0 |  | 2019-10-30 18:44 | 2019-06-01 23:55 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
MYBSTER | 586 |  | 132/33 | 2 x 120 |  | 2019-12-16 17:02 | 11.946 | 1 |  | Diverse | 11.946 | 11.9462 | 11.9464 | 11.9466 | 11.9468 | 11.9471 | 11.9473 | 11.9475 | 11.9477 | 11.9479 | 11.9481 | 11.9484 | 11.9486 | 11.9488 | Diversity/Losses: 0.902 | 88.53% | 68.26% | -1378% | 17830 | [7 empty] | 10.3 | 1.646
|  |  |  | 2 x 120 |  | 43815.7097 |  |  |  | Aggregate | 10.7761 | 10.7763 | 10.7765 | 10.7767 | 10.7769 | 10.7771 | 10.7773 | 10.7775 | 10.7777 | 10.7779 | 10.7781 | 10.7783 | 10.7785 | 10.7787 |  | 10.5757 | 8.1541 | -164.576 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 10.7773: Generation at time of BSP peak:; 10.7775: 0.32348 |  | 2019-10-29 17:35 | 2019-06-17 17:22 | 2019-11-14 14:47
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 11.707 | 11.7073 | 11.7075 | 11.7077 | 11.7079 | 11.7081 | 11.7083 | 11.7085 | 11.7088 | 11.709 | 11.7092 | 11.7094 | 11.7096 | 11.7098
| 584 | LATHERON | 33/11 | 1 x 4 |  | 2019-12-24 20:04 | 1.9452 | 1 | 0 | 0 | 1.9452 | 1.9453 | 1.9453 | 1.9454 | 1.9454 | 1.9454 | 1.9455 | 1.9455 | 1.9455 | 1.9456 | 1.9456 | 1.9456 | 1.9457 | 1.9457 |  | 90.69% | 71.57% | 0% | 84427 | [7 empty] | 1.96 | -0.014753
[6 empty] | 43823.8361 |  |  |  |  | 10.7761: Committed new connections: |  | 1.7641 | 1.3922 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-29 17:34 | 2019-06-06 11:42 | 0
| 594 | WICK | 33/11 | 2 x 24 |  | 2019-12-16 16:56 | 8.8309 | 1 | 0 | 0 | 8.8309 | 8.8311 | 8.8312 | 8.8314 | 8.8315 | 8.8317 | 8.8319 | 8.832 | 8.8322 | 8.8323 | 8.8325 | 8.8327 | 8.8328 | 8.833 |  | 87.68% | 70.47% | 0% | 84401 | [7 empty] | 8.44 | 0.3909
[6 empty] | 43815.7056 |  |  |  |  | 10.7761: Committed new connections: |  | 7.743 | 6.2232 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-28 17:35 | 2019-06-13 17:23 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
NAIRN | 733 |  | 132/33 | 2 x 60 |  | 2019-12-16 17:50 | 28.8495 | 1 |  | Diverse | 28.8495 | 28.9294 | 29.01 | 29.0911 | 29.1729 | 29.2553 | 29.3383 | 29.422 | 29.5063 | 29.5912 | 29.6768 | 29.7631 | 29.85 | 29.9376 | Diversity/Losses: 0.948 | 91.83% | 78.42% | 27.45% | [8 empty] | 31.3 | -2.4505
[6 empty] | 43815.7431 |  |  |  | Aggregate | 27.3626 | 27.4384 | 27.5148 | 27.5918 | 27.6693 | 27.7475 | 27.8262 | 27.9056 | 27.9855 | 28.0661 | 28.1473 | 28.2291 | 28.3115 | 28.3946 |  | 26.492 | 22.6244 | 7.9196 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 10.7773: Generation at time of BSP peak:; 10.7775: 0.18982 |  | 2019-10-28 16:49 | 2019-06-05 16:11 | 2019-07-25 02:10
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 28.2725 | 28.3508 | 28.4298 | 28.5093 | 28.5894 | 28.6702 | 28.7515 | 28.8335 | 28.9161 | 28.9994 | 29.0833 | 29.1678 | 29.253 | 29.3388
| 779 | ARDERSIER | 33/11 | 2 x 5 |  | 2020-02-13 07:20 | 2.6848 | 1 | 0 | 0 | 2.6848 | 2.6848 | 2.6849 | 2.6849 | 2.685 | 2.685 | 2.6851 | 2.6851 | 2.6852 | 2.6852 | 2.6853 | 2.6853 | 2.6854 | 2.6854 |  | 70.06% | 50.1% | 0% | 84526 | [7 empty] | 2.2 | 0.48478
[6 empty] | 43874.3056 |  |  |  |  | 10.7761: Committed new connections: |  | 1.881 | 1.3452 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-04-03 11:41 | 2019-06-05 16:38 | 0
| 752 | DALCROSS | 33/11 | 2 x 15 |  | 2020-03-06 08:30 | 3.1072 | 1 | 0 | 0 | 3.1072 | 3.1072 | 3.1073 | 3.1073 | 3.1074 | 3.1075 | 3.1075 | 3.1076 | 3.1076 | 3.1077 | 3.1077 | 3.1078 | 3.1079 | 3.1079 |  | 0% | 0% | 3.593% | 84530 | [7 empty] | 7.77 | -4.6628
[6 empty] | 43896.3542 |  |  |  |  | 10.7761: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.11163 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0.54062 |  |  |  | 2019-05-14 00:30
| 452 | FORRES | 33/11 | 2 x 15 |  | 2019-12-16 17:55 | 10.1202 | 1 | L | L | 10.1202 | 10.1763 | 10.2327 | 10.2894 | 10.3464 | 10.4037 | 10.4614 | 10.5194 | 10.5777 | 10.6363 | 10.6952 | 10.7545 | 10.8141 | 10.874 |  | 78.44% | 64.67% | 0% | 84504 | [7 empty] | 9.57 | 0.5502
[6 empty] | 43815.7465 |  |  |  |  | 10.7761: Committed new connections: |  | 7.9386 | 6.5448 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-31 17:55 | 2019-06-13 17:54 | 0
| 703 | LETHEN | 33/11 | 1 x 2.5 |  | 2019-11-10 11:24 | 1.429 | 1 | M | M | 1.429 | 1.4484 | 1.4681 | 1.4881 | 1.5083 | 1.5288 | 1.5496 | 1.5707 | 1.5921 | 1.6138 | 1.6357 | 1.658 | 1.6805 | 1.7034 |  | 94.92% | 73.96% | 0% | 84502 | [7 empty] | 1.54 | -0.11105
[6 empty] | 43779.475 |  |  |  |  | 10.7761: Committed new connections: |  | 1.3564 | 1.0568 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-30 17:02 | 2019-06-05 17:01 | 0
| 723 | NAIRN CENTRAL | 33/11 | 2 x 15 |  | 2020-02-12 11:06 | 10.0215 | 1 | 0 | 0 | 10.0215 | 10.0217 | 10.0219 | 10.022 | 10.0222 | 10.0224 | 10.0226 | 10.0228 | 10.0229 | 10.0231 | 10.0233 | 10.0235 | 10.0237 | 10.0239 |  | 84.79% | 75.6% | 0% | 84516 | [7 empty] | 9.5 | 0.52149
[6 empty] | 43873.4625 |  |  |  |  | 10.7761: Committed new connections: |  | 8.4974 | 7.5764 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-31 16:50 | 2019-06-13 16:55 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
PERSLEY | 925 |  | 132/33 | 2 x 90 |  | 2019-11-19 16:57 | 38.3589 | 1 |  | Diverse | 38.3589 | 38.3596 | 38.3603 | 38.361 | 38.3617 | 38.3624 | 38.3631 | 38.3638 | 38.3645 | 38.3652 | 38.3659 | 38.3666 | 38.3673 | 38.368 | Diversity/Losses: 1.152 | 92.93% | 79.95% | 29.07% | 18430 | [7 empty] | 43.1 | -4.7411
[6 empty] | 43788.7063 |  |  |  | Aggregate | 44.1776 | 44.1784 | 44.1792 | 44.18 | 44.1808 | 44.1816 | 44.1824 | 44.1832 | 44.184 | 44.1848 | 44.1857 | 44.1865 | 44.1873 | 44.1881 |  | 35.6483 | 30.6666 | 11.1502 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 10.7773: Generation at time of BSP peak:; 10.7775: 0 |  | 2019-04-03 10:35 | 2019-06-13 12:10 | 2019-08-11 05:38
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 37.5918 | 37.5924 | 37.5931 | 37.5938 | 37.5945 | 37.5952 | 37.5959 | 37.5966 | 37.5972 | 37.5979 | 37.5986 | 37.5993 | 37.6 | 37.6007
| 814 | BRIDGE OF DON | 33/11 | 2 x 24 |  | 2020-02-28 09:29 | 13.8439 | 1 | 0 | 0 | 13.8439 | 13.8442 | 13.8445 | 13.8447 | 13.845 | 13.8452 | 13.8455 | 13.8457 | 13.846 | 13.8462 | 13.8465 | 13.8467 | 13.847 | 13.8472 |  | 96.05% | 83.02% | 0% | 84607 | [7 empty] | 14.12 | -0.27606
[6 empty] | 43889.3951 |  |  |  |  | 10.7761: Committed new connections: |  | 13.2969 | 11.4938 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-04-02 11:57 | 2019-06-13 09:09 | 0
| 865 | HAUDAGAIN | 33/11 | 2 x 23 |  | 2020-02-25 18:49 | 6.0733 | 1 | 0 | 0 | 6.0733 | 6.0735 | 6.0736 | 6.0737 | 6.0738 | 6.0739 | 6.074 | 6.0741 | 6.0742 | 6.0743 | 6.0745 | 6.0746 | 6.0747 | 6.0748 |  | 90.81% | 74.08% | 0% | 84619 | [7 empty] | 5.88 | 0.19334
[6 empty] | 43886.784 |  |  |  |  | 10.7761: Committed new connections: |  | 5.5152 | 4.4994 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-28 18:11 | 2019-06-13 18:37 | 0
| 956 | ST MACHAR | 33/11 | 2 x 24 |  | 2019-11-01 09:48 | 7.8143 | 1 | 0 | 0 | 7.8143 | 7.8145 | 7.8146 | 7.8148 | 7.8149 | 7.815 | 7.8152 | 7.8153 | 7.8155 | 7.8156 | 7.8158 | 7.8159 | 7.816 | 7.8162 |  | 97.57% | 82% | 0% | 84603 | [7 empty] | 7.36 | 0.45433
[6 empty] | 43770.4083 |  |  |  |  | 10.7761: Committed new connections: |  | 7.6246 | 6.4078 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-28 18:11 | 2019-07-11 09:02 | 0
| 947 | STONEYWOOD T1&T2 | 33/11 | 2 x 24 |  | 2019-04-03 09:13 | 9.4006 | 1 | 0 | 0 | 9.4006 | 9.4007 | 9.4009 | 9.4011 | 9.4012 | 9.4014 | 9.4016 | 9.4018 | 9.4019 | 9.4021 | 9.4023 | 9.4024 | 9.4026 | 9.4028 |  | 100% | 88.96% | 0% | 82401 | [7 empty] | 10.59 | -1.1894
[6 empty] | 43558.384 |  |  |  |  | 10.7761: Committed new connections: |  | 9.4006 | 8.3628 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-04-03 09:13 | 2019-06-13 08:58 | 0
| 982 | WHITESTRIPES | 33/11 | 2 x 15 |  | 2020-02-04 11:11 | 7.0454 | 1 | 0 | 0 | 7.0454 | 7.0455 | 7.0457 | 7.0458 | 7.0459 | 7.0461 | 7.0462 | 7.0463 | 7.0464 | 7.0466 | 7.0467 | 7.0468 | 7.047 | 7.0471 |  | 86.68% | 74.56% | 0% | 84611 | [7 empty] | 6.77 | 0.27541
[6 empty] | 43865.466 |  |  |  |  | 10.7761: Committed new connections: |  | 6.107 | 5.253 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-29 17:16 | 2019-06-13 17:31 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
PETERHEAD GRANGE | 927 |  | 132/33 | 2 x 45 |  | 2020-03-27 08:26 | 11.4765 | 1 |  | Diverse | 11.4765 | 11.4767 | 11.4769 | 11.4771 | 11.4773 | 11.4775 | 11.4778 | 11.478 | 11.4782 | 11.4784 | 11.4786 | 11.4788 | 11.479 | 11.4792 | Diversity/Losses: 2.184 | 48.77% | 62.74% | -299.5% | 18330 | [7 empty] | 24.4 | -12.9235
[6 empty] | 43917.3514 |  |  |  | Aggregate | 25.0659 | 25.0664 | 25.0669 | 25.0673 | 25.0678 | 25.0682 | 25.0687 | 25.0691 | 25.0696 | 25.0701 | 25.0705 | 25.071 | 25.0714 | 25.0719 |  | 5.5971 | 7.2002 | -34.3752 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 10.7773: Generation at time of BSP peak:; 10.7775: 0.22826 |  | 2019-05-16 23:55 | 2019-07-21 | 2019-10-29 00:47
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 11.247 | 11.2472 | 11.2474 | 11.2476 | 11.2478 | 11.248 | 11.2482 | 11.2484 | 11.2486 | 11.2488 | 11.249 | 11.2492 | 11.2494 | 11.2496
| 929 | PHEAD NORTH ST | 33/11 | 2 x 24 |  | 2020-02-17 16:48 | 12.0117 | 1 | 0 | 0 | 12.0117 | 12.012 | 12.0122 | 12.0124 | 12.0126 | 12.0128 | 12.0131 | 12.0133 | 12.0135 | 12.0137 | 12.0139 | 12.0142 | 12.0144 | 12.0146 |  | 81.74% | 78.58% | 0% | 84702 | [7 empty] | 13.2177
[6 empty] | 43878.7 |  |  |  |  | 10.7761: Committed new connections: |  | 9.8181 | 9.4386 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0 |  | 2019-10-18 13:08 | 2019-08-21 14:18 | 0
| 928 | PETERHEAD GRANGE 11kV | 33/11 | 2 x 24 |  | 2019-12-16 17:03 | 13.0542 | 1 | 0 | 0 | 13.0542 | 13.0544 | 13.0547 | 13.0549 | 13.0552 | 13.0554 | 13.0556 | 13.0559 | 13.0561 | 13.0563 | 13.0566 | 13.0568 | 13.0571 | 13.0573 |  | 89.58% | 78.89% | 0% | 84700 | [7 empty] | 13.4297 | -0.3755
[6 empty] | 43815.7104 |  |  |  |  | 10.7761: Committed new connections: |  | 11.6938 | 10.2982 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.7773: Generation at time of peak:; 10.7775: 0.15311 |  | 2019-10-30 17:05 | 2019-06-24 17:00 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
PETERHEAD SHELL | 926 |  | 132/11 | 1 x 15 |  | 2019-04-01 07:14 | 5.8218 | 1 |  | Diverse | 5.8218 | 5.8219 | 5.8221 | 5.8222 | 5.8223 | 5.8224 | 5.8225 | 5.8226 | 5.8227 | 5.8228 | 5.8229 | 5.823 | 5.8231 | 5.8232 | Diversity/Losses: 1.669 | 100% | -16.03% | -91.85% | 21150 | [7 empty] | 8.6 | -2.7782
[6 empty] | 43556.3014 |  |  |  | Aggregate | 9.7156 | 9.7158 | 9.7159 | 9.7161 | 9.7163 | 9.7165 | 9.7166 | 9.7168 | 9.717 | 9.7172 | 9.7174 | 9.7175 | 9.7177 | 9.7179 |  | 5.8218 | -0.93333 | -5.3476 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 10.7773: Generation at time of BSP peak:; 10.7775: 0 |  | 2019-04-01 07:14 | 2019-06-12 06:03 | 2019-04-14 10:15
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 5.7054 | 5.7055 | 5.7056 | 5.7057 | 5.7058 | 5.7059 | 5.706 | 5.7061 | 5.7062 | 5.7063 | 5.7064 | 5.7065 | 5.7067 | 5.7068
| 812 | BODDAM | 33/11 | 1 x 15 |  | 2020-02-17 10:23 | 7.0607 | 1 | 0 | 0 | 7.0607 | 7.0609 | 7.061 | 7.0611 | 7.0613 | 7.0614 | 7.0615 | 7.0616 | 7.0618 | 7.0619 | 7.062 | 7.0622 | 7.0623 | 7.0624 |  | 88.48% | 92.61% | 0% | 84801 | [7 empty] | 6.18 | 0.88074
[6 empty] | 43878.4326 |  |  |  |  | 5.7054: Committed new connections: |  | 6.2472 | 6.5389 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-10-30 09:57 | 2019-06-13 12:09 | 0
| 926 | PETERHEAD SHELL | 33/11 | 1 x 15 |  | 2020-01-18 16:30 | 2.6548 | 1 | 0 | 0 | 2.6548 | 2.6549 | 2.6549 | 2.655 | 2.655 | 2.6551 | 2.6551 | 2.6552 | 2.6552 | 2.6553 | 2.6553 | 2.6554 | 2.6554 | 2.6555 |  | 0% | 0% | 0% | 21150 | [7 empty] | 2.4618 | 0.19307
[6 empty] | 43848.6875 |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
PORT ANN | 301 |  | 132/33 | 2 x 30 |  | 2019-10-29 03:34 | 12.8411 | 1 |  | Diverse | 12.8411 | 12.8652 | 12.8895 | 12.9142 | 12.9392 | 12.9646 | 12.9902 | 13.0162 | 13.0426 | 13.0693 | 13.0964 | 13.1238 | 13.1516 | 13.1798 | Diversity/Losses: 2.256 | 100% | 66.39% | -279.1% | 18530 | [7 empty] | 21.5 | -8.6589
[6 empty] | 43767.1486 |  |  |  | Aggregate | 28.974 | 29.0283 | 29.0832 | 29.1389 | 29.1953 | 29.2525 | 29.3104 | 29.3691 | 29.4286 | 29.4889 | 29.55 | 29.6118 | 29.6745 | 29.7381 |  | 12.8411 | 8.5258 | -35.8396 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: 1.4667 |  | 2019-10-29 03:34 | 2019-07-14 21:19 | 2020-01-22 09:37
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 12.5843 | 12.6079 | 12.6317 | 12.6559 | 12.6804 | 12.7053 | 12.7304 | 12.7559 | 12.7818 | 12.8079 | 12.8345 | 12.8613 | 12.8886 | 12.9162
| 319 | AIRIGH-NA-BRODAIG | 33/11 | 1 x 0.315 |  | No PI | 0.075854 | 1 | M | M | 0.075854 | 0.076886 | 0.077932 | 0.078992 | 0.080067 | 0.081156 | 0.08226 | 0.08338 | 0.084514 | 0.085664 | 0.086829 | 0.08801 | 0.089208 | 0.090421 |  | 0% | 0% | 0% | 84942 | [7 empty] | 0.075854 | 0
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
| 313 | BOWMORE | 33/11 | 1 x 8 |  | 2019-11-18 10:05 | 3.536 | 1 | 0 | 0 | 3.536 | 3.5361 | 3.5361 | 3.5362 | 3.5363 | 3.5363 | 3.5364 | 3.5365 | 3.5365 | 3.5366 | 3.5366 | 3.5367 | 3.5368 | 3.5368 |  | 78.73% | 60.18% | 0% | 84928 | [7 empty] | 2.82 | 0.716
[6 empty] | 43787.4201 |  |  |  |  | 5.7054: Committed new connections: |  | 2.784 | 2.128 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-16 09:08 | 2019-06-05 09:17 | 0
| 305 | CRINAN | 33/11 | 1 x 1 |  | 2019-04-17 03:36 | 0.8984 | 1 | 0 | 0 | 0.8984 | 0.89841 | 0.89843 | 0.89845 | 0.89846 | 0.89848 | 0.8985 | 0.89851 | 0.89853 | 0.89855 | 0.89856 | 0.89858 | 0.89859 | 0.89861 |  | 100% | 83.32% | 0% | 84915 | [7 empty] | 0.73385 | 0.16455
[6 empty] | 43572.15 |  |  |  |  | 5.7054: Committed new connections: |  | 0.8984 | 0.74859 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-17 03:36 | 2019-08-19 00:59 | 0
| 326 | CROMALT | 33/11 | 1 x 2.5 |  | 2019-11-18 18:47 | 0.88 | 1 | ? | 0 | 0.88 | 0.88002 | 0.88003 | 0.88005 | 0.88006 | 0.88008 | 0.8801 | 0.88011 | 0.88013 | 0.88014 | 0.88016 | 0.88018 | 0.88019 | 0.88021 |  | 90% | 61.82% | 0% | 84952 | [7 empty] | 0.91 | -0.03
[6 empty] | 43787.7826 |  |  |  |  | 5.7054: Committed new connections: |  | 0.792 | 0.544 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-03 13:20 | 2019-08-31 21:18 | 0
| 309 | INVERNEIL | 33/11 | 1 x 2.5 |  | 2020-03-30 03:35 | 0.75071 | 1 | L | L | 0.75071 | 0.75487 | 0.75905 | 0.76326 | 0.76749 | 0.77174 | 0.77602 | 0.78032 | 0.78464 | 0.78899 | 0.79336 | 0.79776 | 0.80218 | 0.80663 |  | 75.65% | 76.12% | 0% | 84907 | [7 empty] | 1.58 | -0.82929
[6 empty] | 43920.1493 |  |  |  |  | 5.7054: Committed new connections: |  | 0.56791 | 0.5714 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-09-03 09:34 | 2019-08-16 15:58 | 0
| 308 | LOCHGILPHEAD | 33/11 | 2 x 24 |  | 2019-04-05 03:37 | 17.9556 | 1 | 0 | 0 | 17.9556 | 17.9559 | 17.9563 | 17.9566 | 17.9569 | 17.9572 | 17.9576 | 17.9579 | 17.9582 | 17.9586 | 17.9589 | 17.9592 | 17.9595 | 17.9599 |  | 100% | 77.35% | 0% | 84911 | [7 empty] | 8.91 | 9.0456
[6 empty] | 43560.1507 |  |  |  |  | 5.7054: Committed new connections: |  | 17.9556 | 13.8892 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 9.648 |  | 2019-04-05 03:37 | 2019-08-29 21:19 | 0
| 339 | LUSSAGIVEN | 33/11 | 1 x 0.1 |  | No PI | 0.036522 | 1 | 0 | 0 | 0.036522 | 0.036523 | 0.036524 | 0.036524 | 0.036525 | 0.036526 | 0.036526 | 0.036527 | 0.036528 | 0.036528 | 0.036529 | 0.03653 | 0.03653 | 0.036531 |  | 0% | 0% | 0% | 84918 | [7 empty] | 0.036522 | 0
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
| 334 | PORT ASKAIG | 33/11 | 1 x 2.5 |  | 2020-02-24 13:24 | 1.2953 | 1 | 0 | 0 | 1.2953 | 1.2953 | 1.2953 | 1.2953 | 1.2954 | 1.2954 | 1.2954 | 1.2954 | 1.2954 | 1.2955 | 1.2955 | 1.2955 | 1.2955 | 1.2956 |  | 90.66% | 74.07% | 0% | 84925 | [7 empty] | 1.1584 | 0.13681
[6 empty] | 43885.5583 |  |  |  |  | 5.7054: Committed new connections: |  | 1.1743 | 0.95935 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-02 09:58 | 2019-08-15 17:23 | 0
| 331 | PORT ELLEN | 33/11 | 1 x 4 |  | 2020-02-27 18:48 | 3.467 | 1 | M | M | 3.467 | 3.5142 | 3.562 | 3.6105 | 3.6596 | 3.7094 | 3.7599 | 3.811 | 3.8629 | 3.9154 | 3.9687 | 4.0227 | 4.0774 | 4.1329 |  | 88.03% | 79.23% | 0% | 84930 | [7 empty] | 3.0771 | 0.3899
[6 empty] | 43888.7833 |  |  |  |  | 5.7054: Committed new connections: |  | 3.052 | 2.7468 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-10 08:22 | 2019-06-19 08:54 | 0
| 397 | STONEFIELD | 33/11 | 1 x 0.315 |  | No PI | 0.053379 | 1 | H | H | 0.053379 | 0.054809 | 0.056277 | 0.057784 | 0.059332 | 0.060922 | 0.062554 | 0.064229 | 0.06595 | 0.067716 | 0.06953 | 0.071393 | 0.073305 | 0.075269 |  | 0% | 0% | 0% | 84955 | [7 empty] | 0.053379 | 0
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
| 341 | TARBERT JURA | 33/11 | 1 x 0.15 |  | No PI | 0.025285 | 1 | 0 | 0 | 0.025285 | 0.025285 | 0.025286 | 0.025286 | 0.025287 | 0.025287 | 0.025287 | 0.025288 | 0.025288 | 0.025289 | 0.025289 | 0.02529 | 0.02529 | 0.025291 |  | 0% | 0% | 0% | 84921 | [7 empty] | 0.025285 | 0
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
QUOICH | 748 |  | 132/33 | 1 x 30 |  | #N/A | #N/A | 1 |  | Diverse | #N/A | 0.10234 | 0.10234 | 0.10234 | 0.10235 | 0.10235 | 0.10235 | 0.10235 | 0.10235 | 0.10236 | 0.10236 | 0.10236 | 0.10236 | 0.10236 | #N/A | 0% | 0% | 0% | 18650 | [7 empty] | 0.12 | #N/A
Substation was not found in SubstationLoad | [5 empty] | #N/A |  |  |  | Aggregate | 0.10234 | 0.10234 | 0.10234 | 0.10234 | 0.10235 | 0.10235 | 0.10235 | 0.10235 | 0.10235 | 0.10236 | 0.10236 | 0.10236 | 0.10236 | 0.10236 |  | #N/A | #N/A |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: #N/A |  | #N/A | #N/A
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | #N/A | 0.10029 | 0.1003 | 0.1003 | 0.1003 | 0.1003 | 0.1003 | 0.1003 | 0.10031 | 0.10031 | 0.10031 | 0.10031 | 0.10031 | 0.10032
| 748 | QUOICH PRIMARY | 33/11 | 1 x 4 |  | 2020-02-12 07:00 | 0.10234 | 1 | ? | 0 | 0.10234 | 0.10234 | 0.10234 | 0.10234 | 0.10235 | 0.10235 | 0.10235 | 0.10235 | 0.10235 | 0.10236 | 0.10236 | 0.10236 | 0.10236 | 0.10236 |  | 0% | 0% | 20% | 82824 | [7 empty] | 0.11989 | -0.017548
[6 empty] | 43873.2917 |  |  |  |  | 5.7054: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.020468 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  |  |  | No PI, assumed 20% of max
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW)
RANNOCH | 261 |  | 132/33 | 2 x 90 |  | 2020-03-17 22:06 | 66.0342 | 1 |  | Diverse | 66.0342 | 66.0354 | 66.0366 | 66.0378 | 66.039 | 66.0402 | 66.0414 | 66.0427 | 66.0439 | 66.0451 | 66.0463 | 66.0475 | 66.0487 | 66.0499 | Diversity/Losses: 0.024 | 87.16% | 83.04% | -62.69% | 18731 | [7 empty] | 2
[6 empty] | 43907.9208 |  |  |  | Aggregate | 1.5867 | 1.5867 | 1.5867 | 1.5868 | 1.5868 | 1.5868 | 1.5869 | 1.5869 | 1.5869 | 1.5869 | 1.587 | 1.587 | 1.587 | 1.5871 |  | 57.5529 | 54.8369 | -41.3937 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: 4.622 |  | 2019-10-27 15:08 | 2019-08-07 18:56 | 2019-11-17 20:55
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 64.7135 | 64.7147 | 64.7159 | 64.7171 | 64.7183 | 64.7194 | 64.7206 | 64.7218 | 64.723 | 64.7242 | 64.7253 | 64.7265 | 64.7277 | 64.7289
| 343 | BLACKMOUNT | 33/11 | 1 x 0.05 |  | No PI | 0.039332 | 1 | 0 | 0 | 0.039332 | 0.039332 | 0.039333 | 0.039334 | 0.039335 | 0.039335 | 0.039336 | 0.039337 | 0.039337 | 0.039338 | 0.039339 | 0.03934 | 0.03934 | 0.039341 |  | 0% | 0% | 0% | 85007 | [7 empty] | 0.039332 | 0
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
| 274 | BRIDGE OF GAUR | 33/11 | 1 x 0.5 |  | No PI | 0.33432 | 1 | 0 | 0 | 0.33432 | 0.33433 | 0.33433 | 0.33434 | 0.33434 | 0.33435 | 0.33436 | 0.33436 | 0.33437 | 0.33437 | 0.33438 | 0.33439 | 0.33439 | 0.3344 |  | 0% | 0% | 0% | 85020 | [7 empty] | 0.3287 | 0.0056188
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
| 345 | GLENETIVE | 33/11 | 1 x 0.3 |  | No PI | 0.087092 | 1 | 0 | 0 | 0.087092 | 0.087093 | 0.087095 | 0.087096 | 0.087098 | 0.0871 | 0.087101 | 0.087103 | 0.087104 | 0.087106 | 0.087108 | 0.087109 | 0.087111 | 0.087112 |  | 0% | 0% | 0% | 85002 | [7 empty] | 0.087092 | 0
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
| 218 | TYNDRUM | 33/11 | 1 x 2.5 |  | 2019-05-25 19:04 | 1.1259 | 1 | 0 | 0 | 1.1259 | 1.126 | 1.126 | 1.126 | 1.126 | 1.126 | 1.1261 | 1.1261 | 1.1261 | 1.1261 | 1.1261 | 1.1262 | 1.1262 | 1.1262 |  | 100% | 58.69% | 0% | 85011 | [7 empty] | 1.71 | -0.58406
[6 empty] | 43610.7944 |  |  |  |  | 5.7054: Committed new connections: |  | 1.1259 | 0.66081 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-05-25 19:04 | 2019-07-09 07:11 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
REDMOSS | 934 |  | 132/33 | 2 x 60 |  | 2019-11-19 08:37 | 43.1586 | 1 |  | Diverse | 43.1586 | 43.2435 | 43.329 | 43.4149 | 43.5012 | 43.5881 | 43.6754 | 43.7632 | 43.8514 | 43.9402 | 44.0295 | 44.1192 | 44.2094 | 44.3002 | Diversity/Losses: 1.175 | 95.73% | 93.08% | 3.482% | 18830 | [7 empty] | 45.7 | -2.5414
[6 empty] | 43788.359 |  |  |  | Aggregate | 50.7214 | 50.8213 | 50.9217 | 51.0226 | 51.1241 | 51.2261 | 51.3288 | 51.4319 | 51.5357 | 51.64 | 51.7449 | 51.8504 | 51.9564 | 52.0631 |  | 41.315 | 40.1714 | 1.5029 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: 0.51071 |  | 2019-10-30 08:24 | 2019-06-05 10:59 | 2020-01-29 03:54
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 42.2954 | 42.3787 | 42.4624 | 42.5466 | 42.6312 | 42.7163 | 42.8019 | 42.8879 | 42.9744 | 43.0614 | 43.1489 | 43.2368 | 43.3253 | 43.4142
| 832 | CRAIGINCHES | 33/11 | 2 x 30 |  | 2019-05-08 11:25 | 15.36 | 1 | 0 | 0 | 15.36 | 15.3603 | 15.3606 | 15.3608 | 15.3611 | 15.3614 | 15.3617 | 15.362 | 15.3622 | 15.3625 | 15.3628 | 15.3631 | 15.3634 | 15.3636 |  | 100% | 93.83% | 0% | 85102 | [7 empty] | 12.71 | 2.65
[6 empty] | 43593.4757 |  |  |  |  | 5.7054: Committed new connections: |  | 15.36 | 14.412 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-05-08 11:25 | 2019-06-05 11:24 | 0
| 882 | KINCORTH | 33/11 | 2 x 12.5 |  | 2020-01-14 17:10 | 7.0859 | 1 | 0 | 0 | 7.0859 | 7.086 | 7.0862 | 7.0863 | 7.0864 | 7.0865 | 7.0867 | 7.0868 | 7.0869 | 7.0871 | 7.0872 | 7.0873 | 7.0875 | 7.0876 |  | 93.22% | 83.73% | 0% | 85120 | [7 empty] | 7.4462 | -0.3603
[6 empty] | 43844.7153 |  |  |  |  | 5.7054: Committed new connections: |  | 6.6055 | 5.9329 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-10-30 17:00 | 2019-06-12 13:09 | 0
| 915 | NEWTONHILL | 33/11 | 2 x 15 |  | 2019-12-11 17:30 | 10.3687 | 1 | 0 | 0 | 10.3687 | 10.3689 | 10.3691 | 10.3693 | 10.3695 | 10.3697 | 10.3699 | 10.3701 | 10.3702 | 10.3704 | 10.3706 | 10.3708 | 10.371 | 10.3712 |  | 0% | 0% | 28.91% | 85107 | [7 empty] | 10.2803 | 0.088419
[6 empty] | 43810.7292 |  |  |  |  | 5.7054: Committed new connections: |  | Manual Calculation | Manual Calculation | 2.9975 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 2.1837 |  |  |  | 2019-08-26 03:30
| 935 | REDMOSS | 33/11 | 2 x 40 |  | 2020-01-14 08:08 | 17.9068 | 1 | L | L | 17.9068 | 18.006 | 18.1058 | 18.2062 | 18.3071 | 18.4085 | 18.5105 | 18.6131 | 18.7163 | 18.82 | 18.9243 | 19.0291 | 19.1346 | 19.2406 |  | 91.01% | 81.01% | 0% | 85117 | [7 empty] | 18.5575 | -0.65073
[6 empty] | 43844.3389 |  |  |  |  | 5.7054: Committed new connections: |  | 16.2972 | 14.5065 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-10-30 08:24 | 2019-06-13 09:23 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
SHETLAND |  |  | 33 |  |  |  |  | 1 |  | Diverse | #VALUE! | 38.3404 | 38.4158 | 38.4926 | 38.5708 | 38.6504 | 38.7314 | 38.8139 | 38.8979 | 38.9835 | 39.0706 | 39.1592 | 39.2496 | 39.3415 | #VALUE! | 0% | 0% | 0% | [9 empty] | #VALUE!
No PI or No Data | [9 empty] | Aggregate | 38.2662 | 38.3404 | 38.4158 | 38.4926 | 38.5708 | 38.6504 | 38.7314 | 38.8139 | 38.8979 | 38.9835 | 39.0706 | 39.1592 | 39.2496 | 39.3415 |  | #VALUE! | No Data |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak: |  | #VALUE! | Missing Data
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | #VALUE! | 37.5736 | 37.6475 | 37.7228 | 37.7994 | 37.8774 | 37.9568 | 38.0376 | 38.12 | 38.2038 | 38.2891 | 38.3761 | 38.4646 | 38.5547
| 699 | BRAE | 33/11 | 1 x 6 |  | 2019-12-18 06:04 | 2.9583 | 1 | 0 | 0 | 2.9583 | 2.9583 | 2.9584 | 2.9584 | 2.9585 | 2.9585 | 2.9586 | 2.9586 | 2.9587 | 2.9587 | 2.9588 | 2.9589 | 2.9589 | 2.959 |  | 88.99% | 65.09% | 0% | 89930 | [7 empty] | 2.94 | 0.018262
[6 empty] | 43817.2528 |  |  |  |  | 5.7054: Committed new connections: |  | 2.6327 | 1.9257 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-01 06:37 | 2019-06-01 06:03 | 0
| 692 | FIRTH | 33/11 | 1 x 6 |  | 2019-04-11 06:32 | 1.2562 | 1 | 0 | 0 | 1.2562 | 1.2562 | 1.2562 | 1.2562 | 1.2563 | 1.2563 | 1.2563 | 1.2563 | 1.2564 | 1.2564 | 1.2564 | 1.2564 | 1.2564 | 1.2565 |  | 100% | 70.11% | 0% | 89941 | [7 empty] | 1.21 | 0.046175
[6 empty] | 43566.2722 |  |  |  |  | 5.7054: Committed new connections: |  | 1.2562 | 0.88072 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-11 06:32 | 2019-06-14 08:01 | 0
| 696 | GREMISTA (LERWICK) | 33/11 | 3 x 18 |  | 2020-01-30 16:30 | 17.3258 | 1 | 0 | 0 | 17.3258 | 17.3261 | 17.3264 | 17.3267 | 17.327 | 17.3274 | 17.3277 | 17.328 | 17.3283 | 17.3286 | 17.3289 | 17.3293 | 17.3296 | 17.3299 |  | 0% | 0% | 29.18% | 89903 | 89904 | 89905 | [5 empty] | 17.19 | 0.13577
[6 empty] | 43860.6875 |  |  |  |  | 5.7054: Committed new connections: |  | Manual Calculation | Manual Calculation | 5.0556 | 33.33% | 33.33% | 33.33% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  |  |  | 2019-08-01 04:30
| 695 | GUTCHER | 33/11 | 1 x 4 |  | 2019-11-12 05:02 | 0.72788 | 1 | 0 | 0 | 0.72788 | 0.7279 | 0.72791 | 0.72792 | 0.72794 | 0.72795 | 0.72796 | 0.72798 | 0.72799 | 0.728 | 0.72802 | 0.72803 | 0.72804 | 0.72806 |  | 98.66% | 82.26% | 0% | 89951 | [7 empty] | 0.76 | -0.032117
[6 empty] | 43781.2097 |  |  |  |  | 5.7054: Committed new connections: |  | 0.71811 | 0.59878 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-16 05:03 | 2019-06-13 07:49 | 0
| 698 | MID YELL | 33/11 | 1 x 6 |  | 2020-02-25 07:23 | 0.93096 | 1 | H | H | 0.93096 | 0.9559 | 0.98151 | 1.0078 | 1.0348 | 1.0625 | 1.091 | 1.1202 | 1.1502 | 1.181 | 1.2127 | 1.2451 | 1.2785 | 1.3127 |  | 92.73% | 77.51% | 0% | 89961 | [7 empty] | 0.85305 | 0.07791
[6 empty] | 43886.3076 |  |  |  |  | 5.7054: Committed new connections: |  | 0.86327 | 0.7216 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-23 07:11 | 2019-06-06 16:35 | 0
| 700 | SCALLOWAY | 33/11 | 1 x 8 |  | 2020-03-11 19:08 | 4.1998 | 1 | 0 | 0 | 4.1998 | 4.1999 | 4.2 | 4.2 | 4.2001 | 4.2002 | 4.2003 | 4.2003 | 4.2004 | 4.2005 | 4.2006 | 4.2007 | 4.2007 | 4.2008 |  | 91.99% | 70.82% | 0% | 89972 | [7 empty] | 4.12 | 0.07981
[6 empty] | 43901.7972 |  |  |  |  | 5.7054: Committed new connections: |  | 3.8634 | 2.9743 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-17 07:30 | 2019-06-13 07:44 | 0
| 693 | SANDWICK | 33/11 | 1 x 4 |  | 2019-12-18 07:23 | 1.4009 | 1 | 0 | 0 | 1.4009 | 1.4009 | 1.4009 | 1.401 | 1.401 | 1.401 | 1.401 | 1.4011 | 1.4011 | 1.4011 | 1.4011 | 1.4012 | 1.4012 | 1.4012 |  | 83.57% | 66.37% | 0% | 89981 | [7 empty] | 2.78
[6 empty] | 43817.3076 |  |  |  |  | 5.7054: Committed new connections: |  | 1.1708 | 0.92981 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-04 06:42 | 2019-06-13 18:12 | 0
| 697 | SUMBURGH | 33/11 | 1 x 4 |  | 2020-02-27 07:10 | 1.9561 | 1 | 0 | 0 | 1.9561 | 1.9562 | 1.9562 | 1.9563 | 1.9563 | 1.9563 | 1.9564 | 1.9564 | 1.9564 | 1.9565 | 1.9565 | 1.9565 | 1.9566 | 1.9566 |  | 82.77% | 65.68% | 0% | 89936 | [7 empty] | 1.86
[6 empty] | 43888.2986 |  |  |  |  | 5.7054: Committed new connections: |  | 1.6191 | 1.2848 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-03 07:07 | 2019-06-11 07:06 | 0
| 790 | TUMBLIN | 33/11 | 1 x 6 |  | 2019-12-18 05:32 | 2.3205 | 1 | 0 | 0 | 2.3205 | 2.3205 | 2.3206 | 2.3206 | 2.3207 | 2.3207 | 2.3208 | 2.3208 | 2.3208 | 2.3209 | 2.3209 | 2.321 | 2.321 | 2.321 |  | 84.73% | 61.4% | 0% | 89967 | [7 empty] | 2.19
[6 empty] | 43817.2306 |  |  |  |  | 5.7054: Committed new connections: |  | 1.9661 | 1.4247 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-05-07 07:44 | 2019-06-13 07:32 | 0
| 791 | UNST | 33/11 | 1 x 4 |  | 2019-12-18 05:32 | 1.6205 | 1 | 0 | 0 | 1.6205 | 1.6205 | 1.6205 | 1.6206 | 1.6206 | 1.6206 | 1.6206 | 1.6207 | 1.6207 | 1.6207 | 1.6208 | 1.6208 | 1.6208 | 1.6208 |  | 88.46% | 68.73% | 0% | 89956 | [7 empty] | 1.57 | 0.050465
[6 empty] | 43817.2306 |  |  |  |  | 5.7054: Committed new connections: |  | 1.4334 | 1.1138 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-02 05:33 | 2019-06-14 05:34 | 0
| 687 | VOE | 33/11 | 1 x 8 |  | 2020-02-28 05:32 | 3.5694 | 1 | M | M | 3.5694 | 3.618 | 3.6672 | 3.7171 | 3.7676 | 3.8189 | 3.8709 | 3.9235 | 3.9769 | 4.031 | 4.0858 | 4.1414 | 4.1978 | 4.2549 |  | 86.34% | 66.84% | 0% | 89992 | [7 empty] | 3.686 | -0.1166
[6 empty] | 43889.2306 |  |  |  |  | 5.7054: Committed new connections: |  | 3.0818 | 2.3858 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-04 07:18 | 2019-06-13 07:38 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
SHIN | 545 |  | 132/33 | 2 x 90 |  | 2019-08-02 03:14 | 19.0553 | 1 |  | Diverse | 19.0553 | 19.1109 | 19.1672 | 19.2242 | 19.2821 | 19.3407 | 19.4001 | 19.4603 | 19.5214 | 19.5832 | 19.6459 | 19.7095 | 19.7739 | 19.8391 | Diversity/Losses: 0.102 | 11.71% | 100% | -244.4% | 19130 | [7 empty] | 2.2 | 16.8553
[6 empty] | 43679.1347 |  |  |  | Aggregate | 1.9482 | 1.9539 | 1.9596 | 1.9655 | 1.9714 | 1.9774 | 1.9835 | 1.9896 | 1.9959 | 2.0022 | 2.0086 | 2.0151 | 2.0217 | 2.0283 |  | 2.2321 | 19.0553 | -46.5654 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: 0 |  | 2019-05-06 06:56 | 2019-08-02 03:14 | 2020-01-26 02:47
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 18.6742 | 18.7287 | 18.7838 | 18.8398 | 18.8964 | 18.9539 | 19.0121 | 19.0711 | 19.1309 | 19.1915 | 19.253 | 19.3153 | 19.3784 | 19.4424
| 523 | GLEDFIELD | 33/11 | 1 x 2.5 |  | 2019-12-25 11:36 | 1.5328 | 1 | 0 | 0 | 1.5328 | 1.5329 | 1.5329 | 1.5329 | 1.5329 | 1.533 | 1.533 | 1.533 | 1.533 | 1.5331 | 1.5331 | 1.5331 | 1.5332 | 1.5332 |  | 77.71% | 58.69% | 0% | 85407 | [7 empty] | 1.49 | 0.042825
[6 empty] | 43824.4833 |  |  |  |  | 5.7054: Committed new connections: |  | 1.1911 | 0.89955 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-02 06:42 | 2019-06-12 17:50 | 0
| 536 | SHIN | 33/11 | 1 x 2.5 |  | 2019-12-25 11:35 | 0.41538 | 1 | M | M | 0.41538 | 0.42104 | 0.42676 | 0.43257 | 0.43845 | 0.44442 | 0.45047 | 0.45659 | 0.46281 | 0.4691 | 0.47548 | 0.48195 | 0.48851 | 0.49516 |  | 80.95% | 62.43% | 0% | 85401 | [7 empty] | 0.42 | -0.0046158
[6 empty] | 43824.4826 |  |  |  |  | 5.7054: Committed new connections: |  | 0.33626 | 0.25934 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-03 20:10 | 2019-06-07 20:24 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
SLOY | 139 |  | 132/11 | 2 x 50 |  | 2020-03-30 04:09 | 151.0956 | 1 |  | Diverse | 151.0956 | 151.0984 | 151.1011 | 151.1039 | 151.1067 | 151.1094 | 151.1122 | 151.1149 | 151.1177 | 151.1205 | 151.1232 | 151.126 | 151.1287 | 151.1315 | Diversity/Losses: 0.011 | 88.16% | 91.5% | -0.7765% | 19256 | 19213 | [6 empty] | 2.9 | 148.1956
[6 empty] | 43920.1729 |  |  |  | Aggregate | 1.7053 | 1.7053 | 1.7054 | 1.7054 | 1.7054 | 1.7055 | 1.7055 | 1.7055 | 1.7056 | 1.7056 | 1.7056 | 1.7057 | 1.7057 | 1.7057 |  | 133.205 | 138.2599 | -1.1733 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: 1.5072 |  | 2019-09-02 10:03 | 2019-08-31 17:35 | 2019-05-29 18:54
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 148.0737 | 148.0764 | 148.0791 | 148.0818 | 148.0845 | 148.0872 | 148.0899 | 148.0926 | 148.0953 | 148.098 | 148.1008 | 148.1035 | 148.1062 | 148.1089
| 139 | SLOY POWER STATION | 11/11 | 2 x 8 |  | No PI | 1.7053 | 1 | 0 | 0 | 1.7053 | 1.7053 | 1.7054 | 1.7054 | 1.7054 | 1.7055 | 1.7055 | 1.7055 | 1.7056 | 1.7056 | 1.7056 | 1.7057 | 1.7057 | 1.7057 |  | 0% | 0% | 0% | 85501 | 85500 | [6 empty] | 1.7222 | -0.016856
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
ST FERGUS GAS | 955 |  | 132/11 | 2 x 30 |  | 2019-07-22 12:21 | 9.5147 | 1 |  | Diverse | 9.5147 | 9.7696 | 10.0313 | 10.3 | 10.5759 | 10.8592 | 11.1501 | 11.4488 | 11.7555 | 12.0704 | 12.3937 | 12.7257 | 13.0666 | 13.4166 | Diversity/Losses: 1 | 88.48% | 100% | -171.6% | 21350 | [7 empty] | 11 | -1.4853
[6 empty] | 43668.5146 |  |  |  | Aggregate | 9.5147 | 9.7696 | 10.0313 | 10.3 | 10.5759 | 10.8592 | 11.1501 | 11.4488 | 11.7555 | 12.0704 | 12.3937 | 12.7257 | 13.0666 | 13.4166 |  | 8.4186 | 9.5147 | -16.3314 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: 0.26956 |  | 2019-05-29 08:08 | 2019-07-22 12:21 | 2020-01-19 11:58
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 9.3244 | 9.5742 | 9.8307 | 10.094 | 10.3644 | 10.642 | 10.9271 | 11.2198 | 11.5204 | 11.829 | 12.1458 | 12.4712 | 12.8053 | 13.1483
| 955 | ST FERGUS Gas Term |  | 2 x 30 |  | 2019-07-22 12:21 | 9.5147 | 1 | H | H | 9.5147 | 9.7696 | 10.0313 | 10.3 | 10.5759 | 10.8592 | 11.1501 | 11.4488 | 11.7555 | 12.0704 | 12.3937 | 12.7257 | 13.0666 | 13.4166 |  | 88.48% | 100% | 0% | 21350 | [7 empty] | 10.45
[6 empty] | 43668.5146 |  |  |  |  | 5.7054: Committed new connections: |  | 8.4186 | 9.5147 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0.26956 |  | 2019-05-29 08:08 | 2019-07-22 12:21 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
ST FILLANS | 213 |  | 132/11 | 1 x 25 |  | 2020-03-17 11:50 | 5.899 | 1 |  | Diverse | 5.899 | 5.8991 | 5.8992 | 5.8993 | 5.8994 | 5.8995 | 5.8996 | 5.8998 | 5.8999 | 5.9 | 5.9001 | 5.9002 | 5.9003 | 5.9004 | Diversity/Losses: 0.293 | 61.2% | 67.32% | -19.58% | 85301 | [7 empty] | 1.9 | 3.999
[6 empty] | 43907.4931 |  |  |  | Aggregate | 1.728 | 1.728 | 1.7281 | 1.7281 | 1.7281 | 1.7282 | 1.7282 | 1.7282 | 1.7283 | 1.7283 | 1.7283 | 1.7283 | 1.7284 | 1.7284 |  | 3.61 | 3.971 | -1.1552 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: 15.4 |  | 2019-09-01 23:01 | 2019-08-17 17:10 | 2019-04-24 08:10
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 5.781 | 5.7811 | 5.7812 | 5.7813 | 5.7814 | 5.7815 | 5.7817 | 5.7818 | 5.7819 | 5.782 | 5.7821 | 5.7822 | 5.7823 | 5.7824
| 212 | DALCHONZIE | 33/11 | 1 x 6 |  | 2019-12-18 17:00 | 1.728 | 1 | 0 | 0 | 1.728 | 1.728 | 1.7281 | 1.7281 | 1.7281 | 1.7282 | 1.7282 | 1.7282 | 1.7283 | 1.7283 | 1.7283 | 1.7283 | 1.7284 | 1.7284 |  | 88.89% | 64.81% | 0% | 85302 | [7 empty] | 1.86 | -0.132
[6 empty] | 43817.7083 |  |  |  |  | 5.7054: Committed new connections: |  | 1.536 | 1.12 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-10-28 17:27 | 2019-08-09 17:03 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
STORNOWAY |  |  | 132/33 | 1 x 30 |  | #N/A | #N/A | 1 |  | Diverse | #N/A | 23.858 | 23.9005 | 23.944 | 23.9888 | 24.0346 | 24.0817 | 24.13 | 24.1796 | 24.2305 | 24.2826 | 24.3362 | 24.3912 | 24.4476 | #N/A | 0% | 0% | 0% | 85628 | [7 empty] | 19.35 | #N/A
Substation was not found in SubstationLoad | [5 empty] | #N/A |  |  |  | Aggregate | 23.8166 | 23.858 | 23.9005 | 23.944 | 23.9888 | 24.0346 | 24.0817 | 24.13 | 24.1796 | 24.2305 | 24.2826 | 24.3362 | 24.3912 | 24.4476 |  | #N/A | #N/A | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: #N/A |  | #N/A | #N/A | 0
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | #N/A | 23.3808 | 23.4224 | 23.4652 | 23.509 | 23.5539 | 23.6001 | 23.6474 | 23.696 | 23.7458 | 23.797 | 23.8495 | 23.9033 | 23.9586
| 651 | BARVAS | 33/11 | 2 x 2.5 |  | 2019-12-16 16:48 | 2.6066 | 1 | 0 | 0 | 2.6066 | 2.6066 | 2.6067 | 2.6067 | 2.6068 | 2.6068 | 2.6068 | 2.6069 | 2.6069 | 2.607 | 2.607 | 2.6071 | 2.6071 | 2.6072 |  | 95.37% | 67.34% | 0% | 85627 | [7 empty] | 2.62 | -0.013438
[6 empty] | 43815.7 |  |  |  |  | 5.7054: Committed new connections: |  | 2.4858 | 1.7552 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-09 21:54 | 2019-06-13 09:27 | 0
| 652 | BATTERY POINT | 33/11 | 3 x 8 |  | 2019-11-18 16:09 | 13.3187 | 1 | 0 | 0 | 13.3187 | 13.3189 | 13.3192 | 13.3194 | 13.3196 | 13.3199 | 13.3201 | 13.3204 | 13.3206 | 13.3209 | 13.3211 | 13.3213 | 13.3216 | 13.3218 |  | 91.25% | 76.49% | 0% | 85622 | [7 empty] | 12.95 | 0.36867
[6 empty] | 43787.6729 |  |  |  |  | 5.7054: Committed new connections: |  | 12.1538 | 10.1868 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-04 11:18 | 2019-08-07 17:35 | 0
| 670 | CALLANISH | 33/11 | 1 x 4 |  | 2019-12-24 18:59 | 1.9296 | 1 | 0 | 0 | 1.9296 | 1.9297 | 1.9297 | 1.9297 | 1.9298 | 1.9298 | 1.9298 | 1.9299 | 1.9299 | 1.9299 | 1.93 | 1.93 | 1.93 | 1.9301 |  | 87.41% | 78.77% | 0% | 85614 | [7 empty] | 1.78 | 0.14962
[6 empty] | 43823.791 |  |  |  |  | 5.7054: Committed new connections: |  | 1.6868 | 1.52 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-10-29 18:49 | 2019-06-13 20:11 | 0
| 672 | COLL | 33/11 | 1 x 2.5 |  | 2020-02-11 20:30 | 2.6259 | 1 | 0 | 0 | 2.6259 | 2.6259 | 2.626 | 2.626 | 2.6261 | 2.6261 | 2.6262 | 2.6262 | 2.6263 | 2.6263 | 2.6264 | 2.6264 | 2.6265 | 2.6265 |  | 0% | 0% | 2.148% | 85625 | [7 empty] | 2.03 | 0.5959
[6 empty] | 43872.8542 |  |  |  |  | 5.7054: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.056396 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0.89914 |  |  |  | 2019-06-29 03:30
| 648 | GISLA | 33/11 | 1 x 1 |  | 2019-09-03 23:00 | 1.4718 | 1 | H | H | 1.4718 | 1.5112 | 1.5517 | 1.5933 | 1.636 | 1.6798 | 1.7248 | 1.771 | 1.8184 | 1.8671 | 1.9172 | 1.9685 | 2.0212 | 2.0754 |  | 0% | 0% | 14.89% | 85617 | [7 empty] | 1.04 | 0.43181
[6 empty] | 43711.9583 |  |  |  |  | 5.7054: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.21922 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  |  |  | 2019-06-25 02:30
| 657 | LAXAY | 33/11 | 1 x 2.5 |  | 2020-02-12 18:34 | 1.7488 | 1 | 0 | 0 | 1.7488 | 1.7489 | 1.7489 | 1.7489 | 1.749 | 1.749 | 1.749 | 1.7491 | 1.7491 | 1.7491 | 1.7491 | 1.7492 | 1.7492 | 1.7492 |  | 87.44% | 67.96% | 0% | 85609 | [7 empty] | 1.68 | 0.068828
[6 empty] | 43873.7736 |  |  |  |  | 5.7054: Committed new connections: |  | 1.5291 | 1.1885 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-04-03 18:58 | 2019-06-12 17:41 | 0
| 650 | MAARUIG | 33/11 | 1 x 0.2 |  | No PI | 0.11519 | 1 | M | M | 0.11519 | 0.11675 | 0.11834 | 0.11995 | 0.12158 | 0.12324 | 0.12491 | 0.12661 | 0.12834 | 0.13008 | 0.13185 | 0.13365 | 0.13546 | 0.13731 |  | 0% | 0% | 0% | 85606 | [7 empty] | 0.11238 | 0.0028094
[6 empty] | No PI |  |  |  |  | 5.7054: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak: |  | 0 | 0 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
STRATHLEVEN |  |  | 132/33 | 1 x 60 |  | 2019-12-31 17:38 | 53.5303 | 1 |  | Diverse | 53.5303 | 53.5639 | 53.598 | 53.6325 | 53.6675 | 53.703 | 53.7389 | 53.7753 | 53.8122 | 53.8495 | 53.8874 | 53.9258 | 53.9646 | 54.004 | Diversity/Losses: 0.205 | 83.14% | 75.53% | -12.89% | 41033 | [8 empty] | #VALUE!
|  |  |  | 1 x 87 |  | 43830.7347 |  |  |  | Aggregate | 10.9477 | 10.9545 | 10.9615 | 10.9686 | 10.9757 | 10.983 | 10.9903 | 10.9978 | 11.0053 | 11.0129 | 11.0207 | 11.0285 | 11.0365 | 11.0445 |  | 44.5032 | 40.4305 | -6.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Generation at time of BSP peak: 5.706: Generation at time of BSP peak:; 0 5.7061: 0 |  | 2019-10-17 17:12 | 2019-08-02 13:04 | 2019-05-21 03:14
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 52.4597 | 52.4926 | 52.526 | 52.5599 | 52.5942 | 52.6289 | 52.6641 | 52.6998 | 52.7359 | 52.7725 | 52.8097 | 52.8472 | 52.8853 | 52.924
| 206 | ABERFOYLE | 33/11 | 1 x 6.9 |  | 2019-12-31 19:40 | 2.1914 | 1 | 0 | 0 | 2.1914 | 2.1914 | 2.1915 | 2.1915 | 2.1915 | 2.1916 | 2.1916 | 2.1917 | 2.1917 | 2.1917 | 2.1918 | 2.1918 | 2.1919 | 2.1919 |  | 87.16% | 57.94% | 0% | 85711 | [7 empty] | 2.4 | -0.20861
[6 empty] | 43830.8194 |  |  |  |  | 5.7054: Committed new connections: |  | 1.91 | 1.2696 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0.16191 |  | 2019-10-29 19:35 | 2019-06-15 20:08 | 0
| 220 | BLAIRLINNANS | 33/11 | 1 x 2.5 |  | 2020-03-02 18:30 | 0.49157 | 1 | M | M | 0.49157 | 0.49826 | 0.50504 | 0.51191 | 0.51887 | 0.52593 | 0.53309 | 0.54034 | 0.54769 | 0.55514 | 0.5627 | 0.57035 | 0.57811 | 0.58598 |  | 86.09% | 75.53% | 0% | 85715 | [7 empty] | 0.39 | 0.10157
[6 empty] | 43892.7708 |  |  |  |  | 5.7054: Committed new connections: |  | 0.42321 | 0.37127 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-10-30 04:39 | 2019-07-03 22:33 | 0
| 203 | DRYMEN | 33/11 | 1 x 6 |  | 2020-01-28 17:00 | 2.4361 | 1 | 0 | 0 | 2.4361 | 2.4361 | 2.4362 | 2.4362 | 2.4362 | 2.4363 | 2.4363 | 2.4364 | 2.4364 | 2.4365 | 2.4365 | 2.4366 | 2.4366 | 2.4366 |  | 0% | 0% | 9.121% | 85714 | [7 empty] | 2.4 | 0.036066
[6 empty] | 43858.7083 |  |  |  |  | 5.7054: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.22221 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0.0008 |  |  |  | 2019-09-11 02:30
| 205 | KEPCULLOCH | 33/11 | 2 x 6.25 |  | 2020-01-28 17:30 | 3.8246 | 1 | 0 | 0 | 3.8246 | 3.8247 | 3.8248 | 3.8248 | 3.8249 | 3.825 | 3.825 | 3.8251 | 3.8252 | 3.8253 | 3.8253 | 3.8254 | 3.8255 | 3.8255 |  | 0% | 0% | 20.69% | 85712 | [7 empty] | 2.75 | 1.0746
[6 empty] | 43858.7292 |  |  |  |  | 5.7054: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.79133 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0.077656 |  |  |  | 2019-08-27 02:00
| 204 | KILLEARN | 33/11 | 1 x 6.25 |  | 2020-02-25 12:36 | 2.004 | 1 | 0 | 0 | 2.004 | 2.004 | 2.0041 | 2.0041 | 2.0041 | 2.0042 | 2.0042 | 2.0043 | 2.0043 | 2.0043 | 2.0044 | 2.0044 | 2.0044 | 2.0045 |  | 87.67% | 63.86% | 0% | 85718 | [7 empty] | 1.85 | 0.154
[6 empty] | 43886.525 |  |  |  |  | 5.7054: Committed new connections: |  | 1.7569 | 1.2798 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 5.706: Generation at time of peak:; 0 5.7061: 0 |  | 2019-10-28 19:10 | 2019-06-12 17:45 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
STRICHEN | 949 |  | 132/33 | 2 x 90 |  | 2019-10-24 12:35 | 6.9427 | 1 |  | Diverse | 6.9427 | 6.9428 | 6.943 | 6.9431 | 6.9432 | 6.9433 | 6.9435 | 6.9436 | 6.9437 | 6.9438 | 6.944 | 6.9441 | 6.9442 | 6.9444 | Diversity/Losses: 2.383 | 100% | 71.6% | -261.9% | 19530 | [7 empty] | 16.6 | -9.6573
[6 empty] | 43762.5243 |  |  |  | Aggregate | 16.5449 | 16.5452 | 16.5455 | 16.5458 | 16.5461 | 16.5464 | 16.5467 | 16.547 | 16.5473 | 16.5476 | 16.5479 | 16.5482 | 16.5485 | 16.5488 |  | 6.9427 | 4.9707 | -18.1859 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 16.5467: Generation at time of BSP peak:; 16.547: 0 |  | 2019-10-24 12:35 | 2019-08-09 22:14 | 2019-11-05 00:01
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 6.8038 | 6.804 | 6.8041 | 6.8042 | 6.8043 | 6.8045 | 6.8046 | 6.8047 | 6.8048 | 6.805 | 6.8051 | 6.8052 | 6.8053 | 6.8055
| 863 | HATTON | 33/11 | 2 x 5 |  | 2020-01-13 18:52 | 3.0877 | 1 | 0 | 0 | 3.0877 | 3.0878 | 3.0878 | 3.0879 | 3.0879 | 3.088 | 3.088 | 3.0881 | 3.0882 | 3.0882 | 3.0883 | 3.0883 | 3.0884 | 3.0884 |  | 88.83% | 69.35% | 0% | 85813 | [7 empty] | 3.04 | 0.0477
[6 empty] | 43843.7861 |  |  |  |  | 16.5449: Committed new connections: |  | 2.7428 | 2.1413 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-28 18:15 | 2019-06-24 17:32 | 0
| 901 | MAUD | 33/11 | 2 x 8 |  | 2019-11-19 20:00 | 2.5624 | 1 | 0 | 0 | 2.5624 | 2.5624 | 2.5625 | 2.5625 | 2.5626 | 2.5626 | 2.5627 | 2.5627 | 2.5628 | 2.5628 | 2.5629 | 2.5629 | 2.563 | 2.563 |  | 0% | 0% | 2.095% | 85817 | [7 empty] | 2.51 | 0.052402
[6 empty] | 43788.8333 |  |  |  |  | 16.5449: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.053676 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0.27156 |  |  |  | 2019-05-29 14:30
| 909 | MINTLAW | 33/11 | 2 x 15 |  | 2019-11-19 17:04 | 5.9938 | 1 | 0 | 0 | 5.9938 | 5.9939 | 5.994 | 5.9942 | 5.9943 | 5.9944 | 5.9945 | 5.9946 | 5.9947 | 5.9948 | 5.9949 | 5.995 | 5.9951 | 5.9953 |  | 93.16% | 76.12% | 0% | 85807 | [7 empty] | 5.791 | 0.20283
[6 empty] | 43788.7111 |  |  |  |  | 16.5449: Committed new connections: |  | 5.5837 | 4.5622 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0.26227 |  | 2019-10-30 16:56 | 2019-06-05 17:01 | 0
| 913 | NEW PITSLIGO | 33/11 | 2 x 2.5 |  | 2019-11-13 20:00 | 1.4514 | 1 | 0 | 0 | 1.4514 | 1.4514 | 1.4514 | 1.4515 | 1.4515 | 1.4515 | 1.4515 | 1.4516 | 1.4516 | 1.4516 | 1.4517 | 1.4517 | 1.4517 | 1.4517 |  | 0% | 0% | 29.4% | 85802 | [7 empty] | 1.6212 | -0.16982
[6 empty] | 43782.8333 |  |  |  |  | 16.5449: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.42678 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  |  |  | 2019-06-19 10:30
| 950 | STRICHEN | 33/11 | 2 x 10 |  | 2020-02-29 18:07 | 3.4496 | 1 | 0 | 0 | 3.4496 | 3.4496 | 3.4497 | 3.4498 | 3.4498 | 3.4499 | 3.4499 | 3.45 | 3.4501 | 3.4501 | 3.4502 | 3.4503 | 3.4503 | 3.4504 |  | 83.22% | 66.38% | 0% | 85804 | [7 empty] | 3.06 | 0.38957
[6 empty] | 43890.7549 |  |  |  |  | 16.5449: Committed new connections: |  | 2.8708 | 2.2897 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 4.6541 |  | 2019-10-27 17:12 | 2019-08-25 18:53 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
TARLAND | 470 |  | 132/33 | 2 x 30 |  | 2019-11-27 11:34 | 13.633 | 1 |  | Diverse | 13.633 | 13.6531 | 13.6738 | 13.695 | 13.7168 | 13.7391 | 13.762 | 13.7855 | 13.8097 | 13.8345 | 13.86 | 13.8861 | 13.9129 | 13.9405 | Diversity/Losses: 1.344 | 93.2% | 68.41% | -165% | 21430 | [7 empty] | 20.3 | -6.667
[6 empty] | 43796.4819 |  |  |  | Aggregate | 18.3282 | 18.3552 | 18.383 | 18.4115 | 18.4408 | 18.4708 | 18.5016 | 18.5332 | 18.5657 | 18.5991 | 18.6333 | 18.6684 | 18.7045 | 18.7415 |  | 12.7056 | 9.3264 | -22.4904 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 16.5467: Generation at time of BSP peak:; 16.547: 0 |  | 2019-10-21 20:06 | 2019-08-20 20:02 | 2019-11-18 01:39
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 13.3604 | 13.3801 | 13.4003 | 13.4211 | 13.4424 | 13.4643 | 13.4868 | 13.5098 | 13.5335 | 13.5578 | 13.5828 | 13.6084 | 13.6347 | 13.6616
| 801 | ABOYNE | 33/11 | 2 x 15 |  | 2020-02-28 11:54 | 6.2839 | 1 | 0 | 0 | 6.2839 | 6.2841 | 6.2842 | 6.2843 | 6.2844 | 6.2845 | 6.2846 | 6.2847 | 6.2849 | 6.285 | 6.2851 | 6.2852 | 6.2853 | 6.2854 |  | 84.55% | 68.14% | 0% | 86704 | [7 empty] | 6.11 | 0.17395
[6 empty] | 43889.4958 |  |  |  |  | 16.5449: Committed new connections: |  | 5.313 | 4.2816 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-31 11:35 | 2019-06-13 16:50 | 0
| 806 | BALLATER | 33/11 | 2 x 15 |  | 2019-12-31 16:30 | 5.1068 | 1 | 0 | 0 | 5.1068 | 5.1069 | 5.107 | 5.1071 | 5.1072 | 5.1073 | 5.1074 | 5.1075 | 5.1075 | 5.1076 | 5.1077 | 5.1078 | 5.1079 | 5.108 |  | 0% | 0% | 21.34% | 86708 | [7 empty] | 5.44 | -0.3332
[6 empty] | 43830.6875 |  |  |  |  | 16.5449: Committed new connections: |  | Manual Calculation | Manual Calculation | 1.0896 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  |  |  | 2019-06-30 04:00
| 911 | MOSSAT | 33/11 | 2 x 2.5 |  | 2019-11-11 11:00 | 1.6833 | 1 | 0 | 0 | 1.6833 | 1.6833 | 1.6833 | 1.6834 | 1.6834 | 1.6834 | 1.6835 | 1.6835 | 1.6835 | 1.6836 | 1.6836 | 1.6836 | 1.6837 | 1.6837 |  | 0% | 0% | 4.977% | 86711 | [7 empty] | 1.7096 | -0.026281
[6 empty] | 43780.4583 |  |  |  |  | 16.5449: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.083774 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0.0027915 |  |  |  | 2019-07-01 01:30
| 951 | STRATHDON | 33/11 | 1 x 2 |  | 2019-12-07 15:10 | 0.99781 | 1 | H | H | 0.99781 | 1.0245 | 1.052 | 1.0802 | 1.1091 | 1.1388 | 1.1693 | 1.2006 | 1.2328 | 1.2658 | 1.2997 | 1.3345 | 1.3703 | 1.407 |  | 85.24% | 59.71% | 0% | 86715 | [7 empty] | 1.11 | -0.11219
[6 empty] | 43806.6319 |  |  |  |  | 16.5449: Committed new connections: |  | 0.85056 | 0.59578 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-06 12:01 | 2019-08-24 10:46 | 0
| 981 | WHITEHOUSE | 33/11 | 2 x 8 |  | 2019-12-17 20:05 | 4.2564 | 1 | 0 | 0 | 4.2564 | 4.2564 | 4.2565 | 4.2566 | 4.2567 | 4.2567 | 4.2568 | 4.2569 | 4.257 | 4.2571 | 4.2571 | 4.2572 | 4.2573 | 4.2574 |  | 87.38% | 62.47% | 0% | 86717 | [7 empty] | 4.82 | -0.56364
[6 empty] | 43816.8368 |  |  |  |  | 16.5449: Committed new connections: |  | 3.719 | 2.6591 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-15 20:16 | 2019-06-13 20:19 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
TAYNUILT | 303 |  | 132/33 | 2 x 90 |  | 2019-09-15 00:27 | 27.6372 | 1 |  | Diverse | 27.6372 | 27.8521 | 28.0703 | 28.2919 | 28.5169 | 28.7454 | 28.9775 | 29.2132 | 29.4526 | 29.6958 | 29.9428 | 30.1936 | 30.4484 | 30.7072 | Diversity/Losses: 1.261 | 100% | 90.76% | -56.33% | 19730 | [7 empty] | 33.8 | -6.1628
[6 empty] | 43723.0188 |  |  |  | Aggregate | 34.855 | 35.126 | 35.4012 | 35.6806 | 35.9644 | 36.2527 | 36.5454 | 36.8427 | 37.1446 | 37.4513 | 37.7627 | 38.0791 | 38.4004 | 38.7268 |  | 27.6372 | 25.0828 | -15.568 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 16.5467: Generation at time of BSP peak:; 16.547: 0 |  | 2019-09-15 00:27 | 2019-08-24 00:24 | 2019-05-27 21:25
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 27.0845 | 27.295 | 27.5089 | 27.726 | 27.9465 | 28.1705 | 28.398 | 28.629 | 28.8636 | 29.1019 | 29.3439 | 29.5897 | 29.8394 | 30.0931
| 327 | BARCALDINE | 33/11 | 1 x 15 |  | 2019-11-15 08:43 | 3.7205 | 1 | 0 | 0 | 3.7205 | 3.7206 | 3.7206 | 3.7207 | 3.7208 | 3.7208 | 3.7209 | 3.721 | 3.7211 | 3.7211 | 3.7212 | 3.7213 | 3.7213 | 3.7214 |  | 79.42% | 59.97% | 0% | 85910 | [7 empty] | 2.2706 | 1.4499
[6 empty] | 43784.3632 |  |  |  |  | 16.5449: Committed new connections: |  | 2.9547 | 2.2311 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-22 19:31 | 2019-08-11 12:12 | 0
| 328 | BONAWE | 33/11 | 1 x 0.5 |  | No PI | 0.0028094 | 1 | 0 | 0 | 0.0028094 | 0.0028095 | 0.0028095 | 0.0028096 | 0.0028096 | 0.0028097 | 0.0028097 | 0.0028098 | 0.0028098 | 0.0028099 | 0.0028099 | 0.00281 | 0.00281 | 0.0028101 |  | 0% | 0% | 0% | 85905 | [7 empty] | 0.0028094 | 0
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
| 306 | CONNEL | 33/11 | 1 x 8 |  | 2019-11-18 18:34 | 1.7047 | 1 | 0 | 0 | 1.7047 | 1.7047 | 1.7047 | 1.7048 | 1.7048 | 1.7048 | 1.7049 | 1.7049 | 1.7049 | 1.705 | 1.705 | 1.705 | 1.705 | 1.7051 |  | 89.52% | 53.06% | 0% | 85912 | [7 empty] | 1.61 | 0.094675
[6 empty] | 43787.7736 |  |  |  |  | 16.5449: Committed new connections: |  | 1.526 | 0.90445 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-29 18:32 | 2019-06-03 18:31 | 0
| 348 | DALMALLY | 33/11 | 1 x 1 |  | No PI | 0.23599 | 1 | 0 | 0 | 0.23599 | 0.23599 | 0.236 | 0.236 | 0.23601 | 0.23601 | 0.23602 | 0.23602 | 0.23602 | 0.23603 | 0.23603 | 0.23604 | 0.23604 | 0.23605 |  | 0% | 0% | 0% | 85955 | [7 empty] | 0.23599 | 0
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
| 346 | DERVAIG | 33/11 | 1 x 8 |  | 2020-02-13 13:30 | 3.8681 | 1 | 0 | 0 | 3.8681 | 3.8682 | 3.8682 | 3.8683 | 3.8684 | 3.8684 | 3.8685 | 3.8686 | 3.8686 | 3.8687 | 3.8688 | 3.8689 | 3.8689 | 3.869 |  | 0% | 0% | 0.9631% | 85939 | [7 empty] | 3.56 | 0.30808
[6 empty] | 43874.5625 |  |  |  |  | 16.5449: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.037253 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 2 |  |  |  | 2020-01-05 22:30
| 324 | EREDINE | 33/11 | 1 x 0.2 |  | No PI | 0.118 | 1 | 0 | 0 | 0.118 | 0.118 | 0.118 | 0.118 | 0.118 | 0.11801 | 0.11801 | 0.11801 | 0.11801 | 0.11801 | 0.11802 | 0.11802 | 0.11802 | 0.11802 |  | 0% | 0% | 0% | 85972 | [7 empty] | 0.1208 | -0.0028094
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
| 329 | KENMORE | 33/11 | 1 x 1.5 |  | No PI | 0.31465 | 1 | 0 | 0 | 0.31465 | 0.31466 | 0.31467 | 0.31467 | 0.31468 | 0.31468 | 0.31469 | 0.31469 | 0.3147 | 0.31471 | 0.31471 | 0.31472 | 0.31472 | 0.31473 |  | 0% | 0% | 0% | 85908 | [7 empty] | 0.30342 | 0.011238
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
| 335 | KERRERA | 33/11 | 1 x 0.3 |  | No PI | 0.098329 | 1 | 0 | 0 | 0.098329 | 0.098331 | 0.098333 | 0.098335 | 0.098336 | 0.098338 | 0.09834 | 0.098342 | 0.098344 | 0.098345 | 0.098347 | 0.098349 | 0.098351 | 0.098353 |  | 0% | 0% | 0% | 85926 | [7 empty] | 0.09552 | 0.0028094
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
| 323 | KILCHRENAN | 33/11 | 1 x 1 |  | 2019-12-01 18:37 | 0.83498 | 1 | 0 | 0 | 0.83498 | 0.83499 | 0.83501 | 0.83502 | 0.83504 | 0.83505 | 0.83507 | 0.83508 | 0.8351 | 0.83511 | 0.83513 | 0.83515 | 0.83516 | 0.83518 |  | 82.77% | 54.77% | 0% | 85945 | [7 empty] | 0.67 | 0.16498
[6 empty] | 43800.7757 |  |  |  |  | 16.5449: Committed new connections: |  | 0.6911 | 0.45731 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-15 18:55 | 2019-07-04 19:45 | 0
| 304 | KILMELFORD PS | 33/11 | 1 x 2 |  | 2019-10-10 11:04 | 2.2644 | 1 | 0 | 0 | 2.2644 | 2.2644 | 2.2645 | 2.2645 | 2.2645 | 2.2646 | 2.2646 | 2.2647 | 2.2647 | 2.2647 | 2.2648 | 2.2648 | 2.2649 | 2.2649 |  | 100% | 96.51% | 0% | 85986 | [7 empty] | 1.96 | 0.30437
[6 empty] | 43748.4611 |  |  |  |  | 16.5449: Committed new connections: |  | 2.2644 | 2.1853 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-10 11:04 | 2019-07-22 23:05 | 0
| 322 | KILNINVER | 33/11 | 1 x 2.5 |  | 2019-11-30 18:47 | 2.1208 | 1 | M | M | 2.1208 | 2.1497 | 2.1789 | 2.2086 | 2.2386 | 2.2691 | 2.3 | 2.3313 | 2.363 | 2.3951 | 2.4277 | 2.4607 | 2.4942 | 2.5281 |  | 82.99% | 50.97% | 0% | 85920 | [7 empty] | 2.06 | 0.060841
[6 empty] | 43799.7826 |  |  |  |  | 16.5449: Committed new connections: |  | 1.76 | 1.081 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-29 18:44 | 2019-06-07 18:37 | 0
| 333 | KINLOCH | 33/11 | 1 x 2.5 |  | 2019-04-03 13:21 | 1.4703 | 1 | H | H | 1.4703 | 1.5097 | 1.5502 | 1.5917 | 1.6343 | 1.6781 | 1.723 | 1.7692 | 1.8166 | 1.8653 | 1.9152 | 1.9665 | 2.0192 | 2.0733 |  | 100% | 75.44% | 0% | 85935 | [7 empty] | 1.74 | -0.26967
[6 empty] | 43558.5563 |  |  |  |  | 16.5449: Committed new connections: |  | 1.4703 | 1.1092 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-03 13:21 | 2019-06-05 19:00 | 0
| 317 | LOCHDONHEAD | 33/11 | 1 x 1 |  | 2019-04-03 13:34 | 0.91673 | 1 | 0 | 0 | 0.91673 | 0.91674 | 0.91676 | 0.91678 | 0.91679 | 0.91681 | 0.91683 | 0.91684 | 0.91686 | 0.91688 | 0.91689 | 0.91691 | 0.91693 | 0.91694 |  | 100% | 72.24% | 0% | 85929 | [7 empty] | 0.99 | -0.073273
[6 empty] | 43558.5653 |  |  |  |  | 16.5449: Committed new connections: |  | 0.91673 | 0.66227 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-03 13:34 | 2019-06-06 08:26 | 0
| 307 | OBAN | 33/11 | 2 x 24 |  | 2020-02-11 14:08 | 14.88 | 1 | M | M | 14.88 | 15.0824 | 15.2876 | 15.4956 | 15.7064 | 15.9201 | 16.1367 | 16.3562 | 16.5788 | 16.8043 | 17.0329 | 17.2647 | 17.4996 | 17.7376 |  | 87.74% | 67.1% | 0% | 85916 | [7 empty] | 15.6094 | -0.72936
[6 empty] | 43872.5889 |  |  |  |  | 16.5449: Committed new connections: |  | 13.056 | 9.984 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-03 13:21 | 2019-06-05 16:21 | 0
| 315 | SALEN | 33/11 | 2 x 6.3 |  | 2019-12-13 18:34 | 0.69209 | 1 | 0 | 0 | 0.69209 | 0.6921 | 0.69211 | 0.69213 | 0.69214 | 0.69215 | 0.69216 | 0.69218 | 0.69219 | 0.6922 | 0.69221 | 0.69223 | 0.69224 | 0.69225 |  | 88.52% | 67.77% | 0% | 85936 | 85990 | [6 empty] | 2.1577 | -1.4657
[6 empty] | 43812.7736 |  |  |  |  | 16.5449: Committed new connections: |  | 0.61264 | 0.46903 | 0 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-06 13:27 | 2019-06-05 18:33 | 0
| 340 | SCAMMADALE | 33/11 | 1 x 0.1 |  | No PI | 0.078663 | 1 | 0 | 0 | 0.078663 | 0.078665 | 0.078666 | 0.078668 | 0.078669 | 0.078671 | 0.078672 | 0.078673 | 0.078675 | 0.078676 | 0.078678 | 0.078679 | 0.078681 | 0.078682 |  | 0% | 0% | 0% | 85923 | [7 empty] | 0.078663 | 0
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
| 347 | TAYNUILT | 33/11 | 1 x 1.8 |  | 2019-12-14 13:47 | 1.4694 | 1 | 0 | 0 | 1.4694 | 1.4694 | 1.4694 | 1.4695 | 1.4695 | 1.4695 | 1.4695 | 1.4696 | 1.4696 | 1.4696 | 1.4696 | 1.4697 | 1.4697 | 1.4697 |  | 79.64% | 50.01% | 0% | 85902 | [7 empty] | 1.318 | 0.15138
[6 empty] | 43813.5743 |  |  |  |  | 16.5449: Committed new connections: |  | 1.1703 | 0.7348 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-04 03:31 | 2019-06-05 17:22 | 0
| 342 | TIRORAN BRIDGE | 33/11 | 1 x 0.05 |  | No PI | 0.064616 | 1 | 0 | 0 | 0.064616 | 0.064618 | 0.064619 | 0.06462 | 0.064621 | 0.064622 | 0.064623 | 0.064625 | 0.064626 | 0.064627 | 0.064628 | 0.064629 | 0.064631 | 0.064632 |  | 0% | 0% | 0% | 85933 | [7 empty] | 0.064616 | 0
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
THURSO | 593 |  | 132/33 | 2 x 120 |  |  |  | 1 |  | Diverse | #VALUE! | 49.302 | 49.3214 | 49.3412 | 49.3615 | 49.3821 | 49.4033 | 49.4248 | 49.4469 | 49.4694 | 49.4924 | 49.516 | 49.54 | 49.5646 | #VALUE! | 0% | 0% | 0% | 19930 | [7 empty] | 41.4 | #VALUE!
No PI or No Data | [9 empty] | Aggregate | 49.283 | 49.302 | 49.3214 | 49.3412 | 49.3615 | 49.3821 | 49.4033 | 49.4248 | 49.4469 | 49.4694 | 49.4924 | 49.516 | 49.54 | 49.5646 |  | #VALUE! | No Data |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 16.5467: Generation at time of BSP peak: |  | #VALUE! | Missing Data
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | #VALUE! | 48.316 | 48.335 | 48.3544 | 48.3742 | 48.3945 | 48.4152 | 48.4363 | 48.4579 | 48.48 | 48.5026 | 48.5256 | 48.5492 | 48.5733
| 701 | BURGARHILL | 33/11 | 1 x 8 |  | 2019-04-11 07:07 | 1.4289 | 1 | 0 | 0 | 1.4289 | 1.4289 | 1.429 | 1.429 | 1.429 | 1.429 | 1.4291 | 1.4291 | 1.4291 | 1.4291 | 1.4292 | 1.4292 | 1.4292 | 1.4292 |  | 0% | 0% | 0% | 86109 | [7 empty] | 1.63 | -0.2011
[6 empty] | 43566.2965 |  |  |  |  | 16.5449: Committed new connections: |  | #VALUE! | No Data | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | #VALUE! | Missing Data | 0
| 675 | EDAY | 33/11 | 1 x 1 |  | 2019-12-25 11:47 | 0.23861 | 1 | 0 | 0 | 0.23861 | 0.23861 | 0.23862 | 0.23862 | 0.23863 | 0.23863 | 0.23863 | 0.23864 | 0.23864 | 0.23865 | 0.23865 | 0.23866 | 0.23866 | 0.23866 |  | 80.99% | 69.3% | 0% | 86116 | [7 empty] | 0.22 | 0.018608
[6 empty] | 43824.491 |  |  |  |  | 16.5449: Committed new connections: |  | 0.19326 | 0.16535 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-11 19:17 | 2019-06-23 03:17 | 0
| 680 | FLOTTA | 33/11 | 1 x 8 |  | 2020-03-03 18:15 | 0.45355 | 1 | H | H | 0.45355 | 0.4657 | 0.47818 | 0.49098 | 0.50414 | 0.51764 | 0.53151 | 0.54574 | 0.56036 | 0.57537 | 0.59079 | 0.60661 | 0.62286 | 0.63955 |  | 87.94% | 74.71% | 0% | 86136 | [7 empty] | 0.23 | 0.22355
[6 empty] | 43893.7604 |  |  |  |  | 16.5449: Committed new connections: |  | 0.39887 | 0.33883 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0.87652 |  | 2019-04-18 19:41 | 2019-06-04 02:17 | 0
| 597 | HALKIRK | 33/11 | 1 x 2.5 |  | 2019-12-17 11:17 | 2.6042 | 1 | 0 | 0 | 2.6042 | 2.6042 | 2.6043 | 2.6043 | 2.6044 | 2.6044 | 2.6045 | 2.6045 | 2.6046 | 2.6046 | 2.6047 | 2.6047 | 2.6048 | 2.6048 |  | 94.77% | 75.38% | 0% | 86017 | [7 empty] | 2.09 | 0.51419
[6 empty] | 43816.4701 |  |  |  |  | 16.5449: Committed new connections: |  | 2.468 | 1.9632 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-31 07:49 | 2019-08-29 08:03 | 0
| 582 | HASTIGROW | 33/11 | 1 x 5 |  | 2020-02-27 09:13 | 2.9492 | 1 | 0 | 0 | 2.9492 | 2.9493 | 2.9494 | 2.9494 | 2.9495 | 2.9495 | 2.9496 | 2.9496 | 2.9497 | 2.9497 | 2.9498 | 2.9498 | 2.9499 | 2.9499 |  | 73.59% | 57.73% | 0% | 86002 | [7 empty] | 2.59 | 0.35925
[6 empty] | 43888.384 |  |  |  |  | 16.5449: Committed new connections: |  | 2.1703 | 1.7026 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-05 07:56 | 2019-06-13 13:10 | 0
| 677 | KIRKWALL | 33/11 | 2 x 24 |  | 2019-12-17 12:04 | 16.2012 | 1 | 0 | 0 | 16.2012 | 16.2015 | 16.2018 | 16.2021 | 16.2024 | 16.2027 | 16.203 | 16.2033 | 16.2036 | 16.2039 | 16.2042 | 16.2045 | 16.2048 | 16.2051 |  | 81.65% | 74.21% | 0% | 86124 | 86125 | 86142 | [5 empty] | 15.01 | 1.1912
[6 empty] | 43816.5028 |  |  |  |  | 16.5449: Committed new connections: |  | 13.2288 | 12.0225 | 0 | 33.3% | 33.3% | 33.3% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0.50012 |  | 2019-10-31 12:04 | 2019-06-13 12:05 | 0
| 682 | LYNESS | 33/11 | 1 x 1 |  | 2019-12-29 04:30 | 0.71401 | 1 | 0 | 0 | 0.71401 | 0.71403 | 0.71404 | 0.71405 | 0.71406 | 0.71408 | 0.71409 | 0.7141 | 0.71412 | 0.71413 | 0.71414 | 0.71416 | 0.71417 | 0.71418 |  | 0% | 0% | 9.894% | 86133 | [7 empty] | 0.67193 | 0.04208
[6 empty] | 43828.1875 |  |  |  |  | 16.5449: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.070643 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  |  |  | 2019-10-15 11:00
| 585 | MOUNT PLEASANT | 33/11 | 1 x 7.5/15 |  | 2019-11-13 20:04 | 5.7353 | 1 | 0 | 0 | 5.7353 | 5.7354 | 5.7355 | 5.7356 | 5.7357 | 5.7358 | 5.7359 | 5.736 | 5.7361 | 5.7362 | 5.7363 | 5.7364 | 5.7365 | 5.7366 |  | 78.59% | 62.76% | 0% | 86011 | [7 empty] | 4.6052 | 1.1301
[6 empty] | 43782.8361 |  |  |  |  | 16.5449: Committed new connections: |  | 4.5073 | 3.5992 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-31 11:04 | 2019-07-18 16:46 | 0
| 681 | NORTH HOY | 33/11 | 1 x 0.2 |  | No PI | 0.10957 | 1 | 0 | 0 | 0.10957 | 0.10957 | 0.10957 | 0.10957 | 0.10957 | 0.10958 | 0.10958 | 0.10958 | 0.10958 | 0.10958 | 0.10959 | 0.10959 | 0.10959 | 0.10959 |  | 0% | 0% | 0% | 86130 | [7 empty] | 0.10957 | 0
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
| 587 | ORMLIE | 33/11 | 1 x 7.5 |  | 2019-12-17 11:04 | 5.3554 | 1 | 0 | 0 | 5.3554 | 5.3555 | 5.3556 | 5.3557 | 5.3558 | 5.3559 | 5.356 | 5.3561 | 5.3562 | 5.3562 | 5.3563 | 5.3564 | 5.3565 | 5.3566 |  | 75.26% | 65.56% | 0% | 86007 | [7 empty] | 5.4591 | -0.10373
[6 empty] | 43816.4611 |  |  |  |  | 16.5449: Committed new connections: |  | 4.0304 | 3.5109 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-04 12:20 | 2019-06-17 16:50 | 0
| 498 | ROUSAY | 33/11 | 1 x 2.5 |  | 2019-12-31 14:59 | 0.43765 | 1 | M | M | 0.43765 | 0.4436 | 0.44964 | 0.45576 | 0.46196 | 0.46824 | 0.47461 | 0.48107 | 0.48761 | 0.49425 | 0.50097 | 0.50779 | 0.5147 | 0.5217 |  | 76.36% | 69.81% | 0% | 86112 | [7 empty] | 0.34269 | 0.094959
[6 empty] | 43830.6243 |  |  |  |  | 16.5449: Committed new connections: |  | 0.33417 | 0.30553 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0.788 |  | 2019-10-21 20:48 | 2019-07-03 19:41 | 0
| 685 | SANDAY | 33/11 | 1 x 1 |  | 2019-12-17 11:09 | 0.79488 | 1 | 0 | 0 | 0.79488 | 0.79489 | 0.79491 | 0.79492 | 0.79494 | 0.79495 | 0.79497 | 0.79498 | 0.795 | 0.79501 | 0.79502 | 0.79504 | 0.79505 | 0.79507 |  | 85.25% | 68.22% | 0% | 86118 | [7 empty] | 0.79039 | 0.0044886
[6 empty] | 43816.4646 |  |  |  |  | 16.5449: Committed new connections: |  | 0.67764 | 0.54225 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-31 11:06 | 2019-06-06 18:16 | 0
| 683 | SHAPINSAY | 33/11 | 1 x 1 |  | 2019-12-31 18:08 | 0.43745 | 1 | 0 | 0 | 0.43745 | 0.43746 | 0.43746 | 0.43747 | 0.43748 | 0.43749 | 0.4375 | 0.4375 | 0.43751 | 0.43752 | 0.43753 | 0.43754 | 0.43754 | 0.43755 |  | 0% | 0% | 0% | 86122 | [7 empty] | 0.42 | 0.017448
[6 empty] | 43830.7556 |  |  |  |  | 16.5449: Committed new connections: |  | #VALUE! | No Data | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | #VALUE! | Missing Data | 0
| 679 | ST MARYS | 33/11 | 1 x 4 |  | 2020-03-19 18:59 | 2.2075 | 1 | 0 | 0 | 2.2075 | 2.2075 | 2.2076 | 2.2076 | 2.2076 | 2.2077 | 2.2077 | 2.2078 | 2.2078 | 2.2078 | 2.2079 | 2.2079 | 2.208 | 2.208 |  | 84.64% | 90.01% | 0% | 86127 | [7 empty] | 2.43 | -0.22253
[6 empty] | 43909.791 |  |  |  |  | 16.5449: Committed new connections: |  | 1.8684 | 1.987 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-09-12 14:38 | 2019-08-15 13:59 | 0
| 678 | STROMNESS | 33/11 | 2 x 15 |  | 2020-02-25 19:05 | 7.971 | 1 | 0 | 0 | 7.971 | 7.9712 | 7.9713 | 7.9715 | 7.9716 | 7.9718 | 7.9719 | 7.9721 | 7.9722 | 7.9724 | 7.9725 | 7.9726 | 7.9728 | 7.9729 |  | 82.79% | 73.02% | 0% | 86103 | 86105 | [6 empty] | 5.21 | 2.761
[6 empty] | 43886.7951 |  |  |  |  | 16.5449: Committed new connections: |  | 6.5995 | 5.8206 | 0 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 3.108 |  | 2019-10-29 20:20 | 2019-08-16 18:10 | 0
| 684 | STRONSAY | 33/11 | 1 x 1 |  | 2020-03-05 20:02 | 0.44734 | 1 | 0 | 0 | 0.44734 | 0.44735 | 0.44735 | 0.44736 | 0.44737 | 0.44738 | 0.44739 | 0.44739 | 0.4474 | 0.44741 | 0.44742 | 0.44743 | 0.44744 | 0.44744 |  | 75.35% | 54.45% | 0% | 86120 | [7 empty] | 0.44 | 0.0073377
[6 empty] | 43895.8347 |  |  |  |  | 16.5449: Committed new connections: |  | 0.33707 | 0.24356 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-20 21:48 | 2019-06-10 19:27 | 0
| 674 | WESTRAY | 33/11 | 1 x 4 |  | 2020-03-13 09:10 | 1.1973 | 1 | 0 | 0 | 1.1973 | 1.1973 | 1.1973 | 1.1973 | 1.1974 | 1.1974 | 1.1974 | 1.1974 | 1.1975 | 1.1975 | 1.1975 | 1.1975 | 1.1975 | 1.1976 |  | 92.36% | 95.38% | 0% | 86114 | [7 empty] | 1.0799 | 0.11741
[6 empty] | 43903.3819 |  |  |  |  | 16.5449: Committed new connections: |  | 1.1058 | 1.1419 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0.50842 |  | 2019-05-29 17:06 | 2019-08-30 12:08 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
TUMMEL BRIDGE | 260 |  | 132/11 | 2 x 21 |  | 2019-10-12 17:28 | 57.1458 | 1 |  | Diverse | 57.1458 | 57.1554 | 57.1653 | 57.1753 | 57.1857 | 57.1962 | 57.2071 | 57.2182 | 57.2295 | 57.2412 | 57.2531 | 57.2653 | 57.2778 | 57.2906 | Diversity/Losses: 0.237 | 100% | 11.65% | -67.43% | 20130 | [7 empty] | 13.8 | 43.3458
[6 empty] | 43750.7278 |  |  |  | Aggregate | 13.5336 | 13.5359 | 13.5383 | 13.5406 | 13.5431 | 13.5456 | 13.5482 | 13.5508 | 13.5535 | 13.5562 | 13.5591 | 13.5619 | 13.5649 | 13.5679 |  | 57.1458 | 6.6551 | -38.5314 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 16.5467: Generation at time of BSP peak:; 16.547: 0 |  | 2019-10-12 17:28 | 2019-07-17 21:31 | 2019-11-18 15:49
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 56.0029 | 56.0123 | 56.022 | 56.0318 | 56.042 | 56.0523 | 56.0629 | 56.0738 | 56.0849 | 56.0963 | 56.108 | 56.12 | 56.1323 | 56.1448
| 267 | ABERFELDY | 33/11 | 2 x 8 |  | 2020-02-29 09:30 | 2.3701 | 1 | 0 | 0 | 2.3701 | 2.3702 | 2.3702 | 2.3703 | 2.3703 | 2.3704 | 2.3704 | 2.3704 | 2.3705 | 2.3705 | 2.3706 | 2.3706 | 2.3707 | 2.3707 |  | 0% | 0% | 12.76% | 86236 | [7 empty] | 3.84 | -1.4699
[6 empty] | 43890.3958 |  |  |  |  | 16.5449: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.30255 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  |  |  | 2020-02-20 21:00
| 266 | BONSKEID | 33/11 | 1 x 5 |  | 2019-12-02 12:02 | 3.608 | 1 | 0 | 0 | 3.608 | 3.6081 | 3.6081 | 3.6082 | 3.6083 | 3.6083 | 3.6084 | 3.6085 | 3.6085 | 3.6086 | 3.6087 | 3.6087 | 3.6088 | 3.6089 |  | 93.89% | 70.44% | 0% | 86212 | [7 empty] | 3.44 | 0.16801
[6 empty] | 43801.5014 |  |  |  |  | 16.5449: Committed new connections: |  | 3.3875 | 2.5417 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-12 18:55 | 2019-08-01 12:51 | 0
| 265 | CALVINE | 33/11 | 1 x 2.5 |  | 2019-04-06 10:13 | 1.2576 | 1 | 0 | 0 | 1.2576 | 1.2576 | 1.2576 | 1.2576 | 1.2577 | 1.2577 | 1.2577 | 1.2577 | 1.2578 | 1.2578 | 1.2578 | 1.2578 | 1.2578 | 1.2579 |  | 100% | 75.03% | 0% | 86222 | [7 empty] | 1.19 | 0.06757
[6 empty] | 43561.4257 |  |  |  |  | 16.5449: Committed new connections: |  | 1.2576 | 0.94353 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-06 10:13 | 2019-06-02 11:32 | 0
| 268 | COSHIEVILLE | 33/11 | 1 x 2.5 |  | 2019-04-14 20:07 | 1.3503 | 1 | 0 | 0 | 1.3503 | 1.3504 | 1.3504 | 1.3504 | 1.3504 | 1.3505 | 1.3505 | 1.3505 | 1.3505 | 1.3506 | 1.3506 | 1.3506 | 1.3506 | 1.3507 |  | 100% | 83.27% | 0% | 86229 | [7 empty] | 1.75 | -0.39967
[6 empty] | 43569.8382 |  |  |  |  | 16.5449: Committed new connections: |  | 1.3503 | 1.1244 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-14 20:07 | 2019-08-07 05:36 | 0
| 276 | FINCASTLE | 33/11 | 1 x 0.1 |  | No PI | 0.075854 | 1 | H | H | 0.075854 | 0.077886 | 0.079972 | 0.082115 | 0.084314 | 0.086573 | 0.088892 | 0.091273 | 0.093718 | 0.096228 | 0.098806 | 0.10145 | 0.10417 | 0.10696 |  | 0% | 0% | 0% | 86220 | [7 empty] | 0.073045 | 0.0028094
[6 empty] | No PI |  |  |  |  | 16.5449: Committed new connections: |  | 0 | 0 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak: |  | 0 | 0 | 0
| 262 | KINLOCH RANNOCH | 33/11 | 1 x 2.5 |  | 2019-11-19 11:30 | 0.96479 | 1 | 0 | 0 | 0.96479 | 0.96481 | 0.96483 | 0.96485 | 0.96486 | 0.96488 | 0.9649 | 0.96492 | 0.96494 | 0.96495 | 0.96497 | 0.96499 | 0.96501 | 0.96502 |  | 0% | 0% | 18.02% | 86225 | [7 empty] | 0.99521 | -0.030415
[6 empty] | 43788.4792 |  |  |  |  | 16.5449: Committed new connections: |  | Manual Calculation | Manual Calculation | 0.17385 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 1.6098 |  |  |  | 2019-07-26 01:30
| 263 | PITLOCHRY | 33/11 | 2 x 5 |  | 2019-11-19 17:08 | 3.0695 | 1 | 0 | 0 | 3.0695 | 3.0695 | 3.0696 | 3.0697 | 3.0697 | 3.0698 | 3.0698 | 3.0699 | 3.0699 | 3.07 | 3.0701 | 3.0701 | 3.0702 | 3.0702 |  | 96.88% | 69.53% | 0% | 86216 | [7 empty] | 3.6427 | -0.57319
[6 empty] | 43788.7139 |  |  |  |  | 16.5449: Committed new connections: |  | 2.9736 | 2.1343 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-04-16 12:03 | 2019-07-03 17:27 | 0
| 260 | TUMMEL BRIDGE | 33/11 | 1 x 2.5 |  | 2020-03-03 12:16 | 0.83745 | 1 | 0 | 0 | 0.83745 | 0.83747 | 0.83748 | 0.8375 | 0.83751 | 0.83753 | 0.83754 | 0.83756 | 0.83757 | 0.83759 | 0.8376 | 0.83762 | 0.83763 | 0.83765 |  | 97.56% | 67.78% | 0% | 86241 | [7 empty] | 0.66
[6 empty] | 43893.5111 |  |  |  |  | 16.5449: Committed new connections: |  | 0.81698 | 0.5676 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 16.5467: Generation at time of peak:; 16.547: 0 |  | 2019-10-28 20:02 | 2019-06-12 09:28 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
WILLOWDALE | 983 |  | 132/33 | 2 x 60 |  | 2019-11-19 17:43 | 31.2109 | 1 |  | Diverse | 31.2109 | 31.2115 | 31.212 | 31.2126 | 31.2132 | 31.2137 | 31.2143 | 31.2149 | 31.2155 | 31.216 | 31.2166 | 31.2172 | 31.2177 | 31.2183 | Diversity/Losses: 1.194 | 93.82% | 84.57% | 29.76% | 20230 | [7 empty] | 36.4 | -5.1891
[6 empty] | 43788.7382 |  |  |  | Aggregate | 37.2517 | 37.2524 | 37.2531 | 37.2538 | 37.2545 | 37.2551 | 37.2558 | 37.2565 | 37.2572 | 37.2579 | 37.2585 | 37.2592 | 37.2599 | 37.2606 |  | 29.2819 | 26.3956 | 9.2899 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 37.2558: Generation at time of BSP peak:; 37.2565: 0 |  | 2019-04-03 12:05 | 2019-06-13 16:51 | 2019-08-30 04:39
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 30.5867 | 30.5872 | 30.5878 | 30.5884 | 30.5889 | 30.5895 | 30.59 | 30.5906 | 30.5911 | 30.5917 | 30.5923 | 30.5928 | 30.5934 | 30.5939
| 841 | DENBURN | 33/11 | 2 x 21 |  | 2019-11-19 11:38 | 13.9625 | 1 | 0 | 0 | 13.9625 | 13.9628 | 13.963 | 13.9633 | 13.9635 | 13.9638 | 13.964 | 13.9643 | 13.9646 | 13.9648 | 13.9651 | 13.9653 | 13.9656 | 13.9658 |  | 88.75% | 81.72% | 0% | 86320 | [7 empty] | 14.72 | -0.75749
[6 empty] | 43788.4847 |  |  |  |  | 37.2517: Committed new connections: |  | 12.3923 | 11.41 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 37.2558: Generation at time of peak:; 37.2565: 0 |  | 2019-04-03 12:17 | 2019-06-13 12:58 | 0
| 861 | GREYFRIARS | 33/11 | 2 x 24 |  | 2019-11-19 18:02 | 7.5457 | 1 | 0 | 0 | 7.5457 | 7.5458 | 7.546 | 7.5461 | 7.5463 | 7.5464 | 7.5465 | 7.5467 | 7.5468 | 7.547 | 7.5471 | 7.5472 | 7.5474 | 7.5475 |  | 91.34% | 64.26% | 0% | 86314 | [7 empty] | 8.3 | -0.75429
[6 empty] | 43788.7514 |  |  |  |  | 37.2517: Committed new connections: |  | 6.8926 | 4.8489 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 37.2558: Generation at time of peak:; 37.2565: 0 |  | 2019-10-28 18:28 | 2019-06-26 19:37 | 0
| 867 | HAYTON | 33/11 | 2 x 23 |  | 2020-02-04 09:16 | 5.4114 | 1 | 0 | 0 | 5.4114 | 5.4115 | 5.4116 | 5.4117 | 5.4118 | 5.4119 | 5.412 | 5.4121 | 5.4122 | 5.4123 | 5.4124 | 5.4125 | 5.4126 | 5.4127 |  | 93.16% | 66.8% | 0% | 86302 | [7 empty] | 5.5 | -0.088597
[6 empty] | 43865.3861 |  |  |  |  | 37.2517: Committed new connections: |  | 5.0412 | 3.6147 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 37.2558: Generation at time of peak:; 37.2565: 0.51177 |  | 2019-10-28 17:54 | 2019-06-24 17:42 | 0
| 917 | NORTHFIELD | 33/11 | 2 x 15 |  | 2019-04-16 17:16 | 3.856 | 1 | 0 | 0 | 3.856 | 3.8561 | 3.8561 | 3.8562 | 3.8563 | 3.8563 | 3.8564 | 3.8565 | 3.8566 | 3.8566 | 3.8567 | 3.8568 | 3.8568 | 3.8569 |  | 0% | 99.03% | 0% | 86305 | [7 empty] | 4.6688 | -0.81282
[6 empty] | 43571.7194 |  |  |  |  | 37.2517: Committed new connections: |  | #VALUE! | 3.8188 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 37.2558: Generation at time of peak:; 37.2565: 0 |  | #VALUE! | 2019-06-24 17:43 | 0
| 958 | ST NICHOLAS | 33/11 | 2 x 12.5 |  | 2019-11-19 15:01 | 6.4761 | 1 | 0 | 0 | 6.4761 | 6.4762 | 6.4764 | 6.4765 | 6.4766 | 6.4767 | 6.4768 | 6.4769 | 6.4771 | 6.4772 | 6.4773 | 6.4774 | 6.4775 | 6.4777 |  | 87.62% | 75.74% | 0% | 86324 | [7 empty] | 6.7705 | -0.29439
[6 empty] | 43788.6257 |  |  |  |  | 37.2517: Committed new connections: |  | 5.6746 | 4.9052 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 37.2558: Generation at time of peak:; 37.2565: 0 |  | 2019-10-31 15:03 | 2019-06-13 15:06 | 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2019 / 20 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2019 / 2020 | 2020 / 2021 | 2021 / 2022 | 2022 / 2023 | 2023 / 2024 | 2024 / 2025 | 2025 / 2026 | 2026 / 2027 | 2027 / 2028 | 2028 / 2029 | 2029 / 2030 | 2030 / 2031 | 2031 / 2032 | 2032 / 2033 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 2018/19 Peak (MW) | Change
WOODHILL | 986 |  | 132/33 | 2 x 90 |  | 2019-12-12 17:32 | 45.0432 | 1 |  | Diverse | 45.0432 | 45.2743 | 45.5085 | 45.746 | 45.9866 | 46.2305 | 46.4778 | 46.7283 | 46.9823 | 47.2398 | 47.5007 | 47.7652 | 48.0332 | 48.3049 | Diversity/Losses: 1.008 | 87.65% | 77.99% | 19.7% | 20330 | [7 empty] | 33.4 | 11.6432
[6 empty] | 43811.7306 |  |  |  | Aggregate | 45.3867 | 45.6196 | 45.8556 | 46.0948 | 46.3373 | 46.5831 | 46.8322 | 47.0847 | 47.3406 | 47.6 | 47.8629 | 48.1294 | 48.3995 | 48.6733 |  | 39.4785 | 35.1272 | 8.8745 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 37.2558: Generation at time of BSP peak:; 37.2565: 0 |  | 2019-10-07 12:14 | 2019-08-30 11:09 | 2019-07-19 02:38
[6 empty] | Power Factor: | 0.98 |  |  | Div. (MW) | 44.1423 | 44.3688 | 44.5984 | 44.831 | 45.0669 | 45.3059 | 45.5482 | 45.7938 | 46.0427 | 46.295 | 46.5507 | 46.8099 | 47.0726 | 47.3388
| 932 | QUEENS LANE NORTH | 33/11 | 2 x 12.5 |  | 2020-02-14 14:46 | 10.1153 | 1 | 0 | 0 | 10.1153 | 10.1155 | 10.1157 | 10.1159 | 10.1161 | 10.1163 | 10.1164 | 10.1166 | 10.1168 | 10.117 | 10.1172 | 10.1174 | 10.1176 | 10.1177 |  | 95.59% | 73.87% | 0% | 86400 | [7 empty] | 12.9621 | -2.8467
[6 empty] | 43875.6153 |  |  |  |  | 37.2517: Committed new connections: |  | 9.6697 | 7.4718 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 37.2558: Generation at time of peak:; 37.2565: 0 |  | 2019-04-15 17:45 | 2019-06-13 12:21 | 0
| 943 | SPRINGHILL | 33/11 | 2 x 21 |  | 2019-11-19 17:19 | 17.0787 | 1 | M | M | 17.0787 | 17.3111 | 17.5466 | 17.7853 | 18.0273 | 18.2725 | 18.5211 | 18.7731 | 19.0285 | 19.2874 | 19.5498 | 19.8158 | 20.0854 | 20.3586 |  | 86.01% | 62.03% | 0% | 86405 | [7 empty] | 15.92 | 1.1587
[6 empty] | 43788.7215 |  |  |  |  | 37.2517: Committed new connections: |  | 14.6899 | 10.5933 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 37.2558: Generation at time of peak:; 37.2565: 0 |  | 2019-10-29 17:39 | 2019-06-12 17:43 | 0
| 986 | WOODHILL | 33/11 | 2 x 24 |  | 2019-08-01 14:07 | 18.1926 | 1 | 0 | 0 | 18.1926 | 18.193 | 18.1933 | 18.1936 | 18.194 | 18.1943 | 18.1946 | 18.195 | 18.1953 | 18.1956 | 18.1959 | 18.1963 | 18.1966 | 18.1969 |  | 90.33% | 100% | 0% | 86403 | [7 empty] | 14.3 | 3.8926
[6 empty] | 43678.5882 |  |  |  |  | 37.2517: Committed new connections: |  | 16.4333 | 18.1926 | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 37.2558: Generation at time of peak:; 37.2565: 6.6256 |  | 2019-10-04 11:10 | 2019-08-01 14:07 | 0

## MASTER 2018-19
SHEPD | [10 empty] | 2018/19
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8 | 17/18 | Change
ABERNETHY | 242 |  | 132/33 | 2 x 60 |  |  | 38.1 | 1 |  | Diverse | 38.1 | 38.1796 | 38.2611 | 38.3446 | 38.4301 | 38.5177 | 38.6074 | 38.6992 | 38.7934 | 38.8898 | 38.9886 | 39.0898 | 39.1935 | 39.2997 | Diversity/Losses: 1.069 | 0% | 0% | 30.18% | 10130
[10 empty] | Aggregate | 40.722 | 40.8071 | 40.8942 | 40.9835 | 41.0748 | 41.1684 | 41.2643 | 41.3625 | 41.4631 | 41.5662 | 41.6718 | 41.7799 | 41.8908 | 42.0043 |  |  |  | 11.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 37.7952 | 37.8742 | 37.955 | 38.0378 | 38.1226 | 38.2095 | 38.2985 | 38.3897 | 38.483 | 38.5787 | 38.6767 | 38.7771 | 38.8799 | 38.9853
| 242 | ABERNETHY | 33/11 | 1 x 2.5 |  | 2018-11-26 | 2.78 | 1 | H | H | 2.78 | 2.8545 | 2.9309 | 3.0094 | 3.0901 | 3.1728 | 3.2578 | 3.3451 | 3.4347 | 3.5267 | 3.6212 | 3.7182 | 3.8178 | 3.9201 |  | 0% | 0% | 0% | 80048 | [7 empty] | 3.08 | -0.3
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 255 | BALBEGGIE | 33/11 | 1 x 5 |  | 2018-12-05 | 3.89 | 1 | 0 | 0 | 3.89 | 3.8901 | 3.8901 | 3.8902 | 3.8903 | 3.8904 | 3.8904 | 3.8905 | 3.8906 | 3.8906 | 3.8907 | 3.8908 | 3.8909 | 3.8909 |  | 0% | 0% | 15.94% | 80005 | [7 empty] | 4.2162 | -0.32625
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.62 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 279 | BRIDGE OF EARN | 33/11 | 2 x 15 |  | 2018-11-26 | 3.28 | 1 | 0 | 0 | 3.28 | 3.2801 | 3.2801 | 3.2802 | 3.2802 | 3.2803 | 3.2804 | 3.2804 | 3.2805 | 3.2805 | 3.2806 | 3.2807 | 3.2807 | 3.2808 |  | 0% | 0% | 17.07% | 80028 | [7 empty] | 3.62 | -0.34
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.56 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 254 | ERROL | 33/11 | 2 x 5 |  | 2019-01-22 | 4.55 | 1 | 0 | 0 | 4.55 | 4.5501 | 4.5502 | 4.5502 | 4.5503 | 4.5504 | 4.5505 | 4.5506 | 4.5507 | 4.5507 | 4.5508 | 4.5509 | 4.551 | 4.5511 |  | 0% | 0% | 22.86% | 80013 | [7 empty] | 4.5778 | -0.027753
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.04 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 273 | GLENDEVON | 33/11 | 1 x 8 |  | 2019-01-29 | 1.7943 | 1 | L | L | 1.7943 | 1.8042 | 1.8142 | 1.8243 | 1.8344 | 1.8445 | 1.8548 | 1.865 | 1.8754 | 1.8858 | 1.8962 | 1.9067 | 1.9173 | 1.9279 |  | 0% | 0% | 0.002449% | 80033 | [7 empty] | 1.7 | 0.094273
|  | Poor Data |  |  |  | 19:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4.3945e-05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 251 | MILNATHORT | 33/11 | 2 x 15 |  | 2019-01-23 | 11.0647 | 1 | 0 | 0 | 11.0647 | 11.0649 | 11.0651 | 11.0653 | 11.0655 | 11.0657 | 11.0659 | 11.0661 | 11.0663 | 11.0665 | 11.0667 | 11.0669 | 11.0671 | 11.0673 |  | 0% | 0% | 26.53% | 80037 | [7 empty] | 11.4662 | -0.40157
[6 empty] | 2019-01-23: 17:30; 11.0647: Committed new connections: |  |  |  | 2.9358 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 11.0659: Generation at time of peak:; 0 11.0661: 0
| 247 | HARBOUR | 33/11 | 2 x 9.5/20 |  | 2018-12-05 | 9.2331 | 1 | 0 | 0 | 9.2331 | 9.2333 | 9.2334 | 9.2336 | 9.2338 | 9.2339 | 9.2341 | 9.2343 | 9.2345 | 9.2346 | 9.2348 | 9.235 | 9.2351 | 9.2353 |  | 0% | 0% | 28.08% | 80019 | [7 empty] | 10.24 | -1.0069
[6 empty] | 2019-01-23: 12:00; 11.0647: Committed new connections: |  |  |  | 2.5928 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 11.0659: Generation at time of peak:; 0 11.0661: 0
| 271 | SCONE | 33/11 | 2 x 7.5/15 |  | 2018-12-01 | 4.13 | 1 | 0 | 0 | 4.13 | 4.1301 | 4.1302 | 4.1302 | 4.1303 | 4.1304 | 4.1305 | 4.1305 | 4.1306 | 4.1307 | 4.1308 | 4.1308 | 4.1309 | 4.131 |  | 0% | 0% | 21.79% | 80008 | [7 empty] | 4.4032 | -0.27317
[6 empty] | 2019-01-23: 18:00; 11.0647: Committed new connections: |  |  |  | 0.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 11.0659: Generation at time of peak:; 0 11.0661: 0
|  | SCOTTISH POWER |  |  |  | 2018-11-12 | 4.83 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 80039 | 80041 | 80042
[6 empty] | 2019-01-23: 18:30; 11.0647: Committed new connections: |  |  |  | 0 | 33.3% | 33.3% | 33.3% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: |  |  |  | Generation at time of peak: 11.0659: Generation at time of peak:; 0 11.0661: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
ALNESS | 502 |  | 132/33 | 2 x 120 |  |  | 35.1 | 1 |  | Diverse | 35.1 | 35.2405 | 35.3848 | 35.533 | 35.6851 | 35.8412 | 36.0015 | 36.1661 | 36.3351 | 36.5086 | 36.6868 | 36.8697 | 37.0575 | 37.2503 | Diversity/Losses: 0.994 | 0% | 0% | 21.37% | 10330
[10 empty] | Aggregate | 34.8832 | 35.0229 | 35.1662 | 35.3135 | 35.4646 | 35.6198 | 35.7791 | 35.9427 | 36.1107 | 36.2831 | 36.4602 | 36.6419 | 36.8286 | 37.0202 |  |  |  | 7.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 34.8192 | 34.9586 | 35.1018 | 35.2487 | 35.3996 | 35.5545 | 35.7135 | 35.8768 | 36.0445 | 36.2166 | 36.3933 | 36.5747 | 36.761 | 36.9523
| 552 | BALALDIE | 33/11 | 1 x 4 |  | 2019-01-29 | 2.98 | 1 | H | H | 2.98 | 3.0598 | 3.1418 | 3.226 | 3.3124 | 3.4011 | 3.4922 | 3.5858 | 3.6818 | 3.7804 | 3.8817 | 3.9857 | 4.0924 | 4.2021 |  | 0% | 0% | 15.44% | 80109 | [7 empty] | 3.0968 | -0.11679
[6 empty] | 21:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.46 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 509 | BLACKSTAND | 33/11 | 1 x 6 |  | 2019-02-06 | 2.65 | 1 | 0 | 0 | 2.65 | 2.65 | 2.6501 | 2.6501 | 2.6502 | 2.6502 | 2.6503 | 2.6503 | 2.6504 | 2.6504 | 2.6505 | 2.6505 | 2.6506 | 2.6506 |  | 0% | 0% | 21.89% | 80157 | [7 empty] | 2.9061 | -0.25609
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.58 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 541 | CONTULLICH | 33/11 | 1 x 0.1 |  |  | 0.039332 | 1 | 0 | 0 | 0.039332 | 0.039332 | 0.039333 | 0.039334 | 0.039335 | 0.039335 | 0.039336 | 0.039337 | 0.039337 | 0.039338 | 0.039339 | 0.03934 | 0.03934 | 0.039341 |  | 0% | 0% | 0% | 80128 | [7 empty] | 0.04 | -0.00066828
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 551 | CROSSHILLS | 33/11 | 2 x 15 |  | 2019-01-24 | 6.54 | 1 | 0 | 0 | 6.54 | 6.5401 | 6.5402 | 6.5404 | 6.5405 | 6.5406 | 6.5407 | 6.5408 | 6.541 | 6.5411 | 6.5412 | 6.5413 | 6.5414 | 6.5416 |  | 0% | 0% | 28.75% | 80125 | [7 empty] | 6.659 | -0.119
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.88 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 522 | GLASTULLICH | 33/11 | 1 x 8 |  | 2019-01-31 | 1.35 | 1 | 0 | 0 | 1.35 | 1.35 | 1.35 | 1.3501 | 1.3501 | 1.3501 | 1.3501 | 1.3502 | 1.3502 | 1.3502 | 1.3502 | 1.3503 | 1.3503 | 1.3503 |  | 0% | 0% | 2.963% | 80111 | [7 empty] | 1.42 | -0.070008
[6 empty] | 20:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.04 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 559 | INVERGORDON | 33/11 | 2 x 15 |  | 2019-03-11 | 8.5 | 1 | 0 | 0 | 8.5 | 8.5002 | 8.5003 | 8.5005 | 8.5006 | 8.5008 | 8.5009 | 8.5011 | 8.5012 | 8.5014 | 8.5016 | 8.5017 | 8.5019 | 8.502 |  | 0% | 0% | 23.29% | 80138 | [7 empty] | 9.9898 | -1.4898
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.98 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 576 | LEALTY | 33/11 | 1 x 0.5 |  |  | 0 | 1 | ? | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 80150 | [7 empty] | 0.09 | -0.09
|  | No PI & No Customers | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 542 | MUIREND | 33/11 | 1 x 6 |  | 2018-12-25 | 2.4282 | 1 | 0 | 0 | 2.4282 | 2.4283 | 2.4283 | 2.4284 | 2.4284 | 2.4285 | 2.4285 | 2.4285 | 2.4286 | 2.4286 | 2.4287 | 2.4287 | 2.4288 | 2.4288 |  | 0% | 0% | 19.19% | 80160 | [7 empty] | 2.5844 | -0.15612
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.46587 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 554 | NIGG | 33/11 | 1 x 15 |  | 2019-01-23 | 2.2138 | 1 | H | H | 2.2138 | 2.2731 | 2.334 | 2.3966 | 2.4608 | 2.5267 | 2.5944 | 2.6638 | 2.7352 | 2.8085 | 2.8837 | 2.961 | 3.0403 | 3.1217 |  | 0% | 0% | 12.64% | 80117 | [7 empty] | 1.5493 | 0.66452
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.27989 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 553 | PEDDIESTON | 33/11 | 2 x 2.5 |  | 2018-12-25 | 1.7018 | 1 | 0 | 0 | 1.7018 | 1.7018 | 1.7018 | 1.7019 | 1.7019 | 1.7019 | 1.702 | 1.702 | 1.702 | 1.7021 | 1.7021 | 1.7021 | 1.7022 | 1.7022 |  | 0% | 0% | 19.05% | 80132 | [7 empty] | 1.76 | -0.058219
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.32415 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 546 | TAIN | 33/11 | 2 x 15 |  | 2019-01-29 | 6.48 | 1 | 0 | 0 | 6.48 | 6.4801 | 6.4802 | 6.4804 | 6.4805 | 6.4806 | 6.4807 | 6.4808 | 6.4809 | 6.4811 | 6.4812 | 6.4813 | 6.4814 | 6.4815 |  | 0% | 0% | 21.3% | 80105 | [7 empty] | 6.5718 | -0.091755
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.38 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
ARBROATH | 61 |  | 132/33 | 2 x 45 |  |  | 30.9 | 1 |  | Diverse | 30.9 | 30.9006 | 30.9011 | 30.9017 | 30.9023 | 30.9028 | 30.9034 | 30.9039 | 30.9045 | 30.9051 | 30.9056 | 30.9062 | 30.9068 | 30.9073 | Diversity/Losses: 1.093 | 0% | 0% | 30.1% | 10430
[10 empty] | Aggregate | 33.7769 | 33.7775 | 33.7781 | 33.7787 | 33.7793 | 33.7799 | 33.7806 | 33.7812 | 33.7818 | 33.7824 | 33.783 | 33.7836 | 33.7843 | 33.7849 |  |  |  | 9.3 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 30.6528 | 30.6534 | 30.6539 | 30.6545 | 30.655 | 30.6556 | 30.6562 | 30.6567 | 30.6573 | 30.6578 | 30.6584 | 30.659 | 30.6595 | 30.6601
| 64 | CARNOUSTIE | 33/11 | 2 x 15 |  | 2019-01-23 | 7.64 | 1 | 0 | 0 | 7.64 | 7.6401 | 7.6403 | 7.6404 | 7.6406 | 7.6407 | 7.6408 | 7.641 | 7.6411 | 7.6413 | 7.6414 | 7.6415 | 7.6417 | 7.6418 |  | 0% | 0% | 25.26% | 80206 | [7 empty] | 8.16 | -0.52
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.93 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 62 | CHARLES AVENUE | 33/11 | 2 x 10 |  | 2018-12-05 | 9.18 | 1 | 0 | 0 | 9.18 | 9.1802 | 9.1803 | 9.1805 | 9.1807 | 9.1808 | 9.181 | 9.1812 | 9.1813 | 9.1815 | 9.1817 | 9.1818 | 9.182 | 9.1822 |  | 0% | 0% | 29.52% | 80218 | [7 empty] | 9.71 | -0.53
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.71 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 68 | ELLIOT DEPOT | 33/11 | 1 x 15 |  | 2018-12-05 | 5.04 | 1 | 0 | 0 | 5.04 | 5.0401 | 5.0402 | 5.0403 | 5.0404 | 5.0405 | 5.0406 | 5.0406 | 5.0407 | 5.0408 | 5.0409 | 5.041 | 5.0411 | 5.0412 |  | 0% | 0% | 26.79% | 80215 | [7 empty] | 5.3959 | -0.35586
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.35 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 67 | HUME STREET | 33/11 | 2 x 24 |  | 2018-12-18 | 9.01 | 1 | 0 | 0 | 9.01 | 9.0102 | 9.0103 | 9.0105 | 9.0107 | 9.0108 | 9.011 | 9.0112 | 9.0113 | 9.0115 | 9.0116 | 9.0118 | 9.012 | 9.0121 |  | 0% | 0% | 24.31% | 80222 | [7 empty] | 9.4316 | -0.4216
[6 empty] | 15:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.19 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 66 | REDFORD | 33/11 | 1 x 4/8 |  | 2018-11-05 | 2.9069 | 1 | 0 | 0 | 2.9069 | 2.9069 | 2.907 | 2.907 | 2.9071 | 2.9071 | 2.9072 | 2.9072 | 2.9073 | 2.9073 | 2.9074 | 2.9074 | 2.9075 | 2.9076 |  | 0% | 0% | 2.652% | 80202 | [7 empty] | 2.84 | 0.066862
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.077076 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
BEAULY | 506 |  | 132/33 | 2 x 45 |  |  | 31.4 | 1 |  | Diverse | 31.4 | 31.5952 | 31.793 | 31.9934 | 32.1964 | 32.4022 | 32.6107 | 32.8219 | 33.036 | 33.2529 | 33.4727 | 33.6954 | 33.9211 | 34.1497 | Diversity/Losses: 0.94 | 0% | 0% | 23.57% | 10630
[10 empty] | Aggregate | 29.5114 | 29.6948 | 29.8807 | 30.0691 | 30.2599 | 30.4533 | 30.6493 | 30.8478 | 31.049 | 31.2529 | 31.4594 | 31.6687 | 31.8808 | 32.0957 |  |  |  | 7.4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 31.1488 | 31.3424 | 31.5386 | 31.7374 | 31.9389 | 32.143 | 32.3498 | 32.5594 | 32.7717 | 32.9869 | 33.2049 | 33.4258 | 33.6497 | 33.8765
| 501 | AIGAS | 33/11 | 1 x 0.5 |  |  | 0.19104 | 1 | 0 | 0 | 0.19104 | 0.19104 | 0.19105 | 0.19105 | 0.19105 | 0.19106 | 0.19106 | 0.19106 | 0.19107 | 0.19107 | 0.19107 | 0.19108 | 0.19108 | 0.19109 |  | 0% | 0% | 0% | 80336 | [7 empty] | 0.3 | -0.10896
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 562 | COMRIE | 33/11 | 1 x 0.05 |  |  | 0.028094 | 1 | 0 | 0 | 0.028094 | 0.028095 | 0.028095 | 0.028096 | 0.028096 | 0.028097 | 0.028097 | 0.028098 | 0.028098 | 0.028099 | 0.028099 | 0.0281 | 0.0281 | 0.028101 |  | 0% | 0% | 0% | 80341 | [7 empty] | 0.03 | -0.0019059
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 513 | CONON BRIDGE | 33/11 | 2 x 6.25 |  | 2018-04-03 | 2.99 | 1 | 0 | 0 | 2.99 | 2.9901 | 2.9901 | 2.9902 | 2.9902 | 2.9903 | 2.9903 | 2.9904 | 2.9904 | 2.9905 | 2.9905 | 2.9906 | 2.9907 | 2.9907 |  | 0% | 0% | 9.699% | 80322 | [7 empty] | 3.71 | -0.72
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.29 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 514 | CONON FALLS | 33/11 | 1 x 0.5 |  |  | 0.35679 | 1 | M | M | 0.35679 | 0.36165 | 0.36657 | 0.37156 | 0.37661 | 0.38174 | 0.38693 | 0.39219 | 0.39753 | 0.40294 | 0.40842 | 0.41397 | 0.41961 | 0.42532 |  | 0% | 0% | 0% | 80345 | [7 empty] | 0.34 | 0.016795
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 515 | DINGWALL | 33/11 | 2 x 15 |  | 2018-12-05 | 9.45 | 1 | 0 | 0 | 9.45 | 9.4502 | 9.4503 | 9.4505 | 9.4507 | 9.4509 | 9.451 | 9.4512 | 9.4514 | 9.4516 | 9.4517 | 9.4519 | 9.4521 | 9.4522 |  | 0% | 0% | 12.7% | 80302 | [7 empty] | 10.0235 | -0.57346
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 520 | KILTARLITY | 33/11 | 1 x 6 |  | 2018-12-25 | 1.324 | 1 | L | L | 1.324 | 1.3313 | 1.3387 | 1.3461 | 1.3536 | 1.3611 | 1.3686 | 1.3762 | 1.3838 | 1.3915 | 1.3992 | 1.407 | 1.4148 | 1.4226 |  | 0% | 0% | 18.35% | 80361 | [7 empty] | 3.88 | -2.556
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.243 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 538 | MARYBANK | 33/11 | 1 x 4 |  | 2019-02-01 | 1.32 | 1 | 0 | 0 | 1.32 | 1.32 | 1.32 | 1.3201 | 1.3201 | 1.3201 | 1.3201 | 1.3202 | 1.3202 | 1.3202 | 1.3202 | 1.3203 | 1.3203 | 1.3203 |  | 0% | 0% | 0.7576% | 80316 | [7 empty] | 1.3883 | -0.06826
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.01 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 547 | MUIR OF ORD | 33/11 | 2 x 12/24 |  | 2019-01-20 | 12.5677 | 1 | M | M | 12.5677 | 12.7387 | 12.912 | 13.0877 | 13.2657 | 13.4462 | 13.6291 | 13.8146 | 14.0025 | 14.193 | 14.3861 | 14.5818 | 14.7802 | 14.9813 |  | 0% | 0% | 21.29% | 80327 | [7 empty] | 13.2298 | -0.66206
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.6756 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 558 | NORTH KESSOCK | 33/11 | 1 x 4 |  | 2018-12-24 | 1.2838 | 1 | 0 | 0 | 1.2838 | 1.2838 | 1.2838 | 1.2838 | 1.2838 | 1.2839 | 1.2839 | 1.2839 | 1.2839 | 1.284 | 1.284 | 1.284 | 1.284 | 1.2841 |  | 0% | 0% | 11.47% | 80339 | [7 empty] | 1.3676 | -0.083802
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.14725 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
BOAT OF GARTEN | 707 |  | 132/33 | 2 x 60 |  |  | 27.9 | 1 |  | Diverse | 27.9 | 28.0443 | 28.1905 | 28.3388 | 28.489 | 28.6413 | 28.7957 | 28.9521 | 29.1107 | 29.2714 | 29.4343 | 29.5994 | 29.7668 | 29.9364 | Diversity/Losses: 1.053 | 0% | 0% | 29.39% | 10830
[10 empty] | Aggregate | 29.37 | 29.5219 | 29.6758 | 29.8319 | 29.99 | 30.1504 | 30.3128 | 30.4775 | 30.6445 | 30.8137 | 30.9851 | 31.159 | 31.3351 | 31.5137 |  |  |  | 8.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 27.6768 | 27.8199 | 27.965 | 28.1121 | 28.2611 | 28.4122 | 28.5653 | 28.7205 | 28.8778 | 29.0372 | 29.1988 | 29.3626 | 29.5287 | 29.6969
| 704 | AVIEMORE | 33/11 | 2 x 24 |  | 2019-02-03 | 9.48 | 1 | 0 | 0 | 9.48 | 9.4802 | 9.4803 | 9.4805 | 9.4807 | 9.4809 | 9.481 | 9.4812 | 9.4814 | 9.4816 | 9.4817 | 9.4819 | 9.4821 | 9.4823 |  | 0% | 0% | 21.94% | 80416 | [7 empty] | 9.5524 | -0.072398
[6 empty] | 3:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.08 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 706 | BALLINDALLOCH | 33/11 | 2 x 5 |  | 2018-12-13 | 3.95 | 1 | M | M | 3.95 | 4.0037 | 4.0582 | 4.1134 | 4.1694 | 4.2261 | 4.2836 | 4.3419 | 4.401 | 4.4608 | 4.5215 | 4.583 | 4.6454 | 4.7086 |  | 0% | 0% | 15.7% | 80410 | [7 empty] | 3.888 | 0.062
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.62 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 708 | BOAT OF GARTEN 11 kV | 33/11 | 2 x 8 |  | 2019-02-03 | 3.43 | 1 | 0 | 0 | 3.43 | 3.4301 | 3.4301 | 3.4302 | 3.4303 | 3.4303 | 3.4304 | 3.4304 | 3.4305 | 3.4306 | 3.4306 | 3.4307 | 3.4308 | 3.4308 |  | 0% | 0% | 18.95% | 80412 | [7 empty] | 3.6769 | -0.24688
[6 empty] | 3:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.65 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 777 | DALWHINNIE | 33/11 | 1 x 1 |  | 2019-01-31 | 0.75 | 1 | 0 | 0 | 0.75 | 0.75001 | 0.75003 | 0.75004 | 0.75005 | 0.75007 | 0.75008 | 0.7501 | 0.75011 | 0.75012 | 0.75014 | 0.75015 | 0.75016 | 0.75018 |  | 0% | 0% | 24% | 80429 | [7 empty] | 0.767 | -0.017
[6 empty] | 19:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.18 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 722 | GRANTOWN | 33/11 | 2 x 15 |  | 2019-02-01 | 6.42 | 1 | M | M | 6.42 | 6.5073 | 6.5959 | 6.6856 | 6.7766 | 6.8688 | 6.9622 | 7.0569 | 7.1529 | 7.2503 | 7.3489 | 7.4489 | 7.5502 | 7.6529 |  | 0% | 0% | 16.82% | 80405 | [7 empty] | 6.5342 | -0.11425
[6 empty] | 3:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.08 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 727 | KINGUSSIE | 33/11 | 2 x 7 |  | 2019-02-01 | 4.57 | 1 | 0 | 0 | 4.57 | 4.5701 | 4.5702 | 4.5703 | 4.5703 | 4.5704 | 4.5705 | 4.5706 | 4.5707 | 4.5708 | 4.5708 | 4.5709 | 4.571 | 4.5711 |  | 0% | 0% | 15.32% | 80422 | [7 empty] | 5.04 | -0.47
[6 empty] | 3:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.7 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 738 | TOMATIN | 33/11 | 1 x 2 |  | 2019-02-04 | 0.77 | 1 | M | M | 0.77 | 0.78048 | 0.79109 | 0.80186 | 0.81277 | 0.82382 | 0.83503 | 0.84639 | 0.85791 | 0.86958 | 0.88141 | 0.8934 | 0.90556 | 0.91788 |  | 0% | 0% | 12.99% | 80403 | [7 empty] | 0.71196 | 0.05804
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
BRACO WEST | 290 |  | 275/33 | 2 x 120 |  |  | 42.4 | 1 |  | Diverse | 42.4 | 42.4008 | 42.4015 | 42.4023 | 42.4031 | 42.4039 | 42.4046 | 42.4054 | 42.4062 | 42.407 | 42.4077 | 42.4085 | 42.4093 | 42.4101 | Diversity/Losses: 0.945 | 0% | 0% | 38.44% | 10930
[10 empty] | Aggregate | 40.08 | 40.0807 | 40.0815 | 40.0822 | 40.0829 | 40.0837 | 40.0844 | 40.0851 | 40.0859 | 40.0866 | 40.0873 | 40.088 | 40.0888 | 40.0895 |  |  |  | 16.3 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 42.0608 | 42.0616 | 42.0623 | 42.0631 | 42.0639 | 42.0646 | 42.0654 | 42.0662 | 42.0669 | 42.0677 | 42.0685 | 42.0692 | 42.07 | 42.0708
| 210 | CALLANDER | 33/11 | 1 x 5 |  | 2018-04-04 | 4.57 | 1 | 0 | 0 | 4.57 | 4.5701 | 4.5702 | 4.5703 | 4.5703 | 4.5704 | 4.5705 | 4.5706 | 4.5707 | 4.5708 | 4.5708 | 4.5709 | 4.571 | 4.5711 |  | 0% | 0% | 16.85% | 80524 | [7 empty] | 4.62 | -0.05
|  |  |  | 1 x 8 |  | 10:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.77 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 208 | CRIEFF | 33/11 | 2 x 15 |  | 2019-02-05 | 9.27 | 1 | 0 | 0 | 9.27 | 9.2702 | 9.2703 | 9.2705 | 9.2707 | 9.2708 | 9.271 | 9.2712 | 9.2714 | 9.2715 | 9.2717 | 9.2719 | 9.272 | 9.2722 |  | 0% | 0% | 12.94% | 80509 | [7 empty] | 9.674 | -0.404
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 209 | DUNBLANE | 33/11 | 2 x 12.5 |  | 2019-02-01 | 8.93 | 1 | 0 | 0 | 8.93 | 8.9302 | 8.9303 | 8.9305 | 8.9307 | 8.9308 | 8.931 | 8.9311 | 8.9313 | 8.9315 | 8.9316 | 8.9318 | 8.932 | 8.9321 |  | 0% | 0% | 24.86% | 80514 | [7 empty] | 10.6592 | -1.7292
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.22 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 253 | FORTEVIOT | 33/11 | 1 x 6.25 |  | 2018-12-11 | 1.72 | 1 | 0 | 0 | 1.72 | 1.72 | 1.7201 | 1.7201 | 1.7201 | 1.7202 | 1.7202 | 1.7202 | 1.7203 | 1.7203 | 1.7203 | 1.7203 | 1.7204 | 1.7204 |  | 0% | 0% | 27.33% | 80503 | [7 empty] | 1.8857 | -0.16572
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.47 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 207 | GLENEAGLES | 33/11 | 2 x 15 |  | 2018-12-14 | 11.06 | 1 | 0 | 0 | 11.06 | 11.0602 | 11.0604 | 11.0606 | 11.0608 | 11.061 | 11.0612 | 11.0614 | 11.0616 | 11.0618 | 11.062 | 11.0622 | 11.0624 | 11.0626 |  | 0% | 0% | 34.81% | 80506 | [7 empty] | 11.4835 | -0.42346
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.85 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 211 | KIPPEN | 33/11 | 2 x 8 |  | 2019-02-01 | 4.53 | 1 | 0 | 0 | 4.53 | 4.5301 | 4.5302 | 4.5302 | 4.5303 | 4.5304 | 4.5305 | 4.5306 | 4.5307 | 4.5307 | 4.5308 | 4.5309 | 4.531 | 4.5311 |  | 0% | 0% | 11.26% | 80520 | [7 empty] | 4.71 | -0.18
[6 empty] | 7:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.51 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
BRIDGE OF DUN | 71 |  | 132/33 | 2 x 60 |  |  | 26.5 | 1 |  | Diverse | 26.5 | 26.5648 | 26.631 | 26.6985 | 26.7675 | 26.8379 | 26.9098 | 26.9832 | 27.0582 | 27.1347 | 27.2128 | 27.2926 | 27.3742 | 27.4574 | Diversity/Losses: 1.022 | 0% | 0% | 30.19% | 11130
[10 empty] | Aggregate | 27.0812 | 27.1475 | 27.2151 | 27.2841 | 27.3546 | 27.4265 | 27.5 | 27.575 | 27.6516 | 27.7298 | 27.8097 | 27.8913 | 27.9745 | 28.0596 |  |  |  | 8 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 26.288 | 26.3523 | 26.4179 | 26.485 | 26.5534 | 26.6232 | 26.6945 | 26.7673 | 26.8417 | 26.9176 | 26.9951 | 27.0743 | 27.1552 | 27.2377
| 73 | BRECHIN | 33/11 | 2 x 10 |  | 2018-12-05 | 7.14 | 1 | 0 | 0 | 7.14 | 7.1401 | 7.1403 | 7.1404 | 7.1405 | 7.1407 | 7.1408 | 7.1409 | 7.141 | 7.1412 | 7.1413 | 7.1414 | 7.1416 | 7.1417 |  | 0% | 0% | 12.61% | 80608 | [7 empty] | 7.33 | -0.19
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 72 | BRIDGE OF DUN 11kV | 33/11 | 1 x 2.5 |  | 2019-01-25 | 0.56 | 1 | 0 | 0 | 0.56 | 0.56001 | 0.56002 | 0.56003 | 0.56004 | 0.56005 | 0.56006 | 0.56007 | 0.56008 | 0.56009 | 0.5601 | 0.56011 | 0.56012 | 0.56013 |  | 0% | 0% | 7.143% | 80606 | [7 empty] | 0.61 | -0.05
[6 empty] | 19:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.04 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 5 | GLAXO (33kV Customer) | 33 |  |  | 2018-06-27 | 2.6817 | 1 | ? | 0 | 2.6817 | 2.6817 | 2.6818 | 2.6818 | 2.6819 | 2.6819 | 2.682 | 2.682 | 2.6821 | 2.6821 | 2.6822 | 2.6822 | 2.6823 | 2.6823 |  | 0% | 0% | 0.3377% | 80617 | [7 empty] | 0 | 2.6817
[6 empty] | 6:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.0090565 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 76 | INCHBARE | 33/11 | 1 x 2.5 |  | 2019-01-03 | 1.18 | 1 | 0 | 0 | 1.18 | 1.18 | 1.18 | 1.1801 | 1.1801 | 1.1801 | 1.1801 | 1.1802 | 1.1802 | 1.1802 | 1.1802 | 1.1802 | 1.1803 | 1.1803 |  | 0% | 0% | 22.88% | 80605 | [7 empty] | 1.1293 | 0.050688
[6 empty] | 9:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.27 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 77 | LOGIE PERT | 33/11 | 1 x 5 |  | 2019-02-07 | 1.37 | 1 | H | H | 1.37 | 1.4067 | 1.4444 | 1.4831 | 1.5228 | 1.5636 | 1.6055 | 1.6485 | 1.6926 | 1.738 | 1.7845 | 1.8323 | 1.8814 | 1.9318 |  | 0% | 0% | 0.7299% | 80604 | [7 empty] | 1.1689 | 0.20107
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.01 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 75 | MILL RD MONTROSE | 33/11 | 2 x 10 |  | 2018-04-04 | 6.6595 | 1 | 0 | 0 | 6.6595 | 6.6596 | 6.6598 | 6.6599 | 6.66 | 6.6601 | 6.6602 | 6.6604 | 6.6605 | 6.6606 | 6.6607 | 6.6608 | 6.661 | 6.6611 |  | 0% | 0% | 29.84% | 80613 | [7 empty] | 7.6311 | -0.97162
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.9871 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 74 | MONTROSE NORTH | 33/11 | 2 x 15 |  | 2018-12-05 | 8.0317 | 1 | 0 | 0 | 8.0317 | 8.0319 | 8.032 | 8.0321 | 8.0323 | 8.0324 | 8.0326 | 8.0327 | 8.0329 | 8.033 | 8.0332 | 8.0333 | 8.0335 | 8.0336 |  | 0% | 0% | 27.83% | 80623 | [7 empty] | 7.7608 | 0.27091
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.2355 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 952 | ST CYRUS | 33/11 | 1 x 6 & 1 x 8 |  | 2019-01-31 | 2.14 | 1 | M | M | 2.14 | 2.1691 | 2.1986 | 2.2285 | 2.2589 | 2.2896 | 2.3207 | 2.3523 | 2.3843 | 2.4168 | 2.4496 | 2.483 | 2.5167 | 2.551 |  | 0% | 0% | 0% | 80629 | [7 empty] | 2.1226 | 0.017421
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
BROADFORD | 627 |  | 132/33 | 1 x 30 |  |  | 12.2 | 1 |  | Diverse | 12.2 | 12.2247 | 12.25 | 12.276 | 12.3027 | 12.33 | 12.3581 | 12.3869 | 12.4164 | 12.4467 | 12.4778 | 12.5098 | 12.5425 | 12.5761 | Diversity/Losses: 1.062 | 0% | 0% | 28.69% | 11230
[10 empty] | Aggregate | 12.9582 | 12.9844 | 13.0113 | 13.0389 | 13.0672 | 13.0962 | 13.1261 | 13.1566 | 13.188 | 13.2202 | 13.2533 | 13.2872 | 13.322 | 13.3577 |  |  |  | 3.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 12.1024 | 12.1269 | 12.152 | 12.1778 | 12.2042 | 12.2314 | 12.2592 | 12.2878 | 12.3171 | 12.3472 | 12.378 | 12.4097 | 12.4422 | 12.4755
| 624 | ACHINTEE | 33/11 | 1 x 1 |  |  | 0.084282 | 1 | M | M | 0.084282 | 0.085429 | 0.086591 | 0.087769 | 0.088963 | 0.090174 | 0.0914 | 0.092644 | 0.093904 | 0.095182 | 0.096477 | 0.097789 | 0.09912 | 0.10047 |  | 0% | 0% | 0% | 80716 | [7 empty] | 0.08 | 0.0042822
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 637 | BROADFORD | 33/11 | 1 x 5 |  | 2018-04-03 | 1.59 | 1 | 0 | 0 | 1.59 | 1.59 | 1.5901 | 1.5901 | 1.5901 | 1.5901 | 1.5902 | 1.5902 | 1.5902 | 1.5903 | 1.5903 | 1.5903 | 1.5903 | 1.5904 |  | 0% | 0% | 22.01% | 80701 | [7 empty] | 1.69 | -0.1
[6 empty] | 20:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.35 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 629 | DRYNOCH | 33/11 | 1 x 2.5 |  | 2018-04-01 | 1.24 | 1 | 0 | 0 | 1.24 | 1.24 | 1.24 | 1.2401 | 1.2401 | 1.2401 | 1.2401 | 1.2402 | 1.2402 | 1.2402 | 1.2402 | 1.2402 | 1.2403 | 1.2403 |  | 0% | 0% | 9.677% | 80741 | [7 empty] | 1.3375 | -0.097516
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.12 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 633 | KISHORNHILL | 33/11 | 1 x 2 |  | 2018-04-04 | 1.28 | 1 | 0 | 0 | 1.28 | 1.28 | 1.28 | 1.2801 | 1.2801 | 1.2801 | 1.2801 | 1.2802 | 1.2802 | 1.2802 | 1.2802 | 1.2803 | 1.2803 | 1.2803 |  | 0% | 0% | 12.5% | 80709 | [7 empty] | 1.38 | -0.1
[6 empty] | 6:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.16 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 634 | KYLE | 33/11 | 2 x 5 |  | 2019-01-31 | 2.36 | 1 | 0 | 0 | 2.36 | 2.36 | 2.3601 | 2.3601 | 2.3602 | 2.3602 | 2.3603 | 2.3603 | 2.3603 | 2.3604 | 2.3604 | 2.3605 | 2.3605 | 2.3606 |  | 0% | 0% | 32.2% | 80724 | 80725 | [6 empty] | 2.54 | -0.18
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.76 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 623 | LOWER OLLACH | 33/11 | 1 x 1 |  | 2018-04-03 | 0.92779 | 1 | H | H | 0.92779 | 0.95265 | 0.97817 | 1.0044 | 1.0313 | 1.0589 | 1.0873 | 1.1164 | 1.1463 | 1.177 | 1.2085 | 1.2409 | 1.2741 | 1.3083 |  | 0% | 0% | 30.11% | 80740 | [7 empty] | 0.59761 | 0.33019
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.27934 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 636 | NOSTIE BRIDGE | 33/11 | 1 x 4 |  | 2018-04-02 | 2.1461 | 1 | 0 | 0 | 2.1461 | 2.1461 | 2.1462 | 2.1462 | 2.1462 | 2.1463 | 2.1463 | 2.1464 | 2.1464 | 2.1464 | 2.1465 | 2.1465 | 2.1466 | 2.1466 |  | 0% | 0% | 1.081e-05% | 80719 | [7 empty] | 2.4089 | -0.26278
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.3198e-07 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 641 | SHIELDAIG | 33/11 | 1 x 1 |  | 2018-07-29 | 0.73 | 1 | 0 | 0 | 0.73 | 0.73001 | 0.73003 | 0.73004 | 0.73005 | 0.73007 | 0.73008 | 0.73009 | 0.73011 | 0.73012 | 0.73013 | 0.73015 | 0.73016 | 0.73017 |  | 0% | 0% | 6.849% | 80713 | [7 empty] | 0.72032 | 0.0096787
|  | Requires Settlements Data |  |  |  | 5:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 639 | SKULAMUS | 33/11 | 1 x 4 |  | 2018-04-03 | 2.6 | 1 | 0 | 0 | 2.6 | 2.6 | 2.6001 | 2.6001 | 2.6002 | 2.6002 | 2.6003 | 2.6003 | 2.6004 | 2.6004 | 2.6005 | 2.6005 | 2.6006 | 2.6006 |  | 0% | 0% | 21.15% | 80733 | [7 empty] | 2.7185 | -0.11852
[6 empty] | 20:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.55 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
BRORA | 510 |  | 132/33 | 1 x 45 |  |  | 8.8 | 1 |  | Diverse | 8.8 | 8.8002 | 8.8003 | 8.8005 | 8.8006 | 8.8008 | 8.801 | 8.8011 | 8.8013 | 8.8014 | 8.8016 | 8.8018 | 8.8019 | 8.8021 | Diversity/Losses: 1.031 | 0% | 0% | 32.95% | 11330
[10 empty] | Aggregate | 9.07 | 9.0702 | 9.0703 | 9.0705 | 9.0707 | 9.0708 | 9.071 | 9.0712 | 9.0713 | 9.0715 | 9.0717 | 9.0718 | 9.072 | 9.0722 |  |  |  | 2.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 8.7296 | 8.7298 | 8.7299 | 8.7301 | 8.7302 | 8.7304 | 8.7306 | 8.7307 | 8.7309 | 8.731 | 8.7312 | 8.7314 | 8.7315 | 8.7317
| 550 | BRORA | 33/11 | 2 x 5 |  | 2019-02-02 | 2.24 | 1 | 0 | 0 | 2.24 | 2.24 | 2.2401 | 2.2401 | 2.2402 | 2.2402 | 2.2402 | 2.2403 | 2.2403 | 2.2404 | 2.2404 | 2.2404 | 2.2405 | 2.2405 |  | 0% | 0% | 17.86% | 80805 | [7 empty] | 3.34 | -1.1
[6 empty] | 3:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 557 | DORNOCH | 33/11 | 1 x 8 |  | 2019-02-01 | 3.77 | 1 | 0 | 0 | 3.77 | 3.7701 | 3.7701 | 3.7702 | 3.7703 | 3.7703 | 3.7704 | 3.7705 | 3.7706 | 3.7706 | 3.7707 | 3.7708 | 3.7708 | 3.7709 |  | 0% | 0% | 22.81% | 80813 | [7 empty] | 4.0642 | -0.29423
[6 empty] | 7:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.86 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 525 | GOLSPIE | 33/11 | 1 x 4 |  | 2019-01-30 | 2.04 | 1 | 0 | 0 | 2.04 | 2.04 | 2.0401 | 2.0401 | 2.0401 | 2.0402 | 2.0402 | 2.0403 | 2.0403 | 2.0403 | 2.0404 | 2.0404 | 2.0404 | 2.0405 |  | 0% | 0% | 24.02% | 80810 | [7 empty] | 2.1877 | -0.14768
[6 empty] | 20:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.49 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 560 | HELMSDALE | 33/11 | 1 x 4 |  | 2019-01-16 | 1.02 | 1 | 0 | 0 | 1.02 | 1.02 | 1.02 | 1.0201 | 1.0201 | 1.0201 | 1.0201 | 1.0201 | 1.0201 | 1.0202 | 1.0202 | 1.0202 | 1.0202 | 1.0202 |  | 0% | 0% | 18.63% | 80802 | [7 empty] | 1.4909 | -0.47091
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.19 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
BURGHMUIR | 245 |  | 132/33 | 2 x 90 |  |  | 45 | 1 |  | Diverse | 45 | 45.0384 | 45.077 | 45.1158 | 45.1549 | 45.1941 | 45.2336 | 45.2732 | 45.3131 | 45.3532 | 45.3936 | 45.4341 | 45.4749 | 45.5159 | Diversity/Losses: 1.017 | 0% | 0% | 29.56% | 11430
[10 empty] | Aggregate | 45.7608 | 45.7998 | 45.8391 | 45.8786 | 45.9183 | 45.9582 | 45.9983 | 46.0386 | 46.0792 | 46.12 | 46.161 | 46.2022 | 46.2437 | 46.2854 |  |  |  | 13.3 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 44.64 | 44.6781 | 44.7164 | 44.7549 | 44.7936 | 44.8326 | 44.8717 | 44.9111 | 44.9506 | 44.9904 | 45.0304 | 45.0706 | 45.1111 | 45.1517
| 246 | BURGHMUIR | 33/11 | 2 x 12.5 |  | 2019-01-23 | 8.92 | 1 | 0 | 0 | 8.92 | 8.9202 | 8.9203 | 8.9205 | 8.9207 | 8.9208 | 8.921 | 8.9211 | 8.9213 | 8.9215 | 8.9216 | 8.9218 | 8.922 | 8.9221 |  | 0% | 0% | 13.9% | 80917 | [7 empty] | 9.53 | -0.61
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.24 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 249 | GOODLYBURN | 33/11 | 2 x 12.5 |  | 2019-01-24 | 8.89 | 1 | 0 | 0 | 8.89 | 8.8902 | 8.8903 | 8.8905 | 8.8906 | 8.8908 | 8.891 | 8.8911 | 8.8913 | 8.8915 | 8.8916 | 8.8918 | 8.8919 | 8.8921 |  | 0% | 0% | 26.66% | 80911 | [7 empty] | 9.6474 | -0.75736
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.37 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 272 | NORTH MUIRTON | 33/11 | 1 x 10 |  | 2019-02-05 | 6.9188 | 1 | L | L | 6.9188 | 6.9572 | 6.9957 | 7.0345 | 7.0735 | 7.1127 | 7.1521 | 7.1917 | 7.2316 | 7.2717 | 7.312 | 7.3525 | 7.3932 | 7.4342 |  | 0% | 0% | 30.35% | 80908 | [7 empty] | 7.3212 | -0.40239
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 270 | REDGORTON | 33/11 | 2 x 15 |  | 2019-02-01 | 4.6119 | 1 | 0 | 0 | 4.6119 | 4.612 | 4.6121 | 4.6122 | 4.6123 | 4.6124 | 4.6124 | 4.6125 | 4.6126 | 4.6127 | 4.6128 | 4.6129 | 4.6129 | 4.613 |  | 0% | 0% | 17.65% | 80904 | [7 empty] | 4.37 | 0.24193
[6 empty] | 7:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.81385 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 248 | THIMBLEROW | 33/11 | 2 x 21 |  | 2019-02-01 | 16.42 | 1 | 0 | 0 | 16.42 | 16.4203 | 16.4206 | 16.4209 | 16.4212 | 16.4215 | 16.4218 | 16.4221 | 16.4224 | 16.4227 | 16.423 | 16.4233 | 16.4236 | 16.4239 |  | 0% | 0% | 26.67% | 80915 | [7 empty] | 20.1261 | -3.7061
[6 empty] | 12:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4.38 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
CARRADALE | 302 |  | 132/33 | 2 x 60 |  |  | 23.7 | 1 |  | Diverse | 23.7 | 23.8785 | 24.0594 | 24.2428 | 24.4286 | 24.617 | 24.808 | 25.0015 | 25.1977 | 25.3965 | 25.5981 | 25.8023 | 26.0094 | 26.2193 | Diversity/Losses: 0.958 | 0% | 0% | 21.52% | 11530
|  |  |  | 2 x 90 | [5 empty] | Aggregate | 22.7047 | 22.8757 | 23.049 | 23.2246 | 23.4027 | 23.5832 | 23.7661 | 23.9515 | 24.1395 | 24.3299 | 24.523 | 24.7187 | 24.9171 | 25.1181 |  |  |  | 5.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 23.5104 | 23.6875 | 23.8669 | 24.0488 | 24.2332 | 24.4201 | 24.6095 | 24.8015 | 24.9961 | 25.1934 | 25.3933 | 25.5959 | 25.8013 | 26.0095
| 372 | BALLIEKINE | 33/11 | 1 x 1 |  | 2018-04-03 | 0.64 | 1 | 0 | 0 | 0.64 | 0.64001 | 0.64002 | 0.64004 | 0.64005 | 0.64006 | 0.64007 | 0.64008 | 0.64009 | 0.64011 | 0.64012 | 0.64013 | 0.64014 | 0.64015 |  | 0% | 0% | 0% | 81119 | [7 empty] | 0.76294 | -0.12294
[6 empty] | 8:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 318 | BALLURE | 33/11 | 1 x 2.5 |  | 2018-04-03 | 1.18 | 1 | 0 | 0 | 1.18 | 1.18 | 1.18 | 1.1801 | 1.1801 | 1.1801 | 1.1801 | 1.1802 | 1.1802 | 1.1802 | 1.1802 | 1.1802 | 1.1803 | 1.1803 |  | 0% | 0% | 0% | 81137 | [7 empty] | 1.2354 | -0.055448
[6 empty] | 21:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 370 | BRODICK | 33/11 | 2 x 4/8 |  | 2018-04-03 | 5.65 | 1 | 0 | 0 | 5.65 | 5.6501 | 5.6502 | 5.6503 | 5.6504 | 5.6505 | 5.6506 | 5.6507 | 5.6508 | 5.6509 | 5.651 | 5.6511 | 5.6512 | 5.6513 |  | 0% | 0% | 12.92% | 81106 | [7 empty] | 5.99 | -0.34
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.73 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 312 | CAMPBELTOWN | 33/11 | 2 x 15 |  | 2019-01-31 | 8.82 | 1 | M | M | 8.82 | 8.94 | 9.0616 | 9.1849 | 9.3099 | 9.4365 | 9.5649 | 9.695 | 9.8269 | 9.9606 | 10.0961 | 10.2335 | 10.3727 | 10.5138 |  | 0% | 0% | 0% | 81127 | [7 empty] | 7.55 | 1.27
[6 empty] | 0:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 338 | CLAONAIG | 33/11 | 1 x 0.3 |  |  | 0.20509 | 1 | M | M | 0.20509 | 0.20788 | 0.21071 | 0.21357 | 0.21648 | 0.21942 | 0.22241 | 0.22543 | 0.2285 | 0.23161 | 0.23476 | 0.23795 | 0.24119 | 0.24447 |  | 0% | 0% | 0% | 81134 | [7 empty] | 0.22 | -0.014913
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 336 | DIPPEN | 33/11 | 1 x 1 |  |  | 0.94958 | 1 | M | M | 0.94958 | 0.9625 | 0.97559 | 0.98887 | 1.0023 | 1.016 | 1.0298 | 1.0438 | 1.058 | 1.0724 | 1.087 | 1.1018 | 1.1167 | 1.1319 |  | 0% | 0% | 0% | 81123 | [7 empty] | 1.01 | -0.06042
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 373 | MACHRIE | 33/11 | 1 x 2.5 |  | 2018-04-02 | 1.95 | 1 | 0 | 0 | 1.95 | 1.95 | 1.9501 | 1.9501 | 1.9501 | 1.9502 | 1.9502 | 1.9502 | 1.9503 | 1.9503 | 1.9504 | 1.9504 | 1.9504 | 1.9505 |  | 0% | 0% | 9.999% | 81114 | [7 empty] | 2.0365 | -0.086485
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.19498 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 310 | TARBERT LOCH FYNE | 33/11 | 1 x 2.5 |  | 2018-04-03 | 2.53 | 1 | 0 | 0 | 2.53 | 2.53 | 2.5301 | 2.5301 | 2.5302 | 2.5302 | 2.5303 | 2.5303 | 2.5304 | 2.5304 | 2.5305 | 2.5305 | 2.5306 | 2.5306 |  | 0% | 0% | 3.557% | 81140 | 84900 | [6 empty] | 3.1065 | -0.57651
|  | (1 tfr on Carradale, 1 tfr on Port Ann) |  |  |  | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.09 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 349 | WESTPARK FERGUS | 33/11 | 1 x 8 |  | 2019-01-23 | 0.73 | 1 | 0 | 0 | 0.73 | 0.73001 | 0.73003 | 0.73004 | 0.73005 | 0.73007 | 0.73008 | 0.73009 | 0.73011 | 0.73012 | 0.73013 | 0.73015 | 0.73016 | 0.73017 |  | 0% | 0% | 4.11% | 81131 | [7 empty] | 0.65293 | 0.07707
[6 empty] | 13:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.03 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 371 | WHITING BAY | 33/11 | 1 x 8 |  | 2018-04-02 | 2.58 | 1 | M | M | 2.58 | 2.6151 | 2.6507 | 2.6867 | 2.7233 | 2.7603 | 2.7979 | 2.836 | 2.8745 | 2.9137 | 2.9533 | 2.9935 | 3.0342 | 3.0755 |  | 0% | 0% | 12.02% | 81111 | [7 empty] | 2.441 | 0.13902
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.31 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
CASSLEY | 512 |  | 132/33 | 1 x 30 |  |  | 1.9 | 1 |  | Diverse | 1.9 | 1.9 | 1.9001 | 1.9001 | 1.9001 | 1.9002 | 1.9002 | 1.9002 | 1.9003 | 1.9003 | 1.9003 | 1.9004 | 1.9004 | 1.9005 | Diversity/Losses: 1.041 | 0% | 0% | 21.05% | 11830
[10 empty] | Aggregate | 1.9775 | 1.9775 | 1.9776 | 1.9776 | 1.9776 | 1.9777 | 1.9777 | 1.9777 | 1.9778 | 1.9778 | 1.9778 | 1.9779 | 1.9779 | 1.9779 |  |  |  | 0.4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 1.8848 | 1.8848 | 1.8849 | 1.8849 | 1.8849 | 1.885 | 1.885 | 1.885 | 1.8851 | 1.8851 | 1.8851 | 1.8852 | 1.8852 | 1.8852
| 563 | OVERSCAIG | 33/11 | 1 x 0.15 |  |  | 0.030903 | 1 | 0 | 0 | 0.030903 | 0.030904 | 0.030905 | 0.030905 | 0.030906 | 0.030906 | 0.030907 | 0.030907 | 0.030908 | 0.030909 | 0.030909 | 0.03091 | 0.03091 | 0.030911 |  | 0% | 0% | 0% | 81202 | [7 empty] | 0.04 | -0.0090965
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 544 | RHICONICH | 33/11 | 1 x 3.9 |  | 25/02/219 | 1.9466 | 1 | 0 | 0 | 1.9466 | 1.9466 | 1.9466 | 1.9467 | 1.9467 | 1.9468 | 1.9468 | 1.9468 | 1.9469 | 1.9469 | 1.9469 | 1.947 | 1.947 | 1.947 |  | 0% | 0% | 23.7% | 81218 | [7 empty] | 1.75 | 0.19657
[6 empty] | 4:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.46134 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
CHARLESTON | 1 |  | 132/33 | 2 x 90 |  |  | 23.8 | 1 |  | Diverse | 23.8 | 24.0105 | 24.2266 | 24.4486 | 24.6764 | 24.9104 | 25.1506 | 25.3972 | 25.6504 | 25.9105 | 26.1774 | 26.4515 | 26.733 | 27.022 | Diversity/Losses: 1.202 | 0% | 0% | 30.67% | 12030
[10 empty] | Aggregate | 28.5996 | 28.8525 | 29.1122 | 29.3789 | 29.6527 | 29.9338 | 30.2225 | 30.5189 | 30.8232 | 31.1356 | 31.4564 | 31.7858 | 32.124 | 32.4713 |  |  |  | 7.3 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 23.6096 | 23.8184 | 24.0328 | 24.253 | 24.479 | 24.7111 | 24.9494 | 25.194 | 25.4452 | 25.7032 | 25.968 | 26.2399 | 26.5191 | 26.8058
| 2 | CHARLESTON | 33/11 | 2 x 15 |  | 2018-08-15 | 9.43 | 1 | H | H | 9.43 | 9.6826 | 9.942 | 10.2083 | 10.4818 | 10.7625 | 11.0508 | 11.3469 | 11.6508 | 11.9629 | 12.2834 | 12.6124 | 12.9502 | 13.2972 |  | 0% | 0% | 19.83% | 81405 | [7 empty] | 8.86 | 0.57
[6 empty] | 14:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.87 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 4 | GOURDIE | 33/11 | 1 x 6.3 |  | 2018-12-25 | 2.57 | 1 | 0 | 0 | 2.57 | 2.57 | 2.5701 | 2.5701 | 2.5702 | 2.5702 | 2.5703 | 2.5703 | 2.5704 | 2.5704 | 2.5705 | 2.5705 | 2.5706 | 2.5706 |  | 0% | 0% | 22.18% | 81401 | [7 empty] | 2.6439 | -0.073896
[6 empty] | 16:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.57 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 3 | MENZIESHILL | 33/11 | 2 x 21 |  | 2019-01-21 | 11.39 | 1 | 0 | 0 | 11.39 | 11.3902 | 11.3904 | 11.3906 | 11.3908 | 11.391 | 11.3912 | 11.3915 | 11.3917 | 11.3919 | 11.3921 | 11.3923 | 11.3925 | 11.3927 |  | 0% | 0% | 15.63% | 81410 | [7 empty] | 11.6179 | -0.22789
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.78 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 6 | NINEWELLS | 33/11 | 2 x 15 |  | 2019-01-28 | 5.2096 | 1 | 0 | 0 | 5.2096 | 5.2097 | 5.2098 | 5.2098 | 5.2099 | 5.21 | 5.2101 | 5.2102 | 5.2103 | 5.2104 | 5.2105 | 5.2106 | 5.2107 | 5.2108 |  | 0% | 0% | 37.89% | 81420 | [7 empty] | 5.3525 | -0.14289
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.9738 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
CLACHAN | 311 |  | 132/11 | 1 x 60 |  |  | 5.9 | 1 |  | Diverse | 5.9 | 5.9001 | 5.9002 | 5.9003 | 5.9004 | 5.9005 | 5.9006 | 5.9008 | 5.9009 | 5.901 | 5.9011 | 5.9012 | 5.9013 | 5.9014 | Diversity/Losses: 0.556 | 0% | 0% | 0% | 12151
[10 empty] | Aggregate | 3.2784 | 3.2785 | 3.2785 | 3.2786 | 3.2787 | 3.2787 | 3.2788 | 3.2788 | 3.2789 | 3.279 | 3.279 | 3.2791 | 3.2791 | 3.2792 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 5.8528 | 5.8529 | 5.853 | 5.8531 | 5.8532 | 5.8533 | 5.8534 | 5.8535 | 5.8537 | 5.8538 | 5.8539 | 5.854 | 5.8541 | 5.8542
| 387 | BUTTERBRIDGE | 33/11 | 1 x 0.1 |  |  | 0.0084282 | 1 | 0 | 0 | 0.0084282 | 0.0084284 | 0.0084285 | 0.0084287 | 0.0084288 | 0.008429 | 0.0084291 | 0.0084293 | 0.0084295 | 0.0084296 | 0.0084298 | 0.0084299 | 0.0084301 | 0.0084302 |  | 0% | 0% | 0% | 81509 | [7 empty] | 0.015 | -0.0065718
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 388 | DOUGLAS PIER | 33/11 | 1 x 2.5 |  | 2019-01-02 | 1.13 | 1 | 0 | 0 | 1.13 | 1.13 | 1.13 | 1.1301 | 1.1301 | 1.1301 | 1.1301 | 1.1301 | 1.1302 | 1.1302 | 1.1302 | 1.1302 | 1.1302 | 1.1303 |  | 0% | 0% | 0.885% | 81515 | [7 empty] | 1.4666 | -0.33656
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.01 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 321 | INVERARAY | 33/11 | 1 x 2.5 |  | 2018-04-04 | 0.89 | 1 | 0 | 0 | 0.89 | 0.89002 | 0.89003 | 0.89005 | 0.89006 | 0.89008 | 0.8901 | 0.89011 | 0.89013 | 0.89015 | 0.89016 | 0.89018 | 0.8902 | 0.89021 |  | 0% | 0% | 22.47% | 81521 | [7 empty] | 0.94139 | -0.051391
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 369 | LOCHGOILHEAD | 33/11 | 1 x 2.5 |  | 2018-06-15 | 0.41 | 1 | 0 | 0 | 0.41 | 0.41001 | 0.41001 | 0.41002 | 0.41003 | 0.41004 | 0.41004 | 0.41005 | 0.41006 | 0.41007 | 0.41007 | 0.41008 | 0.41009 | 0.4101 |  | 0% | 0% | 0% | 81513 | [7 empty] | 0.4 | 0.01
[6 empty] | 5:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 382 | STRACHUR | 33/11 | 1 x 1 |  | 2019-02-02 | 0.84 | 1 | 0 | 0 | 0.84 | 0.84002 | 0.84003 | 0.84005 | 0.84006 | 0.84008 | 0.84009 | 0.84011 | 0.84012 | 0.84014 | 0.84015 | 0.84017 | 0.84018 | 0.8402 |  | 0% | 0% | 1.19% | 81518 | [7 empty] | 0.88168 | -0.041677
[6 empty] | 4:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.01 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
CLAYHILLS | 823 |  | 132/33 | 2 x 60 |  |  | 32.7 | 1 |  | Diverse | 32.7 | 32.7006 | 32.7012 | 32.7018 | 32.7024 | 32.703 | 32.7036 | 32.7042 | 32.7048 | 32.7054 | 32.706 | 32.7066 | 32.7072 | 32.7078 | Diversity/Losses: 1.032 | 0% | 0% | 28.13% | 12230
[10 empty] | Aggregate | 33.74 | 33.7406 | 33.7412 | 33.7418 | 33.7425 | 33.7431 | 33.7437 | 33.7443 | 33.7449 | 33.7455 | 33.7462 | 33.7468 | 33.7474 | 33.748 |  |  |  | 9.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 32.4384 | 32.439 | 32.4396 | 32.4402 | 32.4408 | 32.4414 | 32.442 | 32.4425 | 32.4431 | 32.4437 | 32.4443 | 32.4449 | 32.4455 | 32.4461
| 808 | BALNAGASK | 33/11 | 1 x 23 |  | 2018-11-29 | 4.48 | 1 | 0 | 0 | 4.48 | 4.4801 | 4.4802 | 4.4802 | 4.4803 | 4.4804 | 4.4805 | 4.4806 | 4.4807 | 4.4807 | 4.4808 | 4.4809 | 4.481 | 4.4811 |  | 0% | 0% | 20.31% | 81607 | [7 empty] | 4.8235 | -0.3435
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.91 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 826 | CLAYHILLS | 33/11 | 2 x 24 |  | 2019-01-31 | 14.79 | 1 | 0 | 0 | 14.79 | 14.7903 | 14.7905 | 14.7908 | 14.7911 | 14.7914 | 14.7916 | 14.7919 | 14.7922 | 14.7924 | 14.7927 | 14.793 | 14.7932 | 14.7935 |  | 0% | 0% | 23.6% | 81604 | [7 empty] | 16.3 | -1.51
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.49 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 827 | COMMERCE STREET | 33/11 | 2 x 23 |  | 2019-01-21 | 14.47 | 1 | 0 | 0 | 14.47 | 14.4703 | 14.4705 | 14.4708 | 14.4711 | 14.4713 | 14.4716 | 14.4718 | 14.4721 | 14.4724 | 14.4726 | 14.4729 | 14.4732 | 14.4734 |  | 0% | 0% | 27.64% | 81602 | [7 empty] | 15.4 | -0.93
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
COUPAR ANGUS | 243 |  | 132/33 | 2 x 120 |  |  | 25 | 1 |  | Diverse | 25 | 25.0005 | 25.0009 | 25.0014 | 25.0018 | 25.0023 | 25.0027 | 25.0032 | 25.0037 | 25.0041 | 25.0046 | 25.005 | 25.0055 | 25.0059 | Diversity/Losses: 1.178 | 0% | 0% | 25.6% | 12430
[10 empty] | Aggregate | 29.4617 | 29.4622 | 29.4627 | 29.4633 | 29.4638 | 29.4643 | 29.4649 | 29.4654 | 29.466 | 29.4665 | 29.467 | 29.4676 | 29.4681 | 29.4686 |  |  |  | 6.4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 24.8 | 24.8005 | 24.8009 | 24.8014 | 24.8018 | 24.8023 | 24.8027 | 24.8032 | 24.8036 | 24.8041 | 24.8045 | 24.805 | 24.8054 | 24.8059
| 258 | ALYTH | 33/11 | 2 x 5 |  | 2018-12-24 | 2.81 | 1 | 0 | 0 | 2.81 | 2.8101 | 2.8101 | 2.8102 | 2.8102 | 2.8103 | 2.8103 | 2.8104 | 2.8104 | 2.8105 | 2.8105 | 2.8106 | 2.8106 | 2.8107 |  | 0% | 0% | 24.91% | 81712 | [7 empty] | 2.77 | 0.04
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.7 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 257 | BLAIRGOWRIE | 33/11 | 2 x 23 |  | 2018-12-04 | 8.71 | 1 | 0 | 0 | 8.71 | 8.7102 | 8.7103 | 8.7105 | 8.7106 | 8.7108 | 8.711 | 8.7111 | 8.7113 | 8.7114 | 8.7116 | 8.7117 | 8.7119 | 8.7121 |  | 0% | 0% | 21.7% | 81708 | [7 empty] | 8.7914 | -0.081404
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.89 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 281 | BP BALBEGGIE | 33/11 |  |  | 2018-06-28 | 1.7217 | 1 | 0 | 0 | 1.7217 | 1.7217 | 1.7217 | 1.7217 | 1.7218 | 1.7218 | 1.7218 | 1.7219 | 1.7219 | 1.7219 | 1.722 | 1.722 | 1.722 | 1.7221 |  | 0% | 0% | 0% | 81723
|  | Poor Data |  |  |  | 7:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 256 | CAPUTH | 33/11 | 2 x 15 |  | 2019-01-17 | 5.46 | 1 | 0 | 0 | 5.46 | 5.4601 | 5.4602 | 5.4603 | 5.4604 | 5.4605 | 5.4606 | 5.4607 | 5.4608 | 5.4609 | 5.461 | 5.4611 | 5.4612 | 5.4613 |  | 0% | 0% | 17.22% | 81720 | [7 empty] | 5.59 | -0.13
[6 empty] | 15:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.94 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 244 | COUPAR ANGUS | 33/11 | 1 x 8 & 1 x 15 |  | 2018-12-01 | 6.1 | 1 | 0 | 0 | 6.1 | 6.1001 | 6.1002 | 6.1003 | 6.1004 | 6.1006 | 6.1007 | 6.1008 | 6.1009 | 6.101 | 6.1011 | 6.1012 | 6.1013 | 6.1014 |  | 0% | 0% | 29.84% | 81726 | [7 empty] | 6.96 | -0.86
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.82 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 259 | DALRULZION | 33/11 | 2 x 2.5 |  | 2019-01-01 | 1.96 | 1 | 0 | 0 | 1.96 | 1.96 | 1.9601 | 1.9601 | 1.9601 | 1.9602 | 1.9602 | 1.9603 | 1.9603 | 1.9603 | 1.9604 | 1.9604 | 1.9604 | 1.9605 |  | 0% | 0% | 17.35% | 81716 | [7 empty] | 1.965 | -0.005
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.34 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 90 | LEOCH | 33/11 | 1 x 6.3 |  | 2019-01-19 | 2.7 | 1 | 0 | 0 | 2.7 | 2.7 | 2.7001 | 2.7001 | 2.7002 | 2.7002 | 2.7003 | 2.7003 | 2.7004 | 2.7004 | 2.7005 | 2.7005 | 2.7006 | 2.7006 |  | 0% | 0% | 0% | 81705 | [7 empty] | 2.88 | -0.18
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
CRAIGIEBUCKLER | 829 |  | 132/33 | 2 x 30 |  |  | 23.4 | 1 |  | Diverse | 23.4 | 23.5383 | 23.6802 | 23.8259 | 23.9756 | 24.1292 | 24.287 | 24.4489 | 24.6152 | 24.786 | 24.9613 | 25.1413 | 25.3261 | 25.5158 | Diversity/Losses: 1.163 | 0% | 0% | 28.63% | 12530
[10 empty] | Aggregate | 27.2254 | 27.3862 | 27.5514 | 27.7209 | 27.895 | 28.0738 | 28.2573 | 28.4458 | 28.6393 | 28.8379 | 29.0419 | 29.2513 | 29.4663 | 29.687 |  |  |  | 6.7 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 23.2128 | 23.3499 | 23.4908 | 23.6353 | 23.7838 | 23.9362 | 24.0927 | 24.2533 | 24.4183 | 24.5877 | 24.7616 | 24.9401 | 25.1234 | 25.3117
| 830 | CRAIGIEBUCKLER | 33/11 | 2 x 24 |  | 2018-12-05 | 5.9905 | 1 | H | H | 5.9905 | 6.151 | 6.3157 | 6.4849 | 6.6586 | 6.837 | 7.0201 | 7.2082 | 7.4013 | 7.5995 | 7.8031 | 8.0121 | 8.2267 | 8.4471 |  | 0% | 0% | 33.27% | 81800 | [7 empty] | 3.58 | 2.4105
|  | No PI - Calculated from 33kV |  |  |  | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.9928 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 834 | CRAIGTON | 33/11 | 2 x10 |  | 2018-12-05 | 5.7065 | 1 | 0 | 0 | 5.7065 | 5.7066 | 5.7068 | 5.7069 | 5.707 | 5.7071 | 5.7072 | 5.7073 | 5.7074 | 5.7075 | 5.7076 | 5.7077 | 5.7078 | 5.7079 |  | 0% | 0% | 30.03% | 81813 | [7 empty] | 9.3 | -3.5935
|  | No PI - Calculated from 33kV |  |  |  | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.7136 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 836 | CULTER | 33/11 | 2 x 24 |  | 2019-02-03 | 5.57 | 1 | 0 | 0 | 5.57 | 5.5701 | 5.5702 | 5.5703 | 5.5704 | 5.5705 | 5.5706 | 5.5707 | 5.5708 | 5.5709 | 5.571 | 5.5711 | 5.5712 | 5.5713 |  | 0% | 0% | 14.36% | 81817 | 83814 | [6 empty] | 5.887 | -0.317
|  | (1 x Craigiebuckler, 1 x Kintore) |  |  |  | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.8 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 939 | RUTHRIESTON | 33/11 | 2 x 23 |  | 2018-11-21 | 9.9583 | 1 | 0 | 0 | 9.9583 | 9.9585 | 9.9587 | 9.9589 | 9.9591 | 9.9592 | 9.9594 | 9.9596 | 9.9598 | 9.96 | 9.9602 | 9.9603 | 9.9605 | 9.9607 |  | 0% | 0% | 29.49% | 81821 | [7 empty] | 11.15 | -1.1917
|  | No PI - Calculated from 33kV |  |  |  | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.9372 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
DOUNREAY | 598 |  | 132/33 | 2 x 90 |  |  | 8 | 1 |  | Diverse | 8 | 8.0252 | 8.0509 | 8.0772 | 8.1042 | 8.1317 | 8.16 | 8.1888 | 8.2184 | 8.2486 | 8.2795 | 8.3112 | 8.3436 | 8.3768 | Diversity/Losses: 1.011 | 0% | 0% | 46.25% | 13130
[10 empty] | Aggregate | 8.09 | 8.1154 | 8.1415 | 8.1681 | 8.1954 | 8.2232 | 8.2518 | 8.2809 | 8.3108 | 8.3414 | 8.3727 | 8.4047 | 8.4375 | 8.471 |  |  |  | 3.7 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 7.936 | 7.961 | 7.9865 | 8.0126 | 8.0393 | 8.0667 | 8.0947 | 8.1233 | 8.1526 | 8.1826 | 8.2133 | 8.2447 | 8.2768 | 8.3098
| 591 | BETTYHILL | 33/11 | 1 x 2.5 |  | 2018-04-03 | 0.76 | 1 | 0 | 0 | 0.76 | 0.76001 | 0.76003 | 0.76004 | 0.76006 | 0.76007 | 0.76008 | 0.7601 | 0.76011 | 0.76012 | 0.76014 | 0.76015 | 0.76017 | 0.76018 |  | 0% | 0% | 25% | 81909 | [7 empty] | 0.79994 | -0.039941
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.19 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 581 | COLDBACKIE | 33/11 | 1 x 2.5 |  | 2018-04-05 | 0.8 | 1 | L | L | 0.8 | 0.80443 | 0.80889 | 0.81337 | 0.81788 | 0.82241 | 0.82697 | 0.83155 | 0.83616 | 0.8408 | 0.84546 | 0.85014 | 0.85485 | 0.85959 |  | 0% | 0% | 17.5% | 81911 | [7 empty] | 0.84 | -0.04
[6 empty] | 7:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.14 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 598 | DOUNREAY | 33/11 | 2 x 15 |  | 2018-04-04 | 5.02 | 1 | 0 | 0 | 5.02 | 5.0201 | 5.0202 | 5.0203 | 5.0204 | 5.0205 | 5.0205 | 5.0206 | 5.0207 | 5.0208 | 5.0209 | 5.021 | 5.0211 | 5.0212 |  | 0% | 0% | 55.78% | 13185 | [7 empty] | 5.5058 | -0.48576
[6 empty] | 10:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.8 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 583 | FORSS | 33/11 | 1 x 2.5 |  | 2019-02-02 | 0.78 | 1 | H | H | 0.78 | 0.80089 | 0.82235 | 0.84438 | 0.867 | 0.89022 | 0.91407 | 0.93855 | 0.96369 | 0.98951 | 1.016 | 1.0432 | 1.0712 | 1.0999 |  | 0% | 0% | 0% | 81920 | [7 empty] | 0.85414 | -0.074135
[6 empty] | 20:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 590 | MELVICH | 33/11 | 1 x 1 |  | 2019-01-22 | 0.73 | 1 | 0 | 0 | 0.73 | 0.73001 | 0.73003 | 0.73004 | 0.73005 | 0.73007 | 0.73008 | 0.73009 | 0.73011 | 0.73012 | 0.73013 | 0.73015 | 0.73016 | 0.73017 |  | 0% | 0% | 1.37% | 81904 | [7 empty] | 0.8365 | -0.1065
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.01 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
DUDHOPE | 31 |  | 132/33 | 2 x 60 |  |  | 44.7 | 1 |  | Diverse | 44.7 | 44.7727 | 44.8457 | 44.9192 | 44.993 | 45.0673 | 45.142 | 45.2171 | 45.2926 | 45.3685 | 45.4448 | 45.5215 | 45.5987 | 45.6763 | Diversity/Losses: 1.019 | 0% | 0% | 24.83% | 13330
[10 empty] | Aggregate | 45.5384 | 45.6124 | 45.6869 | 45.7617 | 45.8369 | 45.9126 | 45.9887 | 46.0652 | 46.1421 | 46.2194 | 46.2972 | 46.3754 | 46.454 | 46.533 |  |  |  | 11.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 44.3424 | 44.4145 | 44.4869 | 44.5598 | 44.6331 | 44.7068 | 44.7808 | 44.8553 | 44.9302 | 45.0055 | 45.0812 | 45.1574 | 45.2339 | 45.3109
| 32 | CONSTABLE STREET | 33/11 | 2 x 15 |  | 2018-12-15 | 13.25 | 1 | L | L | 13.25 | 13.3234 | 13.3973 | 13.4715 | 13.5462 | 13.6212 | 13.6967 | 13.7726 | 13.849 | 13.9257 | 14.0029 | 14.0805 | 14.1585 | 14.237 |  | 0% | 0% | 24.53% | 82002 | [7 empty] | 13 | 0.25
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.25 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 24 | OVERGATE | 33/11 | 3 x 21 |  | 2019-01-31 | 15.7734 | 1 | 0 | 0 | 15.7734 | 15.7737 | 15.7739 | 15.7742 | 15.7745 | 15.7748 | 15.7751 | 15.7754 | 15.7757 | 15.776 | 15.7763 | 15.7765 | 15.7768 | 15.7771 |  | 0% | 0% | 25.6% | 82010 | [7 empty] | 16.056 | -0.28263
[6 empty] | 13:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4.0387 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 33 | ROSEBANK STREET | 33/11 | 3 x 23 |  | 2019-01-23 | 11.475 | 1 | 0 | 0 | 11.475 | 11.4753 | 11.4755 | 11.4757 | 11.4759 | 11.4761 | 11.4763 | 11.4765 | 11.4767 | 11.4769 | 11.4771 | 11.4773 | 11.4776 | 11.4778 |  | 0% | 0% | 32.41% | 82006 | [7 empty] | 17.04 | -5.565
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.7189 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 25 | WALTON | 33/11 | 2 x 24 |  | 2019-01-23 | 5.04 | 1 | 0 | 0 | 5.04 | 5.0401 | 5.0402 | 5.0403 | 5.0404 | 5.0405 | 5.0406 | 5.0406 | 5.0407 | 5.0408 | 5.0409 | 5.041 | 5.0411 | 5.0412 |  | 0% | 0% | 20.44% | 82021 | [7 empty] | 5.7401 | -0.70007
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.03 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
HELENSBURGH (SP) |  |  | 132/33 | 2 x 60 |  |  |  | 1 |  | Diverse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0% | 0% | 0%
[10 empty] | Aggregate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DUMFIN 11kV Circuit | [5 empty] | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0%
|  | No PI - Scottish Power Site | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
DUNOON | 380 |  | 132/33 | 2 x 45 |  |  | 23.2 | 1 |  | Diverse | 23.2 | 23.2569 | 23.3152 | 23.375 | 23.4364 | 23.4994 | 23.5639 | 23.6302 | 23.6981 | 23.7679 | 23.8394 | 23.9128 | 23.988 | 24.0652 | Diversity/Losses: 0.969 | 0% | 0% | 25.86% | 42930
[10 empty] | Aggregate | 22.4782 | 22.5333 | 22.5898 | 22.6478 | 22.7073 | 22.7683 | 22.8308 | 22.895 | 22.9609 | 23.0284 | 23.0977 | 23.1688 | 23.2417 | 23.3166 |  |  |  | 6 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 23.0144 | 23.0708 | 23.1287 | 23.188 | 23.2489 | 23.3114 | 23.3754 | 23.4411 | 23.5086 | 23.5777 | 23.6487 | 23.7215 | 23.7961 | 23.8727
| 365 | BRUCHAG | 33/11 | 2 x 10 |  | 2018-04-02 | 3.56 | 1 | 0 | 0 | 3.56 | 3.5601 | 3.5601 | 3.5602 | 3.5603 | 3.5603 | 3.5604 | 3.5605 | 3.5605 | 3.5606 | 3.5606 | 3.5607 | 3.5608 | 3.5608 |  | 0% | 0% | 15.17% | 82222 | [7 empty] | 3.83 | -0.27
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.54 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 385 | COLINTRAIVE | 33/11 | 1 x 0.5 |  |  | 0.26408 | 1 | M | M | 0.26408 | 0.26768 | 0.27132 | 0.27501 | 0.27875 | 0.28254 | 0.28639 | 0.29028 | 0.29423 | 0.29824 | 0.30229 | 0.30641 | 0.31058 | 0.3148 |  | 0% | 0% | 0% | 82240 | [7 empty] | 0.21 | 0.054084
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 363 | DUNOON | 33/11 | 2 x 24 |  | 2018-12-15 | 6.93 | 1 | 0 | 0 | 6.93 | 6.9301 | 6.9303 | 6.9304 | 6.9305 | 6.9306 | 6.9308 | 6.9309 | 6.931 | 6.9311 | 6.9313 | 6.9314 | 6.9315 | 6.9316 |  | 0% | 0% | 24.39% | 82204 | [7 empty] | 7.9401 | -1.0101
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.69 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 383 | GLENDARUEL | 33/11 | 1 x 0.3 |  |  | 0.3596 | 1 | H | H | 0.3596 | 0.36924 | 0.37913 | 0.38928 | 0.39971 | 0.41042 | 0.42141 | 0.4327 | 0.44429 | 0.45619 | 0.46841 | 0.48096 | 0.49385 | 0.50707 |  | 0% | 0% | 0% | 82237 | [7 empty] | 0.28 | 0.079604
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 379 | INNELLAN | 33/11 | 1 x 6.25 |  | 2018-12-25 | 0.95 | 1 | 0 | 0 | 0.95 | 0.95002 | 0.95003 | 0.95005 | 0.95007 | 0.95009 | 0.9501 | 0.95012 | 0.95014 | 0.95016 | 0.95017 | 0.95019 | 0.95021 | 0.95023 |  | 0% | 0% | 22.11% | 82209 | [7 empty] | 1.1985 | -0.24853
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.21 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 366 | KAMES | 33/11 | 1 x 2.5 |  | 2019-01-02 | 0.58 | 1 | 0 | 0 | 0.58 | 0.58001 | 0.58002 | 0.58003 | 0.58004 | 0.58005 | 0.58006 | 0.58007 | 0.58008 | 0.5801 | 0.58011 | 0.58012 | 0.58013 | 0.58014 |  | 0% | 0% | 10.34% | 82245 | [7 empty] | 0.56 | 0.02
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.06 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 384 | NEWTON | 33/11 | 1 x 0.3 |  |  | 0.27251 | 1 | 0 | 0 | 0.27251 | 0.27252 | 0.27252 | 0.27253 | 0.27253 | 0.27254 | 0.27254 | 0.27255 | 0.27255 | 0.27256 | 0.27256 | 0.27257 | 0.27257 | 0.27258 |  | 0% | 0% | 0% | 82233 | [7 empty] | 0.48413 | -0.21162
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 375 | OTTER FERRY | 33/11 | 1 x 2.5 |  | 2018-04-03 | 1.5492 | 1 | H | H | 1.5492 | 1.5907 | 1.6333 | 1.6771 | 1.722 | 1.7681 | 1.8155 | 1.8641 | 1.9141 | 1.9653 | 2.018 | 2.072 | 2.1275 | 2.1845 |  | 0% | 0% | 0% | 82249 | [7 empty] | 1.5966 | -0.047382
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 362 | ROTHESAY | 33/11 | 2 x 24 |  | 2018-12-05 | 4.5228 | 1 | 0 | 0 | 4.5228 | 4.5229 | 4.523 | 4.5231 | 4.5231 | 4.5232 | 4.5233 | 4.5234 | 4.5235 | 4.5236 | 4.5236 | 4.5237 | 4.5238 | 4.5239 |  | 0% | 0% | 25.61% | 82218 | [7 empty] | 4.73 | -0.20718
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.1581 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 364 | SANDBANK | 33/11 | 2 x 8 |  | 2019-02-02 | 3.49 | 1 | 0 | 0 | 3.49 | 3.4901 | 3.4901 | 3.4902 | 3.4903 | 3.4903 | 3.4904 | 3.4904 | 3.4905 | 3.4906 | 3.4906 | 3.4907 | 3.4908 | 3.4908 |  | 0% | 0% | 13.18% | 82228 | [7 empty] | 3.8817 | -0.39166
[6 empty] | 19:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.46 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
DUNVEGAN | 638 |  | 132/33 | 1 x 60 |  |  | 8.6 | 1 |  | Diverse | 8.6 | 8.6346 | 8.6697 | 8.7052 | 8.7412 | 8.7778 | 8.8148 | 8.8523 | 8.8903 | 8.9288 | 8.9679 | 9.0075 | 9.0476 | 9.0883 | Diversity/Losses: 0.962 | 0% | 0% | 40.7% | 82301
[10 empty] | Aggregate | 8.2773 | 8.3106 | 8.3443 | 8.3785 | 8.4132 | 8.4484 | 8.484 | 8.5201 | 8.5567 | 8.5938 | 8.6314 | 8.6695 | 8.7081 | 8.7473 |  |  |  | 3.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 8.5312 | 8.5655 | 8.6003 | 8.6356 | 8.6713 | 8.7075 | 8.7443 | 8.7815 | 8.8192 | 8.8574 | 8.8962 | 8.9354 | 8.9752 | 9.0156
| 638 | DUNVEGAN | 33/11 | 1 x 4 |  | 2018-04-03 | 2.44 | 1 | M | M | 2.44 | 2.4732 | 2.5068 | 2.5409 | 2.5755 | 2.6106 | 2.6461 | 2.6821 | 2.7186 | 2.7555 | 2.793 | 2.831 | 2.8696 | 2.9086 |  | 0% | 0% | 19.67% | 82311
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.48 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 632 | PORTREE | 33/11 | 1 x 8 & 1 x 7.5 |  | 2019-02-01 | 4.6273 | 1 | 0 | 0 | 4.6273 | 4.6274 | 4.6275 | 4.6275 | 4.6276 | 4.6277 | 4.6278 | 4.6279 | 4.628 | 4.628 | 4.6281 | 4.6282 | 4.6283 | 4.6284 |  | 0% | 0% | 22.51% | 82304 | [7 empty] | 4.93 | -0.30272
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.0415 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 640 | UIG | 33/11 | 1 x 2.5 |  | 2018-04-03 | 1.21 | 1 | 0 | 0 | 1.21 | 1.21 | 1.21 | 1.2101 | 1.2101 | 1.2101 | 1.2101 | 1.2102 | 1.2102 | 1.2102 | 1.2102 | 1.2102 | 1.2103 | 1.2103 |  | 0% | 0% | 16.53% | 82309 | [7 empty] | 1.2752 | -0.065175
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
DYCE | 843 |  | 132/33 | 2 x 60 |  |  | 43.5 | 1 |  | Diverse | 43.5 | 43.5008 | 43.5016 | 43.5024 | 43.5032 | 43.504 | 43.5048 | 43.5056 | 43.5064 | 43.5071 | 43.5079 | 43.5087 | 43.5095 | 43.5103 | Diversity/Losses: 0.95 | 0% | 0% | 18.62% | 13530
[10 empty] | Aggregate | 41.337 | 41.3378 | 41.3385 | 41.3393 | 41.34 | 41.3408 | 41.3415 | 41.3423 | 41.343 | 41.3438 | 41.3445 | 41.3453 | 41.3461 | 41.3468 |  |  |  | 8.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 43.152 | 43.1528 | 43.1536 | 43.1544 | 43.1552 | 43.1559 | 43.1567 | 43.1575 | 43.1583 | 43.1591 | 43.1599 | 43.1607 | 43.1615 | 43.1622
| 807 | BALMEDIE | 33/11 | 1 x 8 |  | 2018-12-13 | 3.58 | 1 | 0 | 0 | 3.58 | 3.5801 | 3.5801 | 3.5802 | 3.5803 | 3.5803 | 3.5804 | 3.5805 | 3.5805 | 3.5806 | 3.5807 | 3.5807 | 3.5808 | 3.5808 |  | 0% | 0% | 17.04% | 82416 | [7 empty] | 3.78 | -0.2
[6 empty] | 17:30 |  |  |  |  | 43.152: Committed new connections: |  |  |  | 0.61 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 43.1567: Generation at time of peak:; 0 43.1575: 0
| 844 | DYCE NORTH | 33/11 | 2 x 24 |  | 2019-01-23 | 15.46 | 1 | 0 | 0 | 15.46 | 15.4603 | 15.4606 | 15.4608 | 15.4611 | 15.4614 | 15.4617 | 15.462 | 15.4623 | 15.4625 | 15.4628 | 15.4631 | 15.4634 | 15.4637 |  | 0% | 0% | 28.65% | 82406 | [7 empty] | 15.7585 | -0.2985
[6 empty] | 9:00 |  |  |  |  | 43.152: Committed new connections: |  |  |  | 4.43 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 43.1567: Generation at time of peak:; 0 43.1575: 0
| 849 | ELLON 11 kV | 33/11 | 2 x 12.5 |  | 2018-12-05 | 10.96 | 1 | 0 | 0 | 10.96 | 10.9602 | 10.9604 | 10.9606 | 10.9608 | 10.961 | 10.9612 | 10.9614 | 10.9616 | 10.9618 | 10.962 | 10.9622 | 10.9624 | 10.9626 |  | 0% | 0% | 25.82% | 82427 | [7 empty] | 11.6381 | -0.67808
[6 empty] | 17:30 |  |  |  |  | 43.152: Committed new connections: |  |  |  | 2.83 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 43.1567: Generation at time of peak:; 0 43.1575: 0
| 991 | HARVEST AVENUE | 33/11 | 2 x 24 |  | 2019-01-21 | 0.64 | 1 | ? | 0 | 0.64 | 0.64001 | 0.64002 | 0.64004 | 0.64005 | 0.64006 | 0.64007 | 0.64008 | 0.64009 | 0.64011 | 0.64012 | 0.64013 | 0.64014 | 0.64015 |  | 0% | 0% | 0% | 82440 | [7 empty] | 0.64697 | -0.0069733
|  | (New Primary - Little Data) |  |  |  | 7:00 |  |  |  |  | 43.152: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[17 empty] | Generation at time of peak: | 0
| 884 | KINGSEAT | 33/11 | 2 x 5 |  | 2018-12-25 | 3.61 | 1 | 0 | 0 | 3.61 | 3.6101 | 3.6101 | 3.6102 | 3.6103 | 3.6103 | 3.6104 | 3.6105 | 3.6105 | 3.6106 | 3.6107 | 3.6107 | 3.6108 | 3.6109 |  | 0% | 0% | 6.648% | 82409 | [7 empty] | 3.92 | -0.31
[6 empty] | 13:00 |  |  |  |  | 43.152: Committed new connections: |  |  |  | 0.24 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 43.1567: Generation at time of peak:; 0 43.1575: 0
| 947 | STONEYWOOD T3 | 33/11 | 1 x 24 |  | 2019-01-08 | 7.087 | 1 | 0 | 0 | 7.087 | 7.0871 | 7.0873 | 7.0874 | 7.0875 | 7.0876 | 7.0878 | 7.0879 | 7.088 | 7.0882 | 7.0883 | 7.0884 | 7.0886 | 7.0887 |  | 0% | 0% | 0% | 82403 | [7 empty] | 6.7964 | 0.29061
|  | T3 |  |  |  | 14:30 |  |  |  |  | 43.152: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 43.1567: Generation at time of peak:; 0 43.1575: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
ELGIN | 456 |  | 132/33 | 2 x 90 |  |  | 47.7 | 1 |  | Diverse | 47.7 | 47.7009 | 47.7017 | 47.7026 | 47.7035 | 47.7044 | 47.7052 | 47.7061 | 47.707 | 47.7078 | 47.7087 | 47.7096 | 47.7105 | 47.7113 | Diversity/Losses: 1.055 | 0% | 0% | 26.83% | 13630
[10 empty] | Aggregate | 50.34 | 50.3409 | 50.3418 | 50.3428 | 50.3437 | 50.3446 | 50.3455 | 50.3464 | 50.3474 | 50.3483 | 50.3492 | 50.3501 | 50.351 | 50.3519 |  |  |  | 12.8 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 47.3184 | 47.3193 | 47.3201 | 47.321 | 47.3219 | 47.3227 | 47.3236 | 47.3244 | 47.3253 | 47.3262 | 47.327 | 47.3279 | 47.3288 | 47.3296
| 458 | ASHGROVE | 33/11 | 1 x 10 |  | 2018-12-10 | 6.73 | 1 | 0 | 0 | 6.73 | 6.7301 | 6.7302 | 6.7304 | 6.7305 | 6.7306 | 6.7307 | 6.7309 | 6.731 | 6.7311 | 6.7312 | 6.7314 | 6.7315 | 6.7316 |  | 0% | 0% | 20.95% | 82513 | [7 empty] | 7.3287 | -0.59865
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.41 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 499 | BILBOHALL | 33/11 | 1 x 24 |  | 2019-01-23 | 3.57 | 1 | 0 | 0 | 3.57 | 3.5701 | 3.5701 | 3.5702 | 3.5703 | 3.5703 | 3.5704 | 3.5705 | 3.5705 | 3.5706 | 3.5707 | 3.5707 | 3.5708 | 3.5708 |  | 0% | 0% | 4.482% | 82502 | [7 empty] | 4.0358 | -0.46576
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.16 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 454 | BURGHEAD | 33/11 | 2 x 15 |  | 2018-12-05 | 6.71 | 1 | 0 | 0 | 6.71 | 6.7101 | 6.7102 | 6.7104 | 6.7105 | 6.7106 | 6.7107 | 6.7109 | 6.711 | 6.7111 | 6.7112 | 6.7113 | 6.7115 | 6.7116 |  | 0% | 0% | 37.56% | 82534 | [7 empty] | 7.21 | -0.5
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.52 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 457 | CUMMING STREET | 33/11 | 2 x 24 |  | 2018-12-05 | 12.4 | 1 | 0 | 0 | 12.4 | 12.4002 | 12.4005 | 12.4007 | 12.4009 | 12.4011 | 12.4014 | 12.4016 | 12.4018 | 12.402 | 12.4023 | 12.4025 | 12.4027 | 12.4029 |  | 0% | 0% | 22.58% | 82518 | [7 empty] | 12.719 | -0.319
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.8 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 482 | ELGIN | 33/11 | 2 x 10 |  | 2019-01-20 | 4.24 | 1 | 0 | 0 | 4.24 | 4.2401 | 4.2402 | 4.2402 | 4.2403 | 4.2404 | 4.2405 | 4.2405 | 4.2406 | 4.2407 | 4.2408 | 4.2409 | 4.2409 | 4.241 |  | 0% | 0% | 16.98% | 82535 | [7 empty] | 4.5242 | -0.28418
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.72 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 487 | FOCHABERS | 33/11 | 2 x 15 |  | 2019-01-29 | 6.03 | 1 | 0 | 0 | 6.03 | 6.0301 | 6.0302 | 6.0303 | 6.0304 | 6.0306 | 6.0307 | 6.0308 | 6.0309 | 6.031 | 6.0311 | 6.0312 | 6.0313 | 6.0314 |  | 0% | 0% | 25.87% | 82505 | 83661 | [6 empty] | 6.1754 | -0.14539
|  | (1 x Elgin, 1 x Keith) |  |  |  | 43138.3546 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.56 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 453 | KINLOSS | 33/11 | 2 x 15 |  | 2019-01-09 | 2.76 | 1 | 0 | 0 | 2.76 | 2.7601 | 2.7601 | 2.7602 | 2.7602 | 2.7603 | 2.7603 | 2.7604 | 2.7604 | 2.7605 | 2.7605 | 2.7606 | 2.7606 | 2.7607 |  | 0% | 0% | 0% | 82506 | 84542 | [6 empty] | 3.31 | -0.55
|  | (1 x Elgin, 1 x Nairn) |  |  |  | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 488 | LHANBRYDE | 33/11 | 2 x 5 |  | 2018-12-25 | 1.38 | 1 | 0 | 0 | 1.38 | 1.38 | 1.3801 | 1.3801 | 1.3801 | 1.3801 | 1.3802 | 1.3802 | 1.3802 | 1.3802 | 1.3803 | 1.3803 | 1.3803 | 1.3803 |  | 0% | 0% | 3.623% | 82523 | [7 empty] | 1.83 | -0.45
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 455 | LOSSIEMOUTH | 33/11 | 2 x 15 |  | 2019-01-29 | 6.52 | 1 | 0 | 0 | 6.52 | 6.5201 | 6.5202 | 6.5204 | 6.5205 | 6.5206 | 6.5207 | 6.5208 | 6.521 | 6.5211 | 6.5212 | 6.5213 | 6.5214 | 6.5215 |  | 0% | 0% | 34.66% | 82526 | [7 empty] | 6.6348 | -0.11484
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.26 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
FASNAKYLE | 521 |  | 275/33 | 2 x 120 |  |  | 0.63 | 1 |  | Diverse | 0.63 | 0.63001 | 0.63002 | 0.63003 | 0.63005 | 0.63006 | 0.63007 | 0.63008 | 0.63009 | 0.6301 | 0.63012 | 0.63013 | 0.63014 | 0.63015 | Diversity/Losses: 1 | 0% | 0% | 9.524% | 13830
[10 empty] | Aggregate | 0.63 | 0.63001 | 0.63002 | 0.63003 | 0.63005 | 0.63006 | 0.63007 | 0.63008 | 0.63009 | 0.6301 | 0.63012 | 0.63013 | 0.63014 | 0.63015 |  |  |  | 0.06 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 0.62496 | 0.62497 | 0.62498 | 0.62499 | 0.62501 | 0.62502 | 0.62503 | 0.62504 | 0.62505 | 0.62506 | 0.62507 | 0.62509 | 0.6251 | 0.62511
| 519 | FASNAKYLE PRIMARY | 33/11 | 1 x 1 |  | 2018-04-03 | 0.63 | 1 | 0 | 0 | 0.63 | 0.63001 | 0.63002 | 0.63003 | 0.63005 | 0.63006 | 0.63007 | 0.63008 | 0.63009 | 0.6301 | 0.63012 | 0.63013 | 0.63014 | 0.63015 |  | 0% | 0% | 9.524% | 82606 | [7 empty] | 0.52394 | 0.10606
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.06 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
FIDDES | 851 |  | 132/33 | 2 x 90 |  |  | 19.8 | 1 |  | Diverse | 19.8 | 19.8004 | 19.8007 | 19.8011 | 19.8014 | 19.8018 | 19.8022 | 19.8025 | 19.8029 | 19.8033 | 19.8036 | 19.804 | 19.8043 | 19.8047 | Diversity/Losses: 1.022 | 0% | 0% | 19.7% | 14030
[10 empty] | Aggregate | 20.23 | 20.2304 | 20.2307 | 20.2311 | 20.2315 | 20.2318 | 20.2322 | 20.2326 | 20.233 | 20.2333 | 20.2337 | 20.2341 | 20.2344 | 20.2348 |  |  |  | 3.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 19.6416 | 19.642 | 19.6423 | 19.6427 | 19.643 | 19.6434 | 19.6438 | 19.6441 | 19.6445 | 19.6448 | 19.6452 | 19.6455 | 19.6459 | 19.6463
| 847 | EDZELL | 33/11 | 1 x 8 |  | 2018-12-05 | 2.52 | 1 | 0 | 0 | 2.52 | 2.52 | 2.5201 | 2.5201 | 2.5202 | 2.5202 | 2.5203 | 2.5203 | 2.5204 | 2.5204 | 2.5205 | 2.5205 | 2.5206 | 2.5206 |  | 0% | 0% | 6.349% | 82706 | [7 empty] | 2.6561 | -0.13608
[6 empty] | 15:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.16 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 873 | INVERBERVIE | 33/11 | 2 x 8 |  | 2018-12-24 | 3.01 | 1 | 0 | 0 | 3.01 | 3.0101 | 3.0101 | 3.0102 | 3.0102 | 3.0103 | 3.0103 | 3.0104 | 3.0104 | 3.0105 | 3.0105 | 3.0106 | 3.0107 | 3.0107 |  | 0% | 0% | 0% | 82714 | [7 empty] | 3.1963 | -0.1863
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 890 | LAURENCEKIRK | 33/11 | 2 x 5 |  | 2018-12-04 | 5.01 | 1 | 0 | 0 | 5.01 | 5.0101 | 5.0102 | 5.0103 | 5.0104 | 5.0105 | 5.0105 | 5.0106 | 5.0107 | 5.0108 | 5.0109 | 5.011 | 5.0111 | 5.0112 |  | 0% | 0% | 1.996% | 82710 | [7 empty] | 5.09 | -0.08
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 945 | STONEHAVEN | 33/11 | 2 x 24 |  | 2019-01-31 | 9.69 | 1 | 0 | 0 | 9.69 | 9.6902 | 9.6904 | 9.6905 | 9.6907 | 9.6909 | 9.6911 | 9.6912 | 9.6914 | 9.6916 | 9.6918 | 9.6919 | 9.6921 | 9.6923 |  | 0% | 0% | 21.67% | 82703 | [7 empty] | 10.2704 | -0.58036
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
FORT AUGUSTUS | 716 |  | 132/33 | 1 x 15 |  |  | 5 | 1 |  | Diverse | 5 | 5.0026 | 5.0053 | 5.0081 | 5.0109 | 5.0139 | 5.0169 | 5.0199 | 5.0231 | 5.0263 | 5.0296 | 5.033 | 5.0365 | 5.0401 | Diversity/Losses: 0.829 | 0% | 0% | 30% | 13930
[10 empty] | Aggregate | 4.1437 | 4.1459 | 4.1481 | 4.1504 | 4.1528 | 4.1552 | 4.1577 | 4.1602 | 4.1628 | 4.1655 | 4.1682 | 4.1711 | 4.1739 | 4.1769 |  |  |  | 1.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 4.96 | 4.9626 | 4.9653 | 4.968 | 4.9709 | 4.9737 | 4.9767 | 4.9798 | 4.9829 | 4.9861 | 4.9894 | 4.9928 | 4.9962 | 4.9998
| 710 | ABERCHALDER | 33/11 | 1 x 0.2 |  |  | 0.078663 | 1 | H | H | 0.078663 | 0.080771 | 0.082934 | 0.085156 | 0.087437 | 0.089779 | 0.092184 | 0.094653 | 0.097189 | 0.099792 | 0.10247 | 0.10521 | 0.10803 | 0.11092 |  | 0% | 0% | 0% | 82807 | [7 empty] | 0.07 | 0.0086634
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 894 | ARDOCHY | 33/11 | 0.1 |  |  | 0.022475 | 1 | ? | 0 | 0.022475 | 0.022476 | 0.022476 | 0.022476 | 0.022477 | 0.022477 | 0.022478 | 0.022478 | 0.022479 | 0.022479 | 0.022479 | 0.02248 | 0.02248 | 0.022481 |  | 0% | 0% | 133.5%
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 745 | BUNOICH | 33/11 | 1 x 2 |  | 2019-02-03 | 0.18 | 1 | 0 | 0 | 0.18 | 0.18 | 0.18001 | 0.18001 | 0.18001 | 0.18002 | 0.18002 | 0.18002 | 0.18003 | 0.18003 | 0.18003 | 0.18004 | 0.18004 | 0.18004 |  | 0% | 0% | 16.67% | 82816 | [7 empty] | 0.2 | -0.02
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.03 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 517 | DRUMNADROCHIT | 33/11 | 1 x 6 |  | 2019-02-01 | 2.39 | 1 | 0 | 0 | 2.39 | 2.39 | 2.3901 | 2.3901 | 2.3902 | 2.3902 | 2.3903 | 2.3903 | 2.3903 | 2.3904 | 2.3904 | 2.3905 | 2.3905 | 2.3906 |  | 0% | 0% | 16.74% | 82814 | [7 empty] | 2.7259 | -0.33593
[6 empty] | 7:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 396 | GLEN LAOGH | 33/11 | 1 x 0.1 |  |  | 0.0084282 | 1 | 0 | 0 | 0.0084282 | 0.0084284 | 0.0084285 | 0.0084287 | 0.0084288 | 0.008429 | 0.0084291 | 0.0084293 | 0.0084295 | 0.0084296 | 0.0084298 | 0.0084299 | 0.0084301 | 0.0084302 |  | 0% | 0% | 0% | [8 empty] | 0.01 | -0.0015718
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 781 | GLENDOE PRIMARY | 33/11 | 1 x 15 |  | 2018-07-10 | 0.95 | 1 | 0 | 0 | 0.95 | 0.95002 | 0.95003 | 0.95005 | 0.95007 | 0.95009 | 0.9501 | 0.95012 | 0.95014 | 0.95016 | 0.95017 | 0.95019 | 0.95021 | 0.95023 |  | 0% | 0% | 29.47% | 82823 | [7 empty] | 0.95271 | -0.002708
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.28 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 766 | INVERGARRY | 33/11 | 1 x 1 |  |  | 0.4776 | 1 | 0 | 0 | 0.4776 | 0.47761 | 0.47762 | 0.47763 | 0.47763 | 0.47764 | 0.47765 | 0.47766 | 0.47767 | 0.47768 | 0.47769 | 0.4777 | 0.4777 | 0.47771 |  | 0% | 0% | 0% | 82810 | [7 empty] | 0.55 | -0.072401
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 763 | WESTER DRUMMOND | 33/11 | 1 x 0.1 |  |  | 0.036522 | 1 | 0 | 0 | 0.036522 | 0.036523 | 0.036524 | 0.036524 | 0.036525 | 0.036526 | 0.036526 | 0.036527 | 0.036528 | 0.036528 | 0.036529 | 0.03653 | 0.03653 | 0.036531 |  | 0% | 0% | 0% | 82831 | [7 empty] | 0.08 | -0.043478
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
FORT WILLIAM | 715 |  | 132/33 | 2 x 120 |  |  | 65.7 | 1 |  | Diverse | 65.7 | 66.302 | 66.9202 | 67.5549 | 68.2065 | 68.8756 | 69.5627 | 70.268 | 70.9923 | 71.7359 | 72.4995 | 73.2835 | 74.0884 | 74.9149 | Diversity/Losses: 0.524 | 0% | 0% | 8.524% | 14430
[10 empty] | Aggregate | 34.4172 | 34.7326 | 35.0564 | 35.3889 | 35.7302 | 36.0807 | 36.4406 | 36.8102 | 37.1896 | 37.5791 | 37.9791 | 38.3898 | 38.8115 | 39.2444 |  |  |  | 5.6 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 65.1744 | 65.7716 | 66.3848 | 67.0144 | 67.6609 | 68.3246 | 69.0062 | 69.7059 | 70.4244 | 71.1621 | 71.9195 | 72.6972 | 73.4957 | 74.3156
| 702 | ANNAT | 33/11 | 1 x 15 |  | 2018-11-26 | 2.68 | 1 | 0 | 0 | 2.68 | 2.68 | 2.6801 | 2.6801 | 2.6802 | 2.6802 | 2.6803 | 2.6803 | 2.6804 | 2.6804 | 2.6805 | 2.6805 | 2.6806 | 2.6806 |  | 0% | 0% | 14.93% | 82961 | [7 empty] | 2.9068 | -0.22683
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 740 | ARISAIG | 33/11 | 1 x 2.5 |  | 2018-12-25 | 0.65 | 1 | 0 | 0 | 0.65 | 0.65001 | 0.65002 | 0.65004 | 0.65005 | 0.65006 | 0.65007 | 0.65008 | 0.65009 | 0.65011 | 0.65012 | 0.65013 | 0.65014 | 0.65015 |  | 0% | 0% | 18.46% | 82966 | [7 empty] | 0.68138 | -0.031375
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.12 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 744 | CORRAN | 33/11 | 1 x 2.5 |  | 2018-04-01 | 1.33 | 1 | 0 | 0 | 1.33 | 1.33 | 1.33 | 1.3301 | 1.3301 | 1.3301 | 1.3301 | 1.3302 | 1.3302 | 1.3302 | 1.3302 | 1.3303 | 1.3303 | 1.3303 |  | 0% | 0% | 5.263% | 82931 | [7 empty] | 1.34 | -0.01
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.07 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 714 | GLENSANDA | 33/11 | 2 x 15 |  | 2018-10-05 | 6.6 | 1 | H | H | 6.6 | 6.7768 | 6.9583 | 7.1447 | 7.3361 | 7.5326 | 7.7344 | 7.9416 | 8.1543 | 8.3728 | 8.597 | 8.8273 | 9.0638 | 9.3066 |  | 0% | 0% | 3.636% | 82927 | [7 empty] | 6.5761 | 0.023922
[6 empty] | 15:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.24 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 756 | GLENUIG | 33/11 | 1 x 0.1 |  |  | 0.078663 | 1 | H | H | 0.078663 | 0.080771 | 0.082934 | 0.085156 | 0.087437 | 0.089779 | 0.092184 | 0.094653 | 0.097189 | 0.099792 | 0.10247 | 0.10521 | 0.10803 | 0.11092 |  | 0% | 0% | 0% | [8 empty] | 0.06 | 0.018663
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 724 | INVERLOCHY | 33/11 | 2 x 15 |  | 2019-01-30 | 9.1 | 1 | 0 | 0 | 9.1 | 9.1002 | 9.1003 | 9.1005 | 9.1007 | 9.1008 | 9.101 | 9.1012 | 9.1013 | 9.1015 | 9.1017 | 9.1018 | 9.102 | 9.1022 |  | 0% | 0% | 11.32% | 82956 | [7 empty] | 10.6882 | -1.5882
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.03 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 771 | KINGAIRLOCH | 33/11 | 1 x 0.1 |  |  | 0.081473 | 1 | H | H | 0.081473 | 0.083655 | 0.085896 | 0.088197 | 0.09056 | 0.092986 | 0.095476 | 0.098034 | 0.10066 | 0.10336 | 0.10613 | 0.10897 | 0.11189 | 0.11488 |  | 0% | 0% | 0% | [8 empty] | 0.06 | 0.021473
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 754 | KINLOCHMOIDART | 33/11 | 1 x 2 |  |  | 0.070235 | 1 | 0 | 0 | 0.070235 | 0.070236 | 0.070238 | 0.070239 | 0.07024 | 0.070242 | 0.070243 | 0.070244 | 0.070245 | 0.070247 | 0.070248 | 0.070249 | 0.070251 | 0.070252 |  | 0% | 0% | 0% | 82974 | [7 empty] | 0.12 | -0.049765
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 721 | LIDDESDALE | 33/11 | 1 x 0.1 |  | 2018-12-04 | 0.77 | 1 | H | H | 0.77 | 0.79063 | 0.81181 | 0.83355 | 0.85588 | 0.87881 | 0.90235 | 0.92652 | 0.95134 | 0.97682 | 1.003 | 1.0299 | 1.0574 | 1.0858 |  | 0% | 0% | 18.18% | [8 empty] | 0.86 | -0.09
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 747 | LOCHALINE | 33/11 | 1 x 5 |  | 2018-04-03 | 0.86 | 1 | H | H | 0.86 | 0.88304 | 0.90669 | 0.93098 | 0.95592 | 0.98152 | 1.0078 | 1.0348 | 1.0625 | 1.091 | 1.1202 | 1.1502 | 1.181 | 1.2127 |  | 0% | 0% | 0% | 82980 | [7 empty] | 0.85 | 0.01
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 731 | MALLAIG | 33/11 | 1 x 6.3 |  | 2019-01-31 | 1.5616 | 1 | 0 | 0 | 1.5616 | 1.5616 | 1.5616 | 1.5617 | 1.5617 | 1.5617 | 1.5617 | 1.5618 | 1.5618 | 1.5618 | 1.5619 | 1.5619 | 1.5619 | 1.5619 |  | 0% | 0% | 25.59% | 82971 | [7 empty] | 1.8719 | -0.31034
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.39966 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 734 | PINEGROVE | 33/11 | 2 x 10 |  | 2018-04-03 | 6.3474 | 1 | 0 | 0 | 6.3474 | 6.3475 | 6.3476 | 6.3477 | 6.3478 | 6.348 | 6.3481 | 6.3482 | 6.3483 | 6.3484 | 6.3485 | 6.3487 | 6.3488 | 6.3489 |  | 0% | 0% | 24.11% | 82935 | [7 empty] | 6.88 | -0.53262
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.5302 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 753 | POOR HOUSE | 33/11 | 1 x 0.1 |  |  | 0.019666 | 1 | 0 | 0 | 0.019666 | 0.019666 | 0.019667 | 0.019667 | 0.019667 | 0.019668 | 0.019668 | 0.019668 | 0.019669 | 0.019669 | 0.019669 | 0.01967 | 0.01967 | 0.019671 |  | 0% | 0% | 0% | [8 empty] | 0.03 | -0.010334
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 732 | RAHOY | 33/11 | 1 x 1 |  |  | 0.042141 | 1 | 0 | 0 | 0.042141 | 0.042142 | 0.042143 | 0.042143 | 0.042144 | 0.042145 | 0.042146 | 0.042147 | 0.042147 | 0.042148 | 0.042149 | 0.04215 | 0.04215 | 0.042151 |  | 0% | 0% | 0% | 82905 | [7 empty] | 0.05 | -0.0078589
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 749 | SALEN 2 | 33/11 | 1 x 2.5 |  | 2018-04-03 | 3.3679 | 1 | H | H | 3.3679 | 3.4582 | 3.5508 | 3.6459 | 3.7436 | 3.8439 | 3.9468 | 4.0526 | 4.1611 | 4.2726 | 4.387 | 4.5045 | 4.6252 | 4.7491 |  | 0% | 0% | 0.2611% | 82921 | [7 empty] | 2.86 | 0.50795
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.008794 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 755 | SHONA BEAG | 33/11 | 1 x 0.1 |  |  | 0.028094 | 1 | 0 | 0 | 0.028094 | 0.028095 | 0.028095 | 0.028096 | 0.028096 | 0.028097 | 0.028097 | 0.028098 | 0.028098 | 0.028099 | 0.028099 | 0.0281 | 0.0281 | 0.028101 |  | 0% | 0% | 0% | [8 empty] | 0.05 | -0.021906
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 751 | STRONTIAN | 33/11 | 1 x 2.5 |  | 2019-02-01 | 0.83 | 1 | 0 | 0 | 0.83 | 0.83002 | 0.83003 | 0.83005 | 0.83006 | 0.83008 | 0.83009 | 0.83011 | 0.83012 | 0.83014 | 0.83015 | 0.83017 | 0.83018 | 0.8302 |  | 0% | 0% | 9.639% | 82919 | [7 empty] | 0.92456 | -0.094556
[6 empty] | 7:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.08 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
FRASERBURGH | 853 |  | 132/33 | 2 x 45 |  |  | 19.4 | 1 |  | Diverse | 19.4 | 19.4004 | 19.4007 | 19.4011 | 19.4014 | 19.4018 | 19.4021 | 19.4025 | 19.4028 | 19.4032 | 19.4035 | 19.4039 | 19.4043 | 19.4046 | Diversity/Losses: 0.984 | 0% | 0% | 30.93% | 14330
[10 empty] | Aggregate | 19.09 | 19.0903 | 19.0907 | 19.091 | 19.0914 | 19.0917 | 19.0921 | 19.0924 | 19.0928 | 19.0931 | 19.0935 | 19.0938 | 19.0942 | 19.0945 |  |  |  | 6 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 19.2448 | 19.2452 | 19.2455 | 19.2459 | 19.2462 | 19.2466 | 19.2469 | 19.2473 | 19.2476 | 19.248 | 19.2483 | 19.2487 | 19.249 | 19.2494
| 854 | FRASERBURGH | 33/11 | 2 x 40 |  | 2019-02-01 | 19.09 | 1 | 0 | 0 | 19.09 | 19.0903 | 19.0907 | 19.091 | 19.0914 | 19.0917 | 19.0921 | 19.0924 | 19.0928 | 19.0931 | 19.0935 | 19.0938 | 19.0942 | 19.0945 |  | 0% | 0% | 22.79% | 83000 | [7 empty] | 19.5522 | -0.46216
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4.35 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
GRUDIE BRIDGE | 526 |  | 132/33 | 2 x 90 |  |  | 9.9 | 1 |  | Diverse | 9.9 | 9.9219 | 9.9445 | 9.9676 | 9.9913 | 10.0157 | 10.0407 | 10.0664 | 10.0927 | 10.1198 | 10.1476 | 10.1761 | 10.2054 | 10.2354 | Diversity/Losses: 1.011 | 0% | 0% | 12.12% | 14830
[10 empty] | Aggregate | 10.0046 | 10.0268 | 10.0495 | 10.0729 | 10.0969 | 10.1215 | 10.1468 | 10.1727 | 10.1994 | 10.2267 | 10.2548 | 10.2836 | 10.3132 | 10.3436 |  |  |  | 1.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 9.8208 | 9.8426 | 9.8649 | 9.8878 | 9.9114 | 9.9355 | 9.9603 | 9.9858 | 10.012 | 10.0388 | 10.0664 | 10.0947 | 10.1237 | 10.1535
| 505 | ACHILTIBUIE | 33/11 | 1 x 1 |  | 2018-07-28 | 0.81 | 1 | H | H | 0.81 | 0.8317 | 0.85398 | 0.87685 | 0.90034 | 0.92446 | 0.94922 | 0.97465 | 1.0008 | 1.0276 | 1.0551 | 1.0834 | 1.1124 | 1.1422 |  | 0% | 0% | 0% | 83335 | [7 empty] | 0.55 | 0.26
[6 empty] | 10:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 504 | AULTBEA | 33/11 | 1 x 6 |  | 2019-03-21 | 1.69 | 1 | 0 | 0 | 1.69 | 1.69 | 1.6901 | 1.6901 | 1.6901 | 1.6902 | 1.6902 | 1.6902 | 1.6902 | 1.6903 | 1.6903 | 1.6903 | 1.6904 | 1.6904 |  | 0% | 0% | 15.38% | 83310 | [7 empty] | 2.0051 | -0.31513
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.26 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 535 | BIDEN CLAN RAONAILD | 33/11 | 1 x 0.1 |  |  | 0.0028094 | 1 | 0 | 0 | 0.0028094 | 0.0028095 | 0.0028095 | 0.0028096 | 0.0028096 | 0.0028097 | 0.0028097 | 0.0028098 | 0.0028098 | 0.0028099 | 0.0028099 | 0.00281 | 0.00281 | 0.0028101 |  | 0% | 0% | 0% | [8 empty] | 0.1 | -0.097191
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 518 | DRUMRUNIE | 33/11 | 1 x 0.2 |  |  | 0.32589 | 1 | 0 | 0 | 0.32589 | 0.3259 | 0.3259 | 0.32591 | 0.32592 | 0.32592 | 0.32593 | 0.32593 | 0.32594 | 0.32594 | 0.32595 | 0.32596 | 0.32596 | 0.32597 |  | 0% | 0% | 0% | 83332 | [7 empty] | 0.35 | -0.024109
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 567 | GARBAT FOREST | 33/11 | 1 x 0.1 |  |  | 0.0056188 | 1 | 0 | 0 | 0.0056188 | 0.0056189 | 0.005619 | 0.0056191 | 0.0056192 | 0.0056193 | 0.0056194 | 0.0056195 | 0.0056196 | 0.0056197 | 0.0056198 | 0.0056199 | 0.00562 | 0.0056202 |  | 0% | 0% | 0% | [8 empty] | 0.01 | -0.0043812
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 527 | INVERBROOM | 33/11 | 1 x 0.2 |  |  | 0.21913 | 1 | 0 | 0 | 0.21913 | 0.21914 | 0.21914 | 0.21915 | 0.21915 | 0.21915 | 0.21916 | 0.21916 | 0.21917 | 0.21917 | 0.21917 | 0.21918 | 0.21918 | 0.21919 |  | 0% | 0% | 0% | 83321 | [7 empty] | 0.23 | -0.010866
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 531 | KERRY FALLS | 33/11 | 1 x 6 |  | 2018-04-03 | 2.12 | 1 | 0 | 0 | 2.12 | 2.12 | 2.1201 | 2.1201 | 2.1202 | 2.1202 | 2.1202 | 2.1203 | 2.1203 | 2.1203 | 2.1204 | 2.1204 | 2.1205 | 2.1205 |  | 0% | 0% | 5.189% | 83308 | [7 empty] | 2.04 | 0.08
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.11 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 532 | KINLOCHEWE | 33/11 | 1 x 1 |  |  | 0.9243 | 1 | 0 | 0 | 0.9243 | 0.92431 | 0.92433 | 0.92435 | 0.92436 | 0.92438 | 0.9244 | 0.92441 | 0.92443 | 0.92445 | 0.92446 | 0.92448 | 0.9245 | 0.92451 |  | 0% | 0% | 0% | 83347 | [7 empty] | 0.95 | -0.025705
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 507 | LETTEREWE | 33/11 | 1 x 0.1 |  |  | 0.011238 | 1 | H | H | 0.011238 | 0.011539 | 0.011848 | 0.012165 | 0.012491 | 0.012826 | 0.013169 | 0.013522 | 0.013884 | 0.014256 | 0.014638 | 0.01503 | 0.015433 | 0.015846 |  | 0% | 0% | 0% | 83367 | [7 empty] | 0.01 | 0.0012376
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 568 | LOCH GLASCARNOCH | 33/11 | 1 x 0.5 |  |  | 0.0028094 | 1 | 0 | 0 | 0.0028094 | 0.0028095 | 0.0028095 | 0.0028096 | 0.0028096 | 0.0028097 | 0.0028097 | 0.0028098 | 0.0028098 | 0.0028099 | 0.0028099 | 0.00281 | 0.00281 | 0.0028101 |  | 0% | 0% | 0% | [8 empty] | 0.01 | -0.0071906
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 556 | LOCHINVER | 33/11 | 1 x 2.5 |  | 2018-04-03 | 1.56 | 1 | 0 | 0 | 1.56 | 1.56 | 1.5601 | 1.5601 | 1.5601 | 1.5601 | 1.5602 | 1.5602 | 1.5602 | 1.5603 | 1.5603 | 1.5603 | 1.5603 | 1.5604 |  | 0% | 0% | 19.87% | 83340 | [7 empty] | 1.4958 | 0.064229
[6 empty] | 6:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.31 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 564 | MINOR GRUDIE | 33/11 | 1 x 0.1 |  |  | 0.0028094 | 1 | 0 | 0 | 0.0028094 | 0.0028095 | 0.0028095 | 0.0028096 | 0.0028096 | 0.0028097 | 0.0028097 | 0.0028098 | 0.0028098 | 0.0028099 | 0.0028099 | 0.00281 | 0.00281 | 0.0028101 |  | 0% | 0% | 0% | 83364 | [7 empty] | 8.6165 | -8.6137
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 549 | ULLAPOOL | 33/11 | 1 x 2.5 |  | 2019-02-05 | 2.33 | 1 | 0 | 0 | 2.33 | 2.33 | 2.3301 | 2.3301 | 2.3302 | 2.3302 | 2.3303 | 2.3303 | 2.3303 | 2.3304 | 2.3304 | 2.3305 | 2.3305 | 2.3306 |  | 0% | 0% | 21.46% | 83324 | [7 empty] | 2.5079 | -0.17789
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
HARRIS | 647 |  | 132/33 | 1 x 60 |  |  | 1.44 | 1 |  | Diverse | 1.44 | 1.4456 | 1.4512 | 1.4569 | 1.4626 | 1.4684 | 1.4741 | 1.4799 | 1.4858 | 1.4916 | 1.4975 | 1.5034 | 1.5094 | 1.5154 | Diversity/Losses: 1.84 | 0% | 0% | 0% | 85652
[10 empty] | Aggregate | 2.65 | 2.6603 | 2.6707 | 2.6811 | 2.6916 | 2.7022 | 2.7128 | 2.7235 | 2.7342 | 2.745 | 2.7558 | 2.7667 | 2.7777 | 2.7887 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 1.4285 | 1.434 | 1.4396 | 1.4453 | 1.4509 | 1.4566 | 1.4623 | 1.4681 | 1.4739 | 1.4797 | 1.4855 | 1.4914 | 1.4973 | 1.5033
| 658 | STOCKINISH | 33/11 | 1 x 1 |  | 2018-04-01 | 0.79 | 1 | 0 | 0 | 0.79 | 0.79001 | 0.79003 | 0.79004 | 0.79006 | 0.79007 | 0.79009 | 0.7901 | 0.79012 | 0.79013 | 0.79014 | 0.79016 | 0.79017 | 0.79019 |  | 0% | 0% | 0% | 85637 | [7 empty] | 0.75947 | 0.030534
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 662 | TARBERT | 33/11 | 2 x 2.5 |  | 2019-02-28 | 1.86 | 1 | L | L | 1.86 | 1.8703 | 1.8807 | 1.8911 | 1.9016 | 1.9121 | 1.9227 | 1.9334 | 1.9441 | 1.9549 | 1.9657 | 1.9766 | 1.9875 | 1.9985 |  | 0% | 0% | 18.28% | 85639 | [7 empty] | 1.7109 | 0.14911
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.34 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
INVERNESS | 725 |  | 132/33 | 2 x 60 |  |  | 63.2 | 1 |  | Diverse | 63.2 | 63.2012 | 63.2023 | 63.2035 | 63.2046 | 63.2058 | 63.2069 | 63.2081 | 63.2092 | 63.2104 | 63.2115 | 63.2127 | 63.2138 | 63.215 | Diversity/Losses: 1.062 | 0% | 0% | 32.75% | 15130
|  |  |  | 1 x 90 | [5 empty] | Aggregate | 67.0937 | 67.0949 | 67.0961 | 67.0973 | 67.0986 | 67.0998 | 67.101 | 67.1022 | 67.1035 | 67.1047 | 67.1059 | 67.1071 | 67.1084 | 67.1096 |  |  |  | 20.7 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 62.6944 | 62.6955 | 62.6967 | 62.6978 | 62.699 | 62.7001 | 62.7013 | 62.7024 | 62.7036 | 62.7047 | 62.7058 | 62.707 | 62.7081 | 62.7093
| 712 | CULLODEN | 33/11 | 2 x 15 |  | 2019-01-31 | 9.34 | 1 | 0 | 0 | 9.34 | 9.3402 | 9.3403 | 9.3405 | 9.3407 | 9.3409 | 9.341 | 9.3412 | 9.3414 | 9.3415 | 9.3417 | 9.3419 | 9.342 | 9.3422 |  | 0% | 0% | 12.42% | 83504 | [7 empty] | 9.845 | -0.505
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.16 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 713 | DALNEIGH | 33/11 | 1 x 24 |  | 2019-01-31 | 8.88 | 1 | 0 | 0 | 8.88 | 8.8802 | 8.8803 | 8.8805 | 8.8806 | 8.8808 | 8.881 | 8.8811 | 8.8813 | 8.8815 | 8.8816 | 8.8818 | 8.8819 | 8.8821 |  | 0% | 0% | 24.21% | 83517 | [7 empty] | 9.311 | -0.431
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.15 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 761 | ERROGIE | 33/11 | 1 x 1.5 |  |  | 0.19947 | 1 | 0 | 0 | 0.19947 | 0.19947 | 0.19948 | 0.19948 | 0.19948 | 0.19949 | 0.19949 | 0.19949 | 0.1995 | 0.1995 | 0.1995 | 0.19951 | 0.19951 | 0.19952 |  | 0% | 0% | 0% | 83532 | [7 empty] | 0.2 | -0.00053201
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 718 | FOYERS | 33/11 | 1 x 2.5 |  | 2019-01-02 | 0.36 | 1 | 0 | 0 | 0.36 | 0.36001 | 0.36001 | 0.36002 | 0.36003 | 0.36003 | 0.36004 | 0.36005 | 0.36005 | 0.36006 | 0.36007 | 0.36007 | 0.36008 | 0.36009 |  | 0% | 0% | 16.67% | 83535 | [7 empty] | 0.38835 | -0.028346
[6 empty] | 10:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.06 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 750 | HILTON | 33/11 | 2 x 24 |  | 2018-12-05 | 11.11 | 1 | 0 | 0 | 11.11 | 11.1102 | 11.1104 | 11.1106 | 11.1108 | 11.111 | 11.1112 | 11.1114 | 11.1116 | 11.1118 | 11.112 | 11.1122 | 11.1124 | 11.1126 |  | 0% | 0% | 22.32% | 83513 | [7 empty] | 11.1998 | -0.089834
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.48 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 757 | INVERARNIE | 33/11 | 1 x 2.5 |  | 2018-05-30 | 0.63 | 1 | 0 | 0 | 0.63 | 0.63001 | 0.63002 | 0.63003 | 0.63005 | 0.63006 | 0.63007 | 0.63008 | 0.63009 | 0.6301 | 0.63012 | 0.63013 | 0.63014 | 0.63015 |  | 0% | 0% | 0% | 83528 | [7 empty] | 0.84996 | -0.21996
[6 empty] | 8:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 726 | INVERNESS 11 kV | 33/11 | 2 x 10 |  | 2018-12-05 | 7.32 | 1 | 0 | 0 | 7.32 | 7.3201 | 7.3203 | 7.3204 | 7.3205 | 7.3207 | 7.3208 | 7.3209 | 7.3211 | 7.3212 | 7.3213 | 7.3215 | 7.3216 | 7.3217 |  | 0% | 0% | 27.32% | 83523 | [7 empty] | 7.3038 | 0.01615
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 735 | RAIGMORE | 33/11 | 2 x 24 |  | 2019-01-24 | 14.6977 | 1 | 0 | 0 | 14.6977 | 14.6979 | 14.6982 | 14.6985 | 14.6987 | 14.699 | 14.6993 | 14.6996 | 14.6998 | 14.7001 | 14.7004 | 14.7006 | 14.7009 | 14.7012 |  | 0% | 0% | 29.94% | 83508 | [7 empty] | 15.84 | -1.1423
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4.3999 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 741 | WATERLOO PLACE | 33/11 | 2 x 23 |  | 2019-01-31 | 14.52 | 1 | 0 | 0 | 14.52 | 14.5203 | 14.5205 | 14.5208 | 14.5211 | 14.5213 | 14.5216 | 14.5219 | 14.5221 | 14.5224 | 14.5227 | 14.5229 | 14.5232 | 14.5234 |  | 0% | 0% | 24.59% | 83519 | [7 empty] | 15.4639 | -0.94393
| ` |  |  |  |  | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.57 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 763 | DUNMAGLASS | 33/11 | 1 x 0.8 |  |  | 0.036522 | 1 | 0 | 0 | 0.036522 | 0.036523 | 0.036524 | 0.036524 | 0.036525 | 0.036526 | 0.036526 | 0.036527 | 0.036528 | 0.036528 | 0.036529 | 0.03653 | 0.03653 | 0.036531 |  | 0% | 0% | 0% | 83530 | [7 empty] | 0.08 | -0.043478
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
KEITH | 463 |  | 132/33 | 2 x 90 |  |  | 50.5 | 1 |  | Diverse | 50.5 | 50.5548 | 50.6099 | 50.6653 | 50.721 | 50.777 | 50.8333 | 50.8899 | 50.9468 | 51.004 | 51.0616 | 51.1194 | 51.1776 | 51.2361 | Diversity/Losses: 0.977 | 0% | 0% | 26.34%
|  |  |  | 2 x 90 | [5 empty] | Aggregate | 49.3529 | 49.4064 | 49.4603 | 49.5144 | 49.5688 | 49.6236 | 49.6786 | 49.7339 | 49.7895 | 49.8455 | 49.9017 | 49.9583 | 50.0151 | 50.0723 |  |  |  | 13.3 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 50.096 | 50.1504 | 50.205 | 50.2599 | 50.3152 | 50.3707 | 50.4266 | 50.4828 | 50.5392 | 50.596 | 50.6531 | 50.7105 | 50.7682 | 50.8262
| 460 | ABERLOUR | 33/11 | 2 x 5 |  | 2018-12-05 | 4.56 | 1 | 0 | 0 | 4.56 | 4.5601 | 4.5602 | 4.5602 | 4.5603 | 4.5604 | 4.5605 | 4.5606 | 4.5607 | 4.5607 | 4.5608 | 4.5609 | 4.561 | 4.5611 |  | 0% | 0% | 23.68% | 83612 | [7 empty] | 5.3524 | -0.79238
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.08 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 462 | BUCKIE | 33/11 | 2 x 24 |  | 2018-11-27 | 10.46 | 1 | 0 | 0 | 10.46 | 10.4602 | 10.4604 | 10.4606 | 10.4608 | 10.461 | 10.4611 | 10.4613 | 10.4615 | 10.4617 | 10.4619 | 10.4621 | 10.4623 | 10.4625 |  | 0% | 0% | 22.47% | 83645 | [7 empty] | 11.19 | -0.73
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.35 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 469 | CULLEN | 33/11 | 1 x 15 |  | 2018-12-10 | 2.4 | 1 | 0 | 0 | 2.4 | 2.4 | 2.4001 | 2.4001 | 2.4002 | 2.4002 | 2.4003 | 2.4003 | 2.4004 | 2.4004 | 2.4004 | 2.4005 | 2.4005 | 2.4006 |  | 0% | 0% | 3.333% | 83641 | [7 empty] | 2.446 | -0.046
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.08 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 461 | DUFFTOWN | 33/11 | 2 x 5 |  | 2019-01-29 | 4.72 | 1 | 0 | 0 | 4.72 | 4.7201 | 4.7202 | 4.7203 | 4.7203 | 4.7204 | 4.7205 | 4.7206 | 4.7207 | 4.7208 | 4.7209 | 4.7209 | 4.721 | 4.7211 |  | 0% | 0% | 23.31% | 83618 | [7 empty] | 5.1755 | -0.45546
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 869 | HUNTLY | 33/11 | 2 x 15 |  | 2019-01-31 | 5.97 | 1 | 0 | 0 | 5.97 | 5.9701 | 5.9702 | 5.9703 | 5.9704 | 5.9705 | 5.9707 | 5.9708 | 5.9709 | 5.971 | 5.9711 | 5.9712 | 5.9713 | 5.9714 |  | 0% | 0% | 12.23% | 83625 | [7 empty] | 6.1889 | -0.21891
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.73 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 871 | INSCH | 33/11 | 2 x 7 |  | 2019-01-31 | 6.23 | 1 | 0 | 0 | 6.23 | 6.2301 | 6.2302 | 6.2303 | 6.2305 | 6.2306 | 6.2307 | 6.2308 | 6.2309 | 6.231 | 6.2311 | 6.2313 | 6.2314 | 6.2315 |  | 0% | 0% | 5.297% | 83630 | [7 empty] | 6.4555 | -0.22547
[6 empty] | 20:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.33 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 464 | KEITH | 33/11 | 2 x 15 |  | 2018-12-10 | 6.74 | 1 | L | L | 6.74 | 6.7774 | 6.8149 | 6.8527 | 6.8907 | 6.9288 | 6.9672 | 7.0058 | 7.0447 | 7.0837 | 7.123 | 7.1624 | 7.2021 | 7.242 |  | 0% | 0% | 9.347% | 83602 | [7 empty] | 6.75 | -0.01
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.63 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 465 | LIMEHILLOCKS | 33/11 | 1 x 2.5 |  | 2018-10-30 | 1.39 | 1 | 0 | 0 | 1.39 | 1.39 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3903 | 1.3903 | 1.3903 | 1.3903 |  | 0% | 0% | 2.878% | 83651 | [7 empty] | 1.44 | -0.05
[6 empty] | 19:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.04 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 401 | MARNOCH | 33/11 | 1 x 5 |  | 2019-02-03 | 2.7909 | 1 | L | L | 2.7909 | 2.8063 | 2.8219 | 2.8375 | 2.8532 | 2.869 | 2.8849 | 2.9009 | 2.917 | 2.9332 | 2.9494 | 2.9658 | 2.9822 | 2.9987 |  | 0% | 0% | 13.85% | 83653 | [7 empty] | 3.8121 | -1.0212
|  |  |  | 1 x 6 |  | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.38655 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 459 | ROTHES | 33/11 | 2 x 5 |  | 2019-01-24 | 4.092 | 1 | 0 | 0 | 4.092 | 4.0921 | 4.0922 | 4.0923 | 4.0923 | 4.0924 | 4.0925 | 4.0926 | 4.0926 | 4.0927 | 4.0928 | 4.0929 | 4.0929 | 4.093 |  | 0% | 0% | 35.53% | 83605 | [7 empty] | 4.5782 | -0.48614
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.454 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
KILLIN | 214 |  | 132/33 | 2 x 45 |  |  | 4 | 1 |  | Diverse | 4 | 4.076 | 4.1538 | 4.2334 | 4.3148 | 4.3982 | 4.4835 | 4.5708 | 4.6602 | 4.7516 | 4.8453 | 4.9411 | 5.0392 | 5.1396 | Diversity/Losses: 0.816 | 0% | 0% | 6% | 15630
[10 empty] | Aggregate | 3.263 | 3.325 | 3.3885 | 3.4534 | 3.5198 | 3.5878 | 3.6574 | 3.7287 | 3.8016 | 3.8762 | 3.9525 | 4.0307 | 4.1107 | 4.1926 |  |  |  | 0.24 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 3.968 | 4.0434 | 4.1206 | 4.1995 | 4.2803 | 4.363 | 4.4476 | 4.5343 | 4.6229 | 4.7136 | 4.8065 | 4.9016 | 4.9989 | 5.0985
| 269 | CASHLIE | 33/11 | 1 x 1 |  |  | 0.20509 | 1 | 0 | 0 | 0.20509 | 0.20509 | 0.20509 | 0.2051 | 0.2051 | 0.20511 | 0.20511 | 0.20511 | 0.20512 | 0.20512 | 0.20512 | 0.20513 | 0.20513 | 0.20514 |  | 0% | 0% | 0% | 83724 | [7 empty] | 0.33 | -0.12491
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 140 | CHAORACH | 33/11 | 1 x 4 |  | 2018-12-16 | 0.12826 | 1 | ? | 0 | 0.12826 | 0.12826 | 0.12827 | 0.12827 | 0.12827 | 0.12827 | 0.12828 | 0.12828 | 0.12828 | 0.12828 | 0.12829 | 0.12829 | 0.12829 | 0.12829 |  | 0% | 0% | 0.00199% | 83751 | [7 empty] | 0.1 | 0.028262
[6 empty] | 12:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.5523e-06 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 219 | KILLIN TOWN | 33/11 | 1 x 2.5 |  | 2019-02-01 | 1.21 | 1 | M | M | 1.21 | 1.2265 | 1.2431 | 1.2601 | 1.2772 | 1.2946 | 1.3122 | 1.33 | 1.3481 | 1.3665 | 1.3851 | 1.4039 | 1.423 | 1.4424 |  | 0% | 0% | 5.785% | 83715 | [7 empty] | 1.26 | -0.05
[6 empty] | 3:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.07 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 221 | LUBNAIG | 33/11 | 1 x 0.2 |  |  | 0.019666 | 1 | 0 | 0 | 0.019666 | 0.019666 | 0.019667 | 0.019667 | 0.019667 | 0.019668 | 0.019668 | 0.019668 | 0.019669 | 0.019669 | 0.019669 | 0.01967 | 0.01967 | 0.019671 |  | 0% | 0% | 0% | 83706 | [7 empty] | 0.03 | -0.010334
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 217 | LOCHEARNHEAD | 33/11 | 1 x 4 |  | 2018-09-21 | 1.7 | 1 | H | H | 1.7 | 1.7455 | 1.7923 | 1.8403 | 1.8896 | 1.9402 | 1.9922 | 2.0456 | 2.1004 | 2.1566 | 2.2144 | 2.2737 | 2.3346 | 2.3972 |  | 0% | 0% | 0% | 83712 | [7 empty] | 1.66 | 0.04
[6 empty] | 2:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
KINLOCHLEVEN | 729 |  | 132/33 | 1 x 45 |  |  | 3.4 | 1 |  | Diverse | 3.4 | 3.4001 | 3.4001 | 3.4002 | 3.4002 | 3.4003 | 3.4004 | 3.4004 | 3.4005 | 3.4006 | 3.4006 | 3.4007 | 3.4007 | 3.4008 | Diversity/Losses: 1.006 | 0% | 0% | 35.29% | 21630
[10 empty] | Aggregate | 3.42 | 3.4201 | 3.4201 | 3.4202 | 3.4202 | 3.4203 | 3.4204 | 3.4204 | 3.4205 | 3.4206 | 3.4206 | 3.4207 | 3.4207 | 3.4208 |  |  |  | 1.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 3.3728 | 3.3729 | 3.3729 | 3.373 | 3.373 | 3.3731 | 3.3732 | 3.3732 | 3.3733 | 3.3734 | 3.3734 | 3.3735 | 3.3735 | 3.3736
| 330 | GLENCOE | 33/11 | 1 x 6.9 |  | 2019-02-02 | 2.11 | 1 | 0 | 0 | 2.11 | 2.11 | 2.1101 | 2.1101 | 2.1102 | 2.1102 | 2.1102 | 2.1103 | 2.1103 | 2.1103 | 2.1104 | 2.1104 | 2.1105 | 2.1105 |  | 0% | 0% | 25.59% | 86607 | [7 empty] | 2.0774 | 0.032594
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.54 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 729 | KINLOCHLEVEN | 33/11 | 2 x 2.5 |  | 2019-02-01 | 1.31 | 1 | 0 | 0 | 1.31 | 1.31 | 1.31 | 1.3101 | 1.3101 | 1.3101 | 1.3101 | 1.3102 | 1.3102 | 1.3102 | 1.3102 | 1.3103 | 1.3103 | 1.3103 |  | 0% | 0% | 19.85% | 86601 | 86602 | [6 empty] | 1.46 | -0.15
[6 empty] | 3:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.26 | 66.6% | 33.3% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
KINTORE | 887 |  | 132/33 | 2 x 60 |  |  | 67.2 | 1 |  | Diverse | 67.2 | 67.6361 | 67.6513 | 67.6665 | 67.6818 | 67.6972 | 67.7127 | 67.7282 | 67.7439 | 67.7596 | 67.7754 | 67.7912 | 67.8072 | 67.8232 | Diversity/Losses: 0.944 | 0% | 0% | 23.21% | 15830
|  |  |  | 1 x 90 | [5 empty] | Aggregate | 63.4599 | 63.8718 | 63.8861 | 63.9005 | 63.915 | 63.9295 | 63.9441 | 63.9588 | 63.9735 | 63.9884 | 64.0033 | 64.0183 | 64.0333 | 64.0485 |  |  |  | 15.6 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 66.6624 | 67.0951 | 67.1101 | 67.1252 | 67.1404 | 67.1556 | 67.171 | 67.1864 | 67.2019 | 67.2175 | 67.2331 | 67.2489 | 67.2647 | 67.2806
| 810 | BANCHORY | 33/11 | 2 x 14 |  | 2019-01-24 | 9.44 | 1 | 0 | 0 | 9.44 | 9.4402 | 9.4403 | 9.4405 | 9.4407 | 9.4409 | 9.441 | 9.4412 | 9.4414 | 9.4416 | 9.4417 | 9.4419 | 9.4421 | 9.4422 |  | 0% | 0% | 25.11% | 83818 | [7 empty] | 10.648 | -1.208
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.37 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 856 | FYVIE | 33/11 | 1 x 6 |  | 2019-02-03 | 3.9 | 1 | 0 | 0 | 3.9 | 3.9001 | 3.9001 | 3.9002 | 3.9003 | 3.9004 | 3.9004 | 3.9005 | 3.9006 | 3.9006 | 3.9007 | 3.9008 | 3.9009 | 3.9009 |  | 0% | 0% | 11.79% | 83852 | [7 empty] | 3.9736 | -0.073639
|  |  |  | 1 x 8 |  | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.46 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 875 | INVERURIE | 33/11 | 2 x 15 |  | 2018-12-05 | 13.77 | 1 | 0 | 0 | 13.77 | 13.7703 | 13.7705 | 13.7708 | 13.771 | 13.7713 | 13.7715 | 13.7718 | 13.772 | 13.7723 | 13.7725 | 13.7728 | 13.773 | 13.7733 |  | 0% | 0% | 17.57% | 83837 | [7 empty] | 14.0183 | -0.24827
|  |  |  | 1 x 17 |  | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.42 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 881 | KEMNAY | 33/11 | 2 x 15 |  | 2018-12-25 | 2.12 | 1 | 0 | 0 | 2.12 | 2.12 | 2.1201 | 2.1201 | 2.1202 | 2.1202 | 2.1202 | 2.1203 | 2.1203 | 2.1203 | 2.1204 | 2.1204 | 2.1205 | 2.1205 |  | 0% | 0% | 19.34% | 83830 | [7 empty] | 2.33 | -0.21
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.41 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 903 | METHLICK | 33/11 | 1 x 5 |  | 2019-01-31 | 1.907 | 1 | 0 | 0 | 1.907 | 2.3047 | 2.3047 | 2.3048 | 2.3048 | 2.3048 | 2.3049 | 2.3049 | 2.3049 | 2.305 | 2.305 | 2.305 | 2.3051 | 2.3051 |  | 0% | 0% | 11.88% | 83849 | [7 empty] | 2.69 | -0.78297
|  |  |  | 1 x 6.3 |  | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections:; Average Cold Spell (ACS) (MVA) 2019/20: 0.425 |  |  |  | 0.22649 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 907 | MIDMAR | 33/11 | 1 x 5 |  | 2019-01-31 | 2.5991 | 1 | 0 | 0 | 2.5991 | 2.5991 | 2.5992 | 2.5992 | 2.5993 | 2.5993 | 2.5994 | 2.5994 | 2.5994 | 2.5995 | 2.5995 | 2.5996 | 2.5996 | 2.5997 |  | 0% | 0% | 0.2054% | 83825 | [7 empty] | 2.7045 | -0.10548
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.0053374 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 921 | OLDMELDRUM | 33/11 | 2 x 8 |  | 2018-12-05 | 4.516 | 1 | 0 | 0 | 4.516 | 4.5161 | 4.5162 | 4.5163 | 4.5164 | 4.5164 | 4.5165 | 4.5166 | 4.5167 | 4.5168 | 4.5169 | 4.5169 | 4.517 | 4.5171 |  | 0% | 0% | 3.629% | 83845 | [7 empty] | 4.4956 | 0.020397
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.1639 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 923 | PARK | 33/11 | 1 x 6 |  | 2019-01-17 | 2.3678 | 1 | L | L | 2.3678 | 2.3809 | 2.3941 | 2.4074 | 2.4207 | 2.4342 | 2.4476 | 2.4612 | 2.4748 | 2.4886 | 2.5024 | 2.5162 | 2.5302 | 2.5442 |  | 0% | 0% | 20.95% | 85103 | [7 empty] | 2.42 | -0.052188
[6 empty] | 8:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.496 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 941 | SKENE | 33/11 | 2 x 30 |  | 2019-01-31 | 13.77 | 1 | 0 | 0 | 13.77 | 13.7703 | 13.7705 | 13.7708 | 13.771 | 13.7713 | 13.7715 | 13.7718 | 13.772 | 13.7723 | 13.7725 | 13.7728 | 13.773 | 13.7733 |  | 0% | 0% | 23.46% | 83836 | [7 empty] | 13.58 | 0.19
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.23 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 962 | TORRYBURN | 33/11 | 2 x 24 |  | 2018-12-10 | 9.07 | 1 | 0 | 0 | 9.07 | 9.0702 | 9.0703 | 9.0705 | 9.0707 | 9.0708 | 9.071 | 9.0712 | 9.0713 | 9.0715 | 9.0717 | 9.0718 | 9.072 | 9.0722 |  | 0% | 0% | 21.06% | 83801 | 83807 | [6 empty] | 9.4835 | -0.41355
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.91 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
LAIRG | 534 |  | 132/33 | 1 x 90 |  |  | 1.9 | 1 |  | Diverse | 1.9 | 1.9 | 1.9001 | 1.9001 | 1.9001 | 1.9002 | 1.9002 | 1.9002 | 1.9003 | 1.9003 | 1.9003 | 1.9004 | 1.9004 | 1.9005 | Diversity/Losses: 0.964 | 0% | 0% | 26.32% | 16230
[10 empty] | Aggregate | 1.8324 | 1.8324 | 1.8324 | 1.8325 | 1.8325 | 1.8325 | 1.8326 | 1.8326 | 1.8326 | 1.8327 | 1.8327 | 1.8327 | 1.8328 | 1.8328 |  |  |  | 0.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 1.8848 | 1.8848 | 1.8849 | 1.8849 | 1.8849 | 1.885 | 1.885 | 1.885 | 1.8851 | 1.8851 | 1.8851 | 1.8852 | 1.8852 | 1.8852
| 534 | LAIRG | 33/11 | 1 x 2.5 |  | 2019-02-03 | 1.13 | 1 | ? | 0 | 1.13 | 1.13 | 1.13 | 1.1301 | 1.1301 | 1.1301 | 1.1301 | 1.1301 | 1.1302 | 1.1302 | 1.1302 | 1.1302 | 1.1302 | 1.1303 |  | 0% | 0% | 15.04% | 83909
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.17 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 540 | TORBOLL | 33/11 | 1 x 0.1 |  |  | 0.016856 | 1 | 0 | 0 | 0.016856 | 0.016857 | 0.016857 | 0.016857 | 0.016858 | 0.016858 | 0.016858 | 0.016859 | 0.016859 | 0.016859 | 0.01686 | 0.01686 | 0.01686 | 0.01686 |  | 0% | 0% | 0% | 83902 | [7 empty] | 0.02 | -0.0031436
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 548 | NORTH HOY 33KV TRANSFORMER | 33/11 | 1 x 0.5 |  |  | 0.6855 | 1 | 0 | 0 | 0.6855 | 0.68551 | 0.68552 | 0.68553 | 0.68555 | 0.68556 | 0.68557 | 0.68558 | 0.6856 | 0.68561 | 0.68562 | 0.68563 | 0.68565 | 0.68566 |  | 0% | 0% | 0% | 83905 | [7 empty] | 0.71 | -0.024504
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
LOCH CARNAN | 665 |  | 33 |  |  |  | 6.87 | 1 |  | Diverse | 6.87 | 6.8796 | 6.8892 | 6.8989 | 6.9087 | 6.9185 | 6.9283 | 6.9382 | 6.9482 | 6.9582 | 6.9683 | 6.9784 | 6.9886 | 6.9988 | Diversity/Losses: 1.261 | 0% | 0% | 0% | 84001
[10 empty] | Aggregate | 8.6622 | 8.6743 | 8.6865 | 8.6987 | 8.711 | 8.7233 | 8.7358 | 8.7483 | 8.7608 | 8.7734 | 8.7861 | 8.7989 | 8.8117 | 8.8247 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 6.815 | 6.8246 | 6.8341 | 6.8437 | 6.8534 | 6.8631 | 6.8729 | 6.8827 | 6.8926 | 6.9025 | 6.9125 | 6.9226 | 6.9327 | 6.9428
| 671 | AIRD | 33/11 | 2 x 8 |  | 2019-01-29 | 2.58 | 1 | 0 | 0 | 2.58 | 2.58 | 2.5801 | 2.5801 | 2.5802 | 2.5802 | 2.5803 | 2.5803 | 2.5804 | 2.5804 | 2.5805 | 2.5805 | 2.5806 | 2.5806 |  | 0% | 0% | 27.13% | 84009 | 84010 | [6 empty] | 2.92 | -0.34
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.7 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 653 | CLACHAN | 33/11 | 1 x 2.5 |  | 2019-01-22 | 2.16 | 1 | L | L | 2.16 | 2.172 | 2.184 | 2.1961 | 2.2083 | 2.2205 | 2.2328 | 2.2452 | 2.2576 | 2.2702 | 2.2827 | 2.2954 | 2.3081 | 2.3209 |  | 0% | 0% | 25.46% | 84013 | [7 empty] | 1.98 | 0.18
[6 empty] | 19:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.55 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 644 | DRIMORE | 33/11 | 1 x 2.5 |  | 2019-01-30 | 1.07 | 1 | 0 | 0 | 1.07 | 1.07 | 1.07 | 1.0701 | 1.0701 | 1.0701 | 1.0701 | 1.0701 | 1.0702 | 1.0702 | 1.0702 | 1.0702 | 1.0702 | 1.0703 |  | 0% | 0% | 4.673% | 84005 | [7 empty] | 1.0977 | -0.027675
[6 empty] | 21:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 665 | LOCH CARNAN | 33/11 | 3 x 6.5 |  |  | 0.50288 | 1 | 0 | 0 | 0.50288 | 0.50289 | 0.5029 | 0.50291 | 0.50292 | 0.50293 | 0.50294 | 0.50295 | 0.50296 | 0.50297 | 0.50298 | 0.50299 | 0.50299 | 0.503 |  | 0% | 0% | 0% | 84018 | [7 empty] | 0.51 | -0.0071159
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 660 | POLLACHAR | 33/11 | 2 x 3.9 |  | 2019-01-21 | 2.3493 | 1 | 0 | 0 | 2.3493 | 2.3494 | 2.3494 | 2.3495 | 2.3495 | 2.3496 | 2.3496 | 2.3496 | 2.3497 | 2.3497 | 2.3498 | 2.3498 | 2.3499 | 2.3499 |  | 0% | 0% | 10.74% | 84017 | [7 empty] | 1.9171 | 0.4322
[6 empty] | 12:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.25229 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
LUNANHEAD | 81 |  | 132/33 | 1 x 90 |  |  | 62.2 | 1 |  | Diverse | 62.2 | 62.4246 | 62.6551 | 62.8918 | 63.1348 | 63.3843 | 63.6405 | 63.9034 | 64.1735 | 64.4507 | 64.7353 | 65.0275 | 65.3275 | 65.6355 | Diversity/Losses: 0.528 | 0% | 0% | 13.5% | 17130
|  |  |  | 1 x 120 | [5 empty] | Aggregate | 32.813 | 32.9315 | 33.0531 | 33.178 | 33.3062 | 33.4378 | 33.5729 | 33.7116 | 33.8541 | 34.0003 | 34.1505 | 34.3046 | 34.4629 | 34.6254 |  |  |  | 8.4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 61.7024 | 61.9252 | 62.1539 | 62.3887 | 62.6297 | 62.8772 | 63.1313 | 63.3922 | 63.6601 | 63.9351 | 64.2174 | 64.5073 | 64.8049 | 65.1104
| 89 | FRIOCKHEIM | 33/11 | 1 x 5 |  | 2018-12-05 | 4.403 | 1 | H | H | 4.403 | 4.5209 | 4.642 | 4.7664 | 4.8941 | 5.0252 | 5.1598 | 5.298 | 5.4399 | 5.5856 | 5.7353 | 5.8889 | 6.0467 | 6.2086 |  | 0% | 0% | 12.95% | 84113 | [7 empty] | 4.5724 | -0.16937
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.57 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 87 | INVERARITY | 33/11 | 1 x 2.5 |  | 2019-01-23 | 0.65 | 1 | 0 | 0 | 0.65 | 0.65001 | 0.65002 | 0.65004 | 0.65005 | 0.65006 | 0.65007 | 0.65008 | 0.65009 | 0.65011 | 0.65012 | 0.65013 | 0.65014 | 0.65015 |  | 0% | 0% | 0% | 84112 | [7 empty] | 0.62612 | 0.023878
[6 empty] | 9:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 83 | LOCHSIDE | 33/11 | 2 x 24 |  | 2019-01-29 | 14.24 | 1 | 0 | 0 | 14.24 | 14.2403 | 14.2405 | 14.2408 | 14.241 | 14.2413 | 14.2416 | 14.2418 | 14.2421 | 14.2423 | 14.2426 | 14.2429 | 14.2431 | 14.2434 |  | 0% | 0% | 43.2% | 84105 | [7 empty] | 14.2278 | 0.012181
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 6.152 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 82 | LUNANHEAD | 33/11 | 2 x 15 |  | 2018-12-05 | 7.22 | 1 | 0 | 0 | 7.22 | 7.2201 | 7.2203 | 7.2204 | 7.2205 | 7.2207 | 7.2208 | 7.2209 | 7.2211 | 7.2212 | 7.2213 | 7.2215 | 7.2216 | 7.2217 |  | 0% | 0% | 7.479% | 84101 | [7 empty] | 6.9852 | 0.23479
[6 empty] | 8:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.54 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 84 | MARYTON | 33/11 | 2 x 15 |  | 2019-01-31 | 6.3 | 1 | 0 | 0 | 6.3 | 6.3001 | 6.3002 | 6.3003 | 6.3005 | 6.3006 | 6.3007 | 6.3008 | 6.3009 | 6.301 | 6.3012 | 6.3013 | 6.3014 | 6.3015 |  | 0% | 0% | 14.6% | 84109 | [7 empty] | 6.9818 | -0.68184
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.92 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
LYNDHURST | 11 |  | 132/33 | 2 x 60 |  |  | 25 | 1 |  | Diverse | 25 | 25.0005 | 25.0009 | 25.0014 | 25.0018 | 25.0023 | 25.0027 | 25.0032 | 25.0037 | 25.0041 | 25.0046 | 25.005 | 25.0055 | 25.0059 | Diversity/Losses: 1.011 | 0% | 0% | 27.2% | 17230
[10 empty] | Aggregate | 25.28 | 25.2805 | 25.2809 | 25.2814 | 25.2818 | 25.2823 | 25.2828 | 25.2832 | 25.2837 | 25.2842 | 25.2846 | 25.2851 | 25.2855 | 25.286 |  |  |  | 6.8 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 24.8 | 24.8005 | 24.8009 | 24.8014 | 24.8018 | 24.8023 | 24.8027 | 24.8032 | 24.8036 | 24.8041 | 24.8045 | 24.805 | 24.8054 | 24.8059
| 13 | LOCHEE | 33/11 | 2 x 23 |  | 2018-12-14 | 5.36 | 1 | 0 | 0 | 5.36 | 5.3601 | 5.3602 | 5.3603 | 5.3604 | 5.3605 | 5.3606 | 5.3607 | 5.3608 | 5.3609 | 5.361 | 5.3611 | 5.3612 | 5.3613 |  | 0% | 0% | 25.56% | 84218 | [7 empty] | 5.97 | -0.61
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.37 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 12 | LYNDHURST | 33/11 | 2 x 10 |  | 2019-01-21 | 5.27 | 1 | 0 | 0 | 5.27 | 5.2701 | 5.2702 | 5.2703 | 5.2704 | 5.2705 | 5.2706 | 5.2707 | 5.2708 | 5.2709 | 5.271 | 5.2711 | 5.2712 | 5.2713 |  | 0% | 0% | 27.89% | 84203 | [7 empty] | 5.645 | -0.37495
[6 empty] | 13:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.47 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 14 | MACALPINE ROAD | 33/11 | 1 x 15 & 1 x 21 |  | 2019-01-21 | 7.19 | 1 | 0 | 0 | 7.19 | 7.1901 | 7.1903 | 7.1904 | 7.1905 | 7.1907 | 7.1908 | 7.1909 | 7.1911 | 7.1912 | 7.1913 | 7.1914 | 7.1916 | 7.1917 |  | 0% | 0% | 20.03% | 84207 | [7 empty] | 7.6292 | -0.43922
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.44 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 15 | WEST KIRKTON | 33/11 | 2 x 23 |  | 2019-01-03 | 7.46 | 1 | 0 | 0 | 7.46 | 7.4601 | 7.4603 | 7.4604 | 7.4605 | 7.4607 | 7.4608 | 7.461 | 7.4611 | 7.4612 | 7.4614 | 7.4615 | 7.4616 | 7.4618 |  | 0% | 0% | 24.66% | 84214 | [7 empty] | 9.2362 | -1.7762
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.84 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
MACDUFF | 405 |  | 132/33 | 2 x 90 |  |  | 21.8 | 1 |  | Diverse | 21.8 | 22.1561 | 22.5218 | 22.8972 | 23.2827 | 23.6785 | 24.085 | 24.5023 | 24.9307 | 25.3707 | 25.8224 | 26.2863 | 26.7625 | 27.2515 | Diversity/Losses: 1.177 | 0% | 0% | 16.51% | 17330
[10 empty] | Aggregate | 25.6636 | 26.0828 | 26.5133 | 26.9553 | 27.4091 | 27.8751 | 28.3535 | 28.8448 | 29.3492 | 29.8671 | 30.3989 | 30.9449 | 31.5056 | 32.0813 |  |  |  | 3.6 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 21.6256 | 21.9789 | 22.3416 | 22.714 | 23.0965 | 23.4891 | 23.8923 | 24.3062 | 24.7313 | 25.1677 | 25.6158 | 26.076 | 26.5484 | 27.0335
| 406 | MACDUFF | 33/11 | 2 x 12.5 |  | 2019-01-23 | 13.064 | 1 | H | H | 13.064 | 13.414 | 13.7733 | 14.1422 | 14.5211 | 14.91 | 15.3094 | 15.7195 | 16.1406 | 16.573 | 17.0169 | 17.4728 | 17.9408 | 18.4214 |  | 0% | 0% | 0% | 83207 | [7 empty] | 13.8115 | -0.7475
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 435 | PORTSOY | 33/11 | 1 x 5 |  | 2018-12-05 | 2.5796 | 1 | H | H | 2.5796 | 2.6487 | 2.7196 | 2.7925 | 2.8673 | 2.9441 | 3.023 | 3.1039 | 3.1871 | 3.2725 | 3.3601 | 3.4501 | 3.5426 | 3.6375 |  | 0% | 0% | 8.936% | 83211 | [7 empty] | 2.3238 | 0.25583
[6 empty] | 7:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.2305 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 964 | TURRIFF | 33/11 | 2 x 15 |  | 2018-11-26 | 10.02 | 1 | 0 | 0 | 10.02 | 10.0202 | 10.0204 | 10.0205 | 10.0207 | 10.0209 | 10.0211 | 10.0213 | 10.0215 | 10.0216 | 10.0218 | 10.022 | 10.0222 | 10.0224 |  | 0% | 0% | 0% | 83214 | [7 empty] | 9.3045 | 0.71552
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
MILTON OF CRAIGIE | 51 |  | 132/33 | 2 x 60 |  |  | 47.9 | 1 |  | Diverse | 47.9 | 47.9009 | 47.9017 | 47.9026 | 47.9035 | 47.9044 | 47.9052 | 47.9061 | 47.907 | 47.9079 | 47.9087 | 47.9096 | 47.9105 | 47.9114 | Diversity/Losses: 1.119 | 0% | 0% | 28.39% | 17430
[10 empty] | Aggregate | 53.5939 | 53.5949 | 53.5958 | 53.5968 | 53.5978 | 53.5988 | 53.5998 | 53.6007 | 53.6017 | 53.6027 | 53.6037 | 53.6046 | 53.6056 | 53.6066 |  |  |  | 13.6 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 53.5998: Generation at time of BSP peak:; 53.6007: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 47.5168 | 47.5177 | 47.5185 | 47.5194 | 47.5203 | 47.5211 | 47.522 | 47.5229 | 47.5237 | 47.5246 | 47.5255 | 47.5263 | 47.5272 | 47.5281
| 55 | ASHLUDIE | 33/11 | 2 x 10 |  | 2019-01-27 | 9.12 | 1 | 0 | 0 | 9.12 | 9.1202 | 9.1203 | 9.1205 | 9.1207 | 9.1208 | 9.121 | 9.1212 | 9.1213 | 9.1215 | 9.1217 | 9.1218 | 9.122 | 9.1222 |  | 0% | 0% | 22.37% | 84331 | [7 empty] | 9.8113 | -0.69134
[6 empty] | 17:30 |  |  |  |  | 53.5939: Committed new connections: |  |  |  | 2.04 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 53.5998: Generation at time of peak:; 53.6007: 0
| 56 | BALDOVIE | 33/11 | 2 x 24 |  | 2019-01-22 | 11.98 | 1 | 0 | 0 | 11.98 | 11.9802 | 11.9804 | 11.9807 | 11.9809 | 11.9811 | 11.9813 | 11.9815 | 11.9817 | 11.982 | 11.9822 | 11.9824 | 11.9826 | 11.9828 |  | 0% | 0% | 13.77% | 84318 | [7 empty] | 12.5248 | -0.54479
[6 empty] | 17:30 |  |  |  |  | 53.5939: Committed new connections: |  |  |  | 1.65 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 53.5998: Generation at time of peak:; 53.6007: 0
| 57 | BROUGHTY FERRY | 33/11 | 2 x 10 |  | 2019-02-24 | 7.16 | 1 | 0 | 0 | 7.16 | 7.1601 | 7.1603 | 7.1604 | 7.1605 | 7.1607 | 7.1608 | 7.1609 | 7.161 | 7.1612 | 7.1613 | 7.1614 | 7.1616 | 7.1617 |  | 0% | 0% | 21.79% | 84327 | [7 empty] | 8.53 | -1.37
[6 empty] | 18:00 |  |  |  |  | 53.5939: Committed new connections: |  |  |  | 1.56 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 53.5998: Generation at time of peak:; 53.6007: 0
| 58 | EDZELL STREET | 33/11 | 1 x 10 |  | 2019-01-20 | 2.86 | 1 | 0 | 0 | 2.86 | 2.8601 | 2.8601 | 2.8602 | 2.8602 | 2.8603 | 2.8603 | 2.8604 | 2.8604 | 2.8605 | 2.8605 | 2.8606 | 2.8606 | 2.8607 |  | 0% | 0% | 15.73% | 84322 | [7 empty] | 2.9715 | -0.11149
[6 empty] | 17:00 |  |  |  |  | 53.5939: Committed new connections: |  |  |  | 0.45 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 53.5998: Generation at time of peak:; 53.6007: 0
| 54 | LONGHAUGH | 33/11 | 2 x 23 |  | 2019-01-24 | 8.34 | 1 | 0 | 0 | 8.34 | 8.3402 | 8.3403 | 8.3405 | 8.3406 | 8.3408 | 8.3409 | 8.3411 | 8.3412 | 8.3414 | 8.3415 | 8.3417 | 8.3418 | 8.342 |  | 0% | 0% | 24.7% | 84304 | [7 empty] | 8.8519 | -0.51186
[6 empty] | 17:30 |  |  |  |  | 53.5939: Committed new connections: |  |  |  | 2.06 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 53.5998: Generation at time of peak:; 53.6007: 0
| 52 | MILTON OF CRAIGIE | 33/11 | 1 x 24 |  | 2019-01-30 | 7.8601 | 1 | 0 | 0 | 7.8601 | 7.8602 | 7.8604 | 7.8605 | 7.8607 | 7.8608 | 7.861 | 7.8611 | 7.8612 | 7.8614 | 7.8615 | 7.8617 | 7.8618 | 7.862 |  | 0% | 0% | 21.25% | 84314 | [7 empty] | 8.7792 | -0.91909
|  |  |  | 1 x 15 |  | 12:00 |  |  |  |  | 53.5939: Committed new connections: |  |  |  | 1.67 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 53.5998: Generation at time of peak:; 53.6007: 0
| 53 | OLD CRAIGIE ROAD | 33/11 | 2 x 10 |  | 2019-01-23 | 6.2738 | 1 | 0 | 0 | 6.2738 | 6.2739 | 6.274 | 6.2741 | 6.2742 | 6.2744 | 6.2745 | 6.2746 | 6.2747 | 6.2748 | 6.2749 | 6.275 | 6.2752 | 6.2753 |  | 0% | 0% | 23.14% | 84310 | [7 empty] | 6.263 | 0.010804
[6 empty] | 17:30 |  |  |  |  | 53.5939: Committed new connections: |  |  |  | 1.4516 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 53.5998: Generation at time of peak:; 53.6007: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
MYBSTER | 586 |  | 132/33 | 2 x 120 |  |  | 10.3 | 1 |  | Diverse | 10.3 | 10.3002 | 10.3004 | 10.3006 | 10.3008 | 10.3009 | 10.3011 | 10.3013 | 10.3015 | 10.3017 | 10.3019 | 10.3021 | 10.3023 | 10.3024 | Diversity/Losses: 1.01 | 0% | 0% | 29.13% | 17830
|  |  |  | 2 x 120 | [5 empty] | Aggregate | 10.4 | 10.4002 | 10.4004 | 10.4006 | 10.4008 | 10.4009 | 10.4011 | 10.4013 | 10.4015 | 10.4017 | 10.4019 | 10.4021 | 10.4023 | 10.4025 |  |  |  | 3 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 10.4011: Generation at time of BSP peak:; 10.4013: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 10.2176 | 10.2178 | 10.218 | 10.2182 | 10.2183 | 10.2185 | 10.2187 | 10.2189 | 10.2191 | 10.2193 | 10.2195 | 10.2197 | 10.2198 | 10.22
| 584 | LATHERON | 33/11 | 1 x 4 |  | 2018-12-25 | 1.96 | 1 | 0 | 0 | 1.96 | 1.96 | 1.9601 | 1.9601 | 1.9601 | 1.9602 | 1.9602 | 1.9603 | 1.9603 | 1.9603 | 1.9604 | 1.9604 | 1.9604 | 1.9605 |  | 0% | 0% | 11.22% | 84427 | [7 empty] | 1.81 | 0.15
[6 empty] | 11:00 |  |  |  |  | 10.4: Committed new connections: |  |  |  | 0.22 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.4011: Generation at time of peak:; 10.4013: 0
| 594 | WICK | 33/11 | 2 x 24 |  | 2019-01-08 | 8.44 | 1 | 0 | 0 | 8.44 | 8.4402 | 8.4403 | 8.4405 | 8.4406 | 8.4408 | 8.4409 | 8.4411 | 8.4412 | 8.4414 | 8.4415 | 8.4417 | 8.4418 | 8.442 |  | 0% | 0% | 27.49% | 84401 | [7 empty] | 9.1682 | -0.72824
[6 empty] | 17:00 |  |  |  |  | 10.4: Committed new connections: |  |  |  | 2.32 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 10.4011: Generation at time of peak:; 10.4013: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
NAIRN | 733 |  | 132/33 | 2 x 60 |  |  | 31.3 | 1 |  | Diverse | 31.3 | 31.3761 | 31.4528 | 31.5301 | 31.6079 | 31.6864 | 31.7656 | 31.8453 | 31.9257 | 32.0066 | 32.0883 | 32.1706 | 32.2535 | 32.3371 | Diversity/Losses: 0.977 | 0% | 0% | 28.12%
[10 empty] | Aggregate | 30.58 | 30.6543 | 30.7293 | 30.8048 | 30.8809 | 30.9576 | 31.0348 | 31.1127 | 31.1913 | 31.2704 | 31.3501 | 31.4305 | 31.5116 | 31.5932 |  |  |  | 8.8 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 31.0496 | 31.1251 | 31.2012 | 31.2778 | 31.3551 | 31.433 | 31.5114 | 31.5905 | 31.6702 | 31.7506 | 31.8316 | 31.9132 | 31.9955 | 32.0784
| 779 | ARDERSIER | 33/11 | 2 x 5 |  | 2018-12-17 | 2.2 | 1 | 0 | 0 | 2.2 | 2.2 | 2.2001 | 2.2001 | 2.2002 | 2.2002 | 2.2002 | 2.2003 | 2.2003 | 2.2004 | 2.2004 | 2.2004 | 2.2005 | 2.2005 |  | 0% | 0% | 18.18% | 84526 | [7 empty] | 2.4016 | -0.20157
[6 empty] | 7:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.4 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 752 | DALCROSS | 33/11 | 2 x 15 |  | 2018-05-02 | 7.77 | 1 | 0 | 0 | 7.77 | 7.7701 | 7.7703 | 7.7704 | 7.7706 | 7.7707 | 7.7709 | 7.771 | 7.7711 | 7.7713 | 7.7714 | 7.7716 | 7.7717 | 7.7718 |  | 0% | 0% | 0% | 84530 | [7 empty] | 8.332 | -0.562
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 452 | FORRES | 33/11 | 2 x 15 |  | 2019-01-23 | 9.57 | 1 | L | L | 9.57 | 9.623 | 9.6764 | 9.73 | 9.7839 | 9.8381 | 9.8927 | 9.9475 | 10.0026 | 10.058 | 10.1138 | 10.1698 | 10.2262 | 10.2829 |  | 0% | 0% | 16.3% | 84504 | [7 empty] | 9.2029 | 0.36707
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.56 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 703 | LETHEN | 33/11 | 1 x 2.5 |  | 2018-10-31 | 1.54 | 1 | M | M | 1.54 | 1.561 | 1.5822 | 1.6037 | 1.6255 | 1.6476 | 1.6701 | 1.6928 | 1.7158 | 1.7392 | 1.7628 | 1.7868 | 1.8111 | 1.8358 |  | 0% | 0% | 22.08% | 84502 | [7 empty] | 1.97 | -0.43
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.34 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 723 | NAIRN CENTRAL | 33/11 | 2 x 15 |  | 2019-01-21 | 9.5 | 1 | 0 | 0 | 9.5 | 9.5002 | 9.5003 | 9.5005 | 9.5007 | 9.5009 | 9.501 | 9.5012 | 9.5014 | 9.5016 | 9.5017 | 9.5019 | 9.5021 | 9.5023 |  | 0% | 0% | 23.15% | 84516 | [7 empty] | 9.2982 | 0.20177
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.199 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
PERSLEY | 925 |  | 132/33 | 2 x 90 |  |  | 43.1 | 1 |  | Diverse | 43.1 | 43.1008 | 43.1016 | 43.1024 | 43.1031 | 43.1039 | 43.1047 | 43.1055 | 43.1063 | 43.1071 | 43.1079 | 43.1087 | 43.1094 | 43.1102 | Diversity/Losses: 1.038 | 0% | 0% | 22.97% | 18430
[10 empty] | Aggregate | 44.72 | 44.7208 | 44.7216 | 44.7224 | 44.7233 | 44.7241 | 44.7249 | 44.7257 | 44.7265 | 44.7273 | 44.7282 | 44.729 | 44.7298 | 44.7306 |  |  |  | 9.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 42.7552 | 42.756 | 42.7568 | 42.7575 | 42.7583 | 42.7591 | 42.7599 | 42.7607 | 42.7614 | 42.7622 | 42.763 | 42.7638 | 42.7646 | 42.7653
| 814 | BRIDGE OF DON | 33/11 | 2 x 24 |  | 2019-01-30 | 14.12 | 1 | 0 | 0 | 14.12 | 14.1203 | 14.1205 | 14.1208 | 14.121 | 14.1213 | 14.1215 | 14.1218 | 14.1221 | 14.1223 | 14.1226 | 14.1228 | 14.1231 | 14.1234 |  | 0% | 0% | 25% | 84607 | [7 empty] | 16.68 | -2.56
[6 empty] | 9:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.53 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 865 | HAUDAGAIN | 33/11 | 2 x 23 |  | 2019-01-31 | 5.88 | 1 | 0 | 0 | 5.88 | 5.8801 | 5.8802 | 5.8803 | 5.8804 | 5.8805 | 5.8806 | 5.8808 | 5.8809 | 5.881 | 5.8811 | 5.8812 | 5.8813 | 5.8814 |  | 0% | 0% | 29.59% | 84619 | [7 empty] | 6.8173 | -0.93734
[6 empty] | 19:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.74 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 956 | ST MACHAR | 33/11 | 2 x 24 |  | 2018-11-05 | 7.36 | 1 | 0 | 0 | 7.36 | 7.3601 | 7.3603 | 7.3604 | 7.3605 | 7.3607 | 7.3608 | 7.3609 | 7.3611 | 7.3612 | 7.3613 | 7.3615 | 7.3616 | 7.3617 |  | 0% | 0% | 18.07% | 84603 | [7 empty] | 8.089 | -0.72902
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.33 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 947 | STONEYWOOD T1&T2 | 33/11 | 2 x 24 |  | 2019-01-15 | 10.59 | 1 | 0 | 0 | 10.59 | 10.5902 | 10.5904 | 10.5906 | 10.5908 | 10.591 | 10.5912 | 10.5914 | 10.5915 | 10.5917 | 10.5919 | 10.5921 | 10.5923 | 10.5925 |  | 0% | 0% | 21.62% | 82401 | [7 empty] | 6.7964 | 3.7936
|  | T1 & T2 |  |  |  | 10:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.29 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 982 | WHITESTRIPES | 33/11 | 2 x 15 |  | 2019-01-21 | 6.77 | 1 | 0 | 0 | 6.77 | 6.7701 | 6.7702 | 6.7704 | 6.7705 | 6.7706 | 6.7707 | 6.7709 | 6.771 | 6.7711 | 6.7712 | 6.7714 | 6.7715 | 6.7716 |  | 0% | 0% | 23.63% | 84611 | [7 empty] | 7.0476 | -0.27764
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.6 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
PETERHEAD GRANGE | 927 |  | 132/33 | 2 x 45 |  |  | 24.4 | 1 |  | Diverse | 24.4 | 24.4004 | 24.4009 | 24.4013 | 24.4018 | 24.4022 | 24.4027 | 24.4031 | 24.4036 | 24.404 | 24.4045 | 24.4049 | 24.4053 | 24.4058 | Diversity/Losses: 1.092 | 0% | 0% | 33.2% | 18330
[10 empty] | Aggregate | 26.6474 | 26.6478 | 26.6483 | 26.6488 | 26.6493 | 26.6498 | 26.6503 | 26.6508 | 26.6513 | 26.6517 | 26.6522 | 26.6527 | 26.6532 | 26.6537 |  |  |  | 8.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | 26.6503: Generation at time of BSP peak:; 26.6508: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 24.2048 | 24.2052 | 24.2057 | 24.2061 | 24.2066 | 24.207 | 24.2075 | 24.2079 | 24.2083 | 24.2088 | 24.2092 | 24.2097 | 24.2101 | 24.2105
| 929 | NORTH STREET | 33/11 | 2 x 24 |  | 2018-11-08 | 13.2177 | 1 | 0 | 0 | 13.2177 | 13.2179 | 13.2182 | 13.2184 | 13.2186 | 13.2189 | 13.2191 | 13.2194 | 13.2196 | 13.2198 | 13.2201 | 13.2203 | 13.2206 | 13.2208 |  | 0% | 0% | 0.1676% | 84702
[6 empty] | 16:30 |  |  |  |  | 26.6474: Committed new connections: |  |  |  | 0.022153 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 26.6503: Generation at time of peak:; 26.6508: 0
| 928 | PETERHEAD GRANGE 11kV | 33/11 | 2 x 24 |  | 2019-01-21 | 13.4297 | 1 | 0 | 0 | 13.4297 | 13.4299 | 13.4302 | 13.4304 | 13.4307 | 13.4309 | 13.4312 | 13.4314 | 13.4317 | 13.4319 | 13.4321 | 13.4324 | 13.4326 | 13.4329 |  | 0% | 0% | 28.06% | 84700 | [7 empty] | 13.5466 | -0.1169
[6 empty] | 16:30 |  |  |  |  | 26.6474: Committed new connections: |  |  |  | 3.7684 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | 26.6503: Generation at time of peak:; 26.6508: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
PETERHEAD SHELL | 926 |  | 132/11 | 1 x 15 |  |  | 8.6 | 1 |  | Diverse | 8.6 | 8.6002 | 8.6003 | 8.6005 | 8.6006 | 8.6008 | 8.6009 | 8.6011 | 8.6013 | 8.6014 | 8.6016 | 8.6017 | 8.6019 | 8.602 | Diversity/Losses: 1.005 | 0% | 0% | 25.58% | 21150
[10 empty] | Aggregate | 8.6418 | 8.6419 | 8.6421 | 8.6422 | 8.6424 | 8.6426 | 8.6427 | 8.6429 | 8.643 | 8.6432 | 8.6433 | 8.6435 | 8.6437 | 8.6438 |  |  |  | 2.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 8.5312 | 8.5314 | 8.5315 | 8.5317 | 8.5318 | 8.532 | 8.5321 | 8.5323 | 8.5324 | 8.5326 | 8.5328 | 8.5329 | 8.5331 | 8.5332
| 812 | BODDAM | 33/11 |  |  | 2019-01-30 | 6.18 | 1 | 0 | 0 | 6.18 | 6.1801 | 6.1802 | 6.1803 | 6.1805 | 6.1806 | 6.1807 | 6.1808 | 6.1809 | 6.181 | 6.1811 | 6.1812 | 6.1814 | 6.1815 |  | 0% | 0% | 25.73% | 84801 | [7 empty] | 6.2622 | -0.082241
[6 empty] | 10:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.59 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 926 | PETERHEAD SHELL | 33/11 | 1 x 15 |  | 2019-03-12 | 2.4618 | 1 | 0 | 0 | 2.4618 | 2.4618 | 2.4619 | 2.4619 | 2.4619 | 2.462 | 2.462 | 2.4621 | 2.4621 | 2.4622 | 2.4622 | 2.4623 | 2.4623 | 2.4624 |  | 0% | 0% | 22.97% | 21150 | [7 empty] | 9.7258 | -7.2641
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.56544 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
PORT ANN | 301 |  | 132/33 | 2 x 30 |  |  | 21.5 | 1 |  | Diverse | 21.5 | 21.5592 | 21.6191 | 21.6798 | 21.7412 | 21.8035 | 21.8665 | 21.9303 | 21.9949 | 22.0603 | 22.1266 | 22.1937 | 22.2616 | 22.3304 | Diversity/Losses: 0.901 | 0% | 0% | 14.88% | 18530
[10 empty] | Aggregate | 19.3805 | 19.4338 | 19.4878 | 19.5425 | 19.5979 | 19.654 | 19.7108 | 19.7683 | 19.8266 | 19.8855 | 19.9453 | 20.0058 | 20.067 | 20.129 |  |  |  | 3.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 21.328 | 21.3867 | 21.4462 | 21.5064 | 21.5673 | 21.629 | 21.6915 | 21.7548 | 21.8189 | 21.8838 | 21.9495 | 22.0161 | 22.0835 | 22.1518
| 319 | AIRIGH-NA-BRODAIG | 33/11 | 1 x 0.315 |  |  | 0.075854 | 1 | M | M | 0.075854 | 0.076886 | 0.077932 | 0.078992 | 0.080067 | 0.081156 | 0.08226 | 0.08338 | 0.084514 | 0.085664 | 0.086829 | 0.08801 | 0.089208 | 0.090421 |  | 0% | 0% | 0% | 84942 | [7 empty] | 0.15 | -0.074146
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 313 | BOWMORE | 33/11 | 1 x 8 |  | 2018-04-02 | 2.82 | 1 | 0 | 0 | 2.82 | 2.8201 | 2.8201 | 2.8202 | 2.8202 | 2.8203 | 2.8203 | 2.8204 | 2.8204 | 2.8205 | 2.8205 | 2.8206 | 2.8206 | 2.8207 |  | 0% | 0% | 17.73% | 84928 | [7 empty] | 3.2 | -0.38
[6 empty] | 0:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 305 | CRINAN | 33/11 | 1 x 1 |  | 2018-10-10 | 0.73385 | 1 | 0 | 0 | 0.73385 | 0.73386 | 0.73387 | 0.73389 | 0.7339 | 0.73391 | 0.73393 | 0.73394 | 0.73395 | 0.73397 | 0.73398 | 0.734 | 0.73401 | 0.73402 |  | 0% | 0% | 3.765% | 84915 | [7 empty] | 1.06 | -0.32615
[6 empty] | 0:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.027631 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 326 | CROMALT | 33/11 | 1 x 2.5 |  | 2018-12-25 | 0.91 | 1 | ? | 0 | 0.91 | 0.91002 | 0.91003 | 0.91005 | 0.91007 | 0.91008 | 0.9101 | 0.91012 | 0.91013 | 0.91015 | 0.91017 | 0.91018 | 0.9102 | 0.91022 |  | 0% | 0% | 17.58% | 84952 | [7 empty] | 1 | -0.09
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.16 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 309 | INVERNEIL | 33/11 | 1 x 2.5 |  | 2018-11-02 | 1.58 | 1 | L | L | 1.58 | 1.5888 | 1.5976 | 1.6064 | 1.6153 | 1.6243 | 1.6333 | 1.6423 | 1.6514 | 1.6606 | 1.6698 | 1.679 | 1.6883 | 1.6977 |  | 0% | 0% | 0.6329% | 84907 | [7 empty] | 1.1117 | 0.46826
[6 empty] | 4:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.01 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 308 | LOCHGILPHEAD | 33/11 | 2 x 24 |  | 2019-02-01 | 8.91 | 1 | 0 | 0 | 8.91 | 8.9102 | 8.9103 | 8.9105 | 8.9107 | 8.9108 | 8.911 | 8.9111 | 8.9113 | 8.9115 | 8.9116 | 8.9118 | 8.912 | 8.9121 |  | 0% | 0% | 13.92% | 84911 | [7 empty] | 8.39 | 0.52
[6 empty] | 4:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.24 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 339 | LUSSAGIVEN | 33/11 | 1 x 0.1 |  |  | 0.036522 | 1 | 0 | 0 | 0.036522 | 0.036523 | 0.036524 | 0.036524 | 0.036525 | 0.036526 | 0.036526 | 0.036527 | 0.036528 | 0.036528 | 0.036529 | 0.03653 | 0.03653 | 0.036531 |  | 0% | 0% | 0% | 84918 | [7 empty] | 0.04 | -0.0034777
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 334 | PORT ASKAIG | 33/11 | 1 x 2.5 |  | 2019-01-31 | 1.1584 | 1 | 0 | 0 | 1.1584 | 1.1585 | 1.1585 | 1.1585 | 1.1585 | 1.1586 | 1.1586 | 1.1586 | 1.1586 | 1.1586 | 1.1587 | 1.1587 | 1.1587 | 1.1587 |  | 0% | 0% | 28.72% | 84925 | [7 empty] | 1.2269 | -0.068463
[6 empty] | 8:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.3327 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 331 | PORT ELLEN | 33/11 | 1 x 4 |  | 2019-02-04 | 3.0771 | 1 | M | M | 3.0771 | 3.119 | 3.1614 | 3.2045 | 3.248 | 3.2922 | 3.337 | 3.3824 | 3.4284 | 3.4751 | 3.5224 | 3.5703 | 3.6189 | 3.6681 |  | 0% | 0% | 15.24% | 84930 | [7 empty] | 3.2188 | -0.14163
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.46895 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 397 | STONEFIELD | 33/11 | 1 x 0.315 |  |  | 0.053379 | 1 | H | H | 0.053379 | 0.054809 | 0.056277 | 0.057784 | 0.059332 | 0.060922 | 0.062554 | 0.064229 | 0.06595 | 0.067716 | 0.06953 | 0.071393 | 0.073305 | 0.075269 |  | 0% | 0% | 0% | 84955 | [7 empty] | 0.03 | 0.023379
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 341 | TARBERT JURA | 33/11 | 1 x 0.15 |  |  | 0.025285 | 1 | 0 | 0 | 0.025285 | 0.025285 | 0.025286 | 0.025286 | 0.025287 | 0.025287 | 0.025287 | 0.025288 | 0.025288 | 0.025289 | 0.025289 | 0.02529 | 0.02529 | 0.025291 |  | 0% | 0% | 0% | 84921 | [7 empty] | 0.04 | -0.014715
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN |  | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
QUOICH | 748 |  | 132/33 | 1 x 30 |  |  | 0.12 | 1 |  | Diverse | 0.12 | 0.12 | 0.12 | 0.12001 | 0.12001 | 0.12001 | 0.12001 | 0.12002 | 0.12002 | 0.12002 | 0.12002 | 0.12002 | 0.12003 | 0.12003 | Diversity/Losses: 0.999 | 0% | 0% | 58.33% | 18650
[10 empty] | Aggregate | 0.11989 | 0.11989 | 0.11989 | 0.11989 | 0.1199 | 0.1199 | 0.1199 | 0.1199 | 0.1199 | 0.11991 | 0.11991 | 0.11991 | 0.11991 | 0.11992 |  |  |  | 0.07 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 0.11904 | 0.11904 | 0.11904 | 0.11905 | 0.11905 | 0.11905 | 0.11905 | 0.11906 | 0.11906 | 0.11906 | 0.11906 | 0.11906 | 0.11907 | 0.11907
| 748 | QUOICH PRIMARY | 33/11 | 1 x 4 |  | 2018-04-06 | 0.11989 | 1 | ? | 0 | 0.11989 | 0.11989 | 0.11989 | 0.11989 | 0.1199 | 0.1199 | 0.1199 | 0.1199 | 0.1199 | 0.11991 | 0.11991 | 0.11991 | 0.11991 | 0.11992 |  | 0% | 0% | 0% | 82824 | [7 empty] | 0.85 | -0.73011
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
RANNOCH | 261 |  | 132/33 | 2 x 90 |  |  | 2 | 1 |  | Diverse | 2 | 2 | 2.0001 | 2.0001 | 2.0001 | 2.0002 | 2.0002 | 2.0003 | 2.0003 | 2.0003 | 2.0004 | 2.0004 | 2.0004 | 2.0005 | Diversity/Losses: 1.083 | 0% | 0% | 12.5% | 18731
[10 empty] | Aggregate | 2.1651 | 2.1652 | 2.1652 | 2.1652 | 2.1653 | 2.1653 | 2.1654 | 2.1654 | 2.1654 | 2.1655 | 2.1655 | 2.1656 | 2.1656 | 2.1656 |  |  |  | 0.25 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 1.984 | 1.984 | 1.9841 | 1.9841 | 1.9841 | 1.9842 | 1.9842 | 1.9843 | 1.9843 | 1.9843 | 1.9844 | 1.9844 | 1.9844 | 1.9845
| 343 | BLACKMOUNT | 33/11 | 1 x 0.05 |  |  | 0.039332 | 1 | 0 | 0 | 0.039332 | 0.039332 | 0.039333 | 0.039334 | 0.039335 | 0.039335 | 0.039336 | 0.039337 | 0.039337 | 0.039338 | 0.039339 | 0.03934 | 0.03934 | 0.039341 |  | 0% | 0% | 0% | 85007 | [7 empty] | 0.39 | -0.35067
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 274 | BRIDGE OF GAUR | 33/11 | 1 x 0.5 |  |  | 0.3287 | 1 | 0 | 0 | 0.3287 | 0.32871 | 0.32871 | 0.32872 | 0.32872 | 0.32873 | 0.32874 | 0.32874 | 0.32875 | 0.32875 | 0.32876 | 0.32877 | 0.32877 | 0.32878 |  | 0% | 0% | 0% | 85020 | [7 empty] | 0.321 | 0.0077008
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 345 | GLENETIVE | 33/11 | 1 x 0.3 |  |  | 0.087092 | 1 | 0 | 0 | 0.087092 | 0.087093 | 0.087095 | 0.087096 | 0.087098 | 0.0871 | 0.087101 | 0.087103 | 0.087104 | 0.087106 | 0.087108 | 0.087109 | 0.087111 | 0.087112 |  | 0% | 0% | 0% | 85002 | [7 empty] | 0.14 | -0.052908
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 218 | TYNDRUM | 33/11 | 1 x 2.5 |  | 2018-04-02 | 1.71 | 1 | 0 | 0 | 1.71 | 1.71 | 1.7101 | 1.7101 | 1.7101 | 1.7102 | 1.7102 | 1.7102 | 1.7102 | 1.7103 | 1.7103 | 1.7103 | 1.7104 | 1.7104 |  | 0% | 0% | 0% | 85011 | [7 empty] | 1.7449 | -0.034903
[6 empty] | 7:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
REDMOSS | 934 |  | 132/33 | 2 x 60 |  |  | 45.7 | 1 |  | Diverse | 45.7 | 45.7964 | 45.8934 | 45.9909 | 46.089 | 46.1876 | 46.2867 | 46.3864 | 46.4866 | 46.5874 | 46.6887 | 46.7906 | 46.8931 | 46.9961 | Diversity/Losses: 1.072 | 0% | 0% | 26.04% | 18830
[10 empty] | Aggregate | 48.994 | 49.0974 | 49.2014 | 49.3059 | 49.4111 | 49.5168 | 49.623 | 49.7299 | 49.8374 | 49.9454 | 50.054 | 50.1633 | 50.2731 | 50.3836 |  |  |  | 11.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 45.3344 | 45.4301 | 45.5263 | 45.623 | 45.7203 | 45.8181 | 45.9164 | 46.0153 | 46.1147 | 46.2147 | 46.3152 | 46.4163 | 46.5179 | 46.6201
| 832 | CRAIGINCHES | 33/11 | 2 x 30 |  | 2019-02-01 | 12.71 | 1 | 0 | 0 | 12.71 | 12.7102 | 12.7105 | 12.7107 | 12.7109 | 12.7112 | 12.7114 | 12.7116 | 12.7119 | 12.7121 | 12.7123 | 12.7126 | 12.7128 | 12.713 |  | 0% | 0% | 22.66% | 85102 | [7 empty] | 13.31 | -0.6
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.88 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 882 | KINCORTH | 33/11 | 2 x 12.5 |  | 2019-02-08 | 7.4462 | 1 | 0 | 0 | 7.4462 | 7.4463 | 7.4465 | 7.4466 | 7.4467 | 7.4469 | 7.447 | 7.4472 | 7.4473 | 7.4474 | 7.4476 | 7.4477 | 7.4478 | 7.448 |  | 0% | 0% | 27.1% | 85120 | [7 empty] | 9.67 | -2.2238
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.0177 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 915 | NEWTONHILL | 33/11 | 2 x 15 |  | 2019-01-29 | 10.2803 | 1 | 0 | 0 | 10.2803 | 10.2805 | 10.2807 | 10.2809 | 10.2811 | 10.2813 | 10.2814 | 10.2816 | 10.2818 | 10.282 | 10.2822 | 10.2824 | 10.2826 | 10.2828 |  | 0% | 0% | 27.92% | 85107 | [7 empty] | 10.4353 | -0.15494
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.8699 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 935 | REDMOSS | 33/11 | 2 x 40 |  | 2019-01-31 | 18.5575 | 1 | L | L | 18.5575 | 18.6604 | 18.7638 | 18.8678 | 18.9723 | 19.0775 | 19.1832 | 19.2895 | 19.3964 | 19.5039 | 19.612 | 19.7207 | 19.8299 | 19.9398 |  | 0% | 0% | 27.91% | 85117 | [7 empty] | 19.8011 | -1.2436
[6 empty] | 80:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 5.1788 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
SHETLAND |  |  | 33 |  |  |  |  | 1 |  | Diverse | 0 | 43.9922 | 44.1946 | 44.4017 | 44.6137 | 44.8307 | 45.0528 | 45.2801 | 45.5128 | 45.7509 | 45.9947 | 46.2442 | 46.4997 | 46.7612 | #DIV/0! | 0% | 0% | 0%
[10 empty] | Aggregate | 43.7944 | 43.9922 | 44.1946 | 44.4017 | 44.6137 | 44.8307 | 45.0528 | 45.2801 | 45.5128 | 45.7509 | 45.9947 | 46.2442 | 46.4997 | 46.7612 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 0 | 43.6402 | 43.841 | 44.0465 | 44.2568 | 44.4721 | 44.6924 | 44.9179 | 45.1487 | 45.3849 | 45.6267 | 45.8743 | 46.1277 | 46.3871
| 699 | BRAE | 33/11 | 1 x 6 |  | 2019-01-30 | 2.94 | 1 | 0 | 0 | 2.94 | 2.9401 | 2.9401 | 2.9402 | 2.9402 | 2.9403 | 2.9403 | 2.9404 | 2.9404 | 2.9405 | 2.9405 | 2.9406 | 2.9406 | 2.9407 |  | 0% | 0% | 40.82% | 89930 | [7 empty] | 2.88 | 0.06
[6 empty] | 5:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.2 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 692 | FIRTH | 33/11 | 1 x 6 |  | 2018-04-04 | 1.21 | 1 | 0 | 0 | 1.21 | 1.21 | 1.21 | 1.2101 | 1.2101 | 1.2101 | 1.2101 | 1.2102 | 1.2102 | 1.2102 | 1.2102 | 1.2102 | 1.2103 | 1.2103 |  | 0% | 0% | 31.4% | 89941 | [7 empty] | 1.3518 | -0.1418
[6 empty] | 6:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.38 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 696 | GREMISTA (LERWICK) | 33/11 | 3 x 18 |  | 2019-01-25 | 17.19 | 1 | 0 | 0 | 17.19 | 17.1903 | 17.1906 | 17.1909 | 17.1913 | 17.1916 | 17.1919 | 17.1922 | 17.1925 | 17.1928 | 17.1931 | 17.1935 | 17.1938 | 17.1941 |  | 0% | 0% | 24.43% | 89903 | 89904 | 89905 | [5 empty] | 17.8859 | -0.69593
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4.2 | 33.33% | 33.33% | 33.33% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 695 | GUTCHER | 33/11 | 1 x 4 |  | 2019-02-03 | 0.76 | 1 | 0 | 0 | 0.76 | 0.76001 | 0.76003 | 0.76004 | 0.76006 | 0.76007 | 0.76008 | 0.7601 | 0.76011 | 0.76012 | 0.76014 | 0.76015 | 0.76017 | 0.76018 |  | 0% | 0% | 0% | 89951 | [7 empty] | 0.93616 | -0.17616
[6 empty] | 5:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 698 | MID YELL | 33/11 | 1 x 6 |  | 2019-01-23 | 0.85305 | 1 | H | H | 0.85305 | 0.87591 | 0.89937 | 0.92346 | 0.9482 | 0.9736 | 0.99968 | 1.0265 | 1.054 | 1.0822 | 1.1112 | 1.1409 | 1.1715 | 1.2029 |  | 0% | 0% | 10.92% | 89961 | [7 empty] | 0.8529 | 0.00014973
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.093187 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 700 | SCALLOWAY | 33/11 | 1 x 8 |  | 2019-01-17 | 4.12 | 1 | 0 | 0 | 4.12 | 4.1201 | 4.1202 | 4.1202 | 4.1203 | 4.1204 | 4.1205 | 4.1205 | 4.1206 | 4.1207 | 4.1208 | 4.1208 | 4.1209 | 4.121 |  | 0% | 0% | 24.03% | 89972 | [7 empty] | 4.707 | -0.58702
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.99 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 693 | SETTER SANDWICK | 33/11 | 1 x 4 |  | 2019-01-28 | 2.78 | 1 | 0 | 0 | 2.78 | 2.7801 | 2.7801 | 2.7802 | 2.7802 | 2.7803 | 2.7803 | 2.7804 | 2.7804 | 2.7805 | 2.7805 | 2.7806 | 2.7806 | 2.7807 |  | 0% | 0% | 17.63% | 89981
[6 empty] | 7:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.49 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 697 | SUMBURGH | 33/11 | 1 x 4 |  | 2019-01-28 | 1.86 | 1 | 0 | 0 | 1.86 | 1.86 | 1.8601 | 1.8601 | 1.8601 | 1.8602 | 1.8602 | 1.8602 | 1.8603 | 1.8603 | 1.8603 | 1.8604 | 1.8604 | 1.8604 |  | 0% | 0% | 23.66% | 89936
[6 empty] | 7:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.44 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 790 | TUMBLIN | 33/11 | 1 x 6 |  | 2019-02-03 | 2.19 | 1 | 0 | 0 | 2.19 | 2.19 | 2.1901 | 2.1901 | 2.1902 | 2.1902 | 2.1902 | 2.1903 | 2.1903 | 2.1904 | 2.1904 | 2.1904 | 2.1905 | 2.1905 |  | 0% | 0% | 10.96% | 89967
[6 empty] | 5:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.24 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 696A | SHETLAND GAS PLANT | 33kV Customer |  |  | 2018-09-16 | 4.6353 | 1 | H | H | 4.6353 | 4.7595 | 4.887 | 5.0179 | 5.1523 | 5.2903 | 5.432 | 5.5775 | 5.7269 | 5.8803 | 6.0379 | 6.1996 | 6.3657 | 6.5362 |  | 0% | 0% | 0.004232% | 89929
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.00019615 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 791 | UNST | 33/11 | 1 x 4 |  | 2019-02-12 | 1.57 | 1 | 0 | 0 | 1.57 | 1.57 | 1.5701 | 1.5701 | 1.5701 | 1.5701 | 1.5702 | 1.5702 | 1.5702 | 1.5703 | 1.5703 | 1.5703 | 1.5703 | 1.5704 |  | 0% | 0% | 28.03% | 89956 | [7 empty] | 1.6549 | -0.084856
[6 empty] | 5:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.44 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 687 | VOE | 33/11 | 1 x 8 |  | 2018-12-12 | 3.686 | 1 | M | M | 3.686 | 3.7361 | 3.787 | 3.8385 | 3.8907 | 3.9437 | 3.9973 | 4.0517 | 4.1068 | 4.1627 | 4.2193 | 4.2767 | 4.3349 | 4.3939 |  | 0% | 0% | 17.09% | 89992 | [7 empty] | 3.7038 | -0.017756
[6 empty] | 16:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.63 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
SHIN | 545 |  | 132/33 | 2 x 90 |  |  | 2.2 | 1 |  | Diverse | 2.2 | 2.2066 | 2.2133 | 2.2201 | 2.227 | 2.234 | 2.241 | 2.2482 | 2.2555 | 2.2628 | 2.2703 | 2.2779 | 2.2855 | 2.2933 | Diversity/Losses: 0.868 | 0% | 0% | 27.27% | 19130
[10 empty] | Aggregate | 1.91 | 1.9157 | 1.9216 | 1.9275 | 1.9334 | 1.9395 | 1.9456 | 1.9519 | 1.9582 | 1.9646 | 1.971 | 1.9776 | 1.9843 | 1.991 |  |  |  | 0.6 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 2.1824 | 2.189 | 2.1956 | 2.2023 | 2.2092 | 2.2161 | 2.2231 | 2.2302 | 2.2374 | 2.2447 | 2.2521 | 2.2597 | 2.2673 | 2.275
| 523 | GLEDFIELD | 33/11 | 1 x 2.5 |  | 2019-02-03 | 1.49 | 1 | 0 | 0 | 1.49 | 1.49 | 1.4901 | 1.4901 | 1.4901 | 1.4901 | 1.4902 | 1.4902 | 1.4902 | 1.4902 | 1.4903 | 1.4903 | 1.4903 | 1.4904 |  | 0% | 0% | 21.48% | 85407 | [7 empty] | 1.5401 | -0.050067
[6 empty] | 3:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.32 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 536 | SHIN | 33/11 | 1 x 2.5 |  | 2019-02-02 | 0.42 | 1 | M | M | 0.42 | 0.42571 | 0.43151 | 0.43738 | 0.44333 | 0.44936 | 0.45547 | 0.46167 | 0.46795 | 0.47432 | 0.48077 | 0.48731 | 0.49394 | 0.50066 |  | 0% | 0% | 11.9% | 85401 | [7 empty] | 0.39289 | 0.027113
[6 empty] | 20:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
SLOY | 139 |  | 132/11 | 2 x 50 |  |  | 2.9 | 1 |  | Diverse | 2.9 | 2.9001 | 2.9001 | 2.9002 | 2.9002 | 2.9003 | 2.9003 | 2.9004 | 2.9004 | 2.9005 | 2.9005 | 2.9006 | 2.9006 | 2.9007 | Diversity/Losses: 0.594 | 0% | 0% | 0.3448% | 19256 | 19213
[10 empty] | Aggregate | 1.7222 | 1.7222 | 1.7222 | 1.7223 | 1.7223 | 1.7223 | 1.7224 | 1.7224 | 1.7224 | 1.7225 | 1.7225 | 1.7225 | 1.7225 | 1.7226 |  |  |  | 0.01 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 2.8768 | 2.8769 | 2.8769 | 2.877 | 2.877 | 2.8771 | 2.8771 | 2.8772 | 2.8772 | 2.8773 | 2.8773 | 2.8774 | 2.8774 | 2.8775
| 139 | SLOY POWER STATION | 11/11 | 2 x 8 |  |  | 1.7222 | 1 | 0 | 0 | 1.7222 | 1.7222 | 1.7222 | 1.7223 | 1.7223 | 1.7223 | 1.7224 | 1.7224 | 1.7224 | 1.7225 | 1.7225 | 1.7225 | 1.7225 | 1.7226 |  | 0% | 0% | 0% | 85501 | 85500 | [6 empty] | 3.55 | -1.8278
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
ST FERGUS GAS | 955 |  | 132/11 | 2 x 30 |  |  | 11 | 1 |  | Diverse | 11 | 11.2947 | 11.5972 | 11.9079 | 12.2269 | 12.5544 | 12.8907 | 13.236 | 13.5905 | 13.9546 | 14.3284 | 14.7122 | 15.1063 | 15.511 | Diversity/Losses: 0.95 | 0% | 0% | 26.36% | 21350
[10 empty] | Aggregate | 10.45 | 10.7299 | 11.0174 | 11.3125 | 11.6155 | 11.9267 | 12.2461 | 12.5742 | 12.911 | 13.2569 | 13.612 | 13.9766 | 14.351 | 14.7354 |  |  |  | 2.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 10.912 | 11.2043 | 11.5044 | 11.8126 | 12.129 | 12.4539 | 12.7876 | 13.1301 | 13.4818 | 13.843 | 14.2138 | 14.5945 | 14.9855 | 15.3869
| 955 | ST FERGUS Gas Term |  | 2 x 30 |  | 2019-03-02 | 10.45 | 1 | H | H | 10.45 | 10.7299 | 11.0174 | 11.3125 | 11.6155 | 11.9267 | 12.2461 | 12.5742 | 12.911 | 13.2569 | 13.612 | 13.9766 | 14.351 | 14.7354 |  | 0% | 0% | 27.75% | 21350
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
ST FILLANS | 213 |  | 132/11 | 1 x 25 |  |  | 1.9 | 1 |  | Diverse | 1.9 | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Diversity/Losses: 1.035 | 0% | 0% | 26.32% | 85301
[10 empty] | Aggregate | 1.9661 | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | 0.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 1.8848 | #REF! | #REF! | #REF! | #REF! | #REF! | #VALUE! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 212 | DALCHONZIE | 33/11 | 1 x 6 |  | 2019-02-04 | 1.86 | 1 | 0 | 0 | 1.86 | 1.86 | 1.8601 | 1.8601 | 1.8601 | 1.8602 | 1.8602 | 1.8602 | 1.8603 | 1.8603 | 1.8603 | 1.8604 | 1.8604 | 1.8604 |  | 0% | 0% | 39.78% | 85302 | [7 empty] | 1.92 | -0.06
[6 empty] | 12:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.74 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| N/A | ST FILLANS 33/LV | 33 |  |  | 2019-02-03 11:00 | 0.10608 | 1 | #N/A | 0 | 0.10608 | 0.10608 | 0.10608 | 0.10609 | 0.10609 | 0.10609 | 0.10609 | 0.10609 | 0.1061 | 0.1061 | 0.1061 | 0.1061 | 0.1061 | 0.10611 |  | 0% | 0% | 0% | 85305
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
STORNOWAY |  |  | 132/33 | 1 x 30 |  |  | 19.35 | 1 |  | Diverse | 19.35 | 19.3759 | 19.4025 | 19.4298 | 19.4578 | 19.4865 | 19.516 | 19.5462 | 19.5772 | 19.609 | 19.6416 | 19.6751 | 19.7095 | 19.7447 | Diversity/Losses: 1.148 | 0% | 0% | 0% | 85628
[10 empty] | Aggregate | 22.2124 | 22.2421 | 22.2727 | 22.304 | 22.3361 | 22.3691 | 22.4029 | 22.4376 | 22.4732 | 22.5097 | 22.5472 | 22.5856 | 22.625 | 22.6655 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 19.1952 | 19.2209 | 19.2473 | 19.2744 | 19.3022 | 19.3306 | 19.3599 | 19.3898 | 19.4206 | 19.4521 | 19.4845 | 19.5177 | 19.5518 | 19.5867
| 651 | BARVAS | 33/11 | 2 x 2.5 |  | 2018-12-03 | 2.62 | 1 | 0 | 0 | 2.62 | 2.62 | 2.6201 | 2.6201 | 2.6202 | 2.6202 | 2.6203 | 2.6203 | 2.6204 | 2.6204 | 2.6205 | 2.6205 | 2.6206 | 2.6206 |  | 0% | 0% | 13.36% | 85627 | [7 empty] | 2.7951 | -0.17511
[6 empty] | 16:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.35 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 652 | BATTERY POINT | 33/11 | 3 x 8 |  | 2018-10-30 | 12.95 | 1 | 0 | 0 | 12.95 | 12.9502 | 12.9505 | 12.9507 | 12.9509 | 12.9512 | 12.9514 | 12.9517 | 12.9519 | 12.9521 | 12.9524 | 12.9526 | 12.9528 | 12.9531 |  | 0% | 0% | 19.54% | 85622 | [7 empty] | 13.8912 | -0.94117
[6 empty] | 9:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.53 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 670 | CALLANISH | 33/11 | 1 x 4 |  | 2019-03-10 | 1.78 | 1 | 0 | 0 | 1.78 | 1.78 | 1.7801 | 1.7801 | 1.7801 | 1.7802 | 1.7802 | 1.7802 | 1.7803 | 1.7803 | 1.7803 | 1.7804 | 1.7804 | 1.7804 |  | 0% | 0% | 14.04% | 85614 | [7 empty] | 1.85 | -0.07
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.25 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 672 | COLL | 33/11 | 1 x 2.5 |  | 2019-01-10 | 2.03 | 1 | 0 | 0 | 2.03 | 2.03 | 2.0301 | 2.0301 | 2.0301 | 2.0302 | 2.0302 | 2.0303 | 2.0303 | 2.0303 | 2.0304 | 2.0304 | 2.0304 | 2.0305 |  | 0% | 0% | 0.9852% | 85625 | [7 empty] | 2.13 | -0.1
[6 empty] | 10:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.02 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 648 | GISLA | 33/11 | 1 x 1 |  | 2019-01-27 | 1.04 | 1 | H | H | 1.04 | 1.0679 | 1.0965 | 1.1258 | 1.156 | 1.187 | 1.2188 | 1.2514 | 1.2849 | 1.3193 | 1.3547 | 1.391 | 1.4282 | 1.4665 |  | 0% | 0% | 0% | 85617 | [7 empty] | 0.99387 | 0.046134
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 657 | LAXAY | 33/11 | 1 x 2.5 |  | 2019-01-21 | 1.68 | 1 | 0 | 0 | 1.68 | 1.68 | 1.6801 | 1.6801 | 1.6801 | 1.6802 | 1.6802 | 1.6802 | 1.6802 | 1.6803 | 1.6803 | 1.6803 | 1.6804 | 1.6804 |  | 0% | 0% | 17.26% | 85609 | [7 empty] | 1.72 | -0.04
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.29 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 650 | MAARUIG | 33/11 | 1 x 0.2 |  |  | 0.11238 | 1 | M | M | 0.11238 | 0.11391 | 0.11545 | 0.11703 | 0.11862 | 0.12023 | 0.12187 | 0.12353 | 0.12521 | 0.12691 | 0.12864 | 0.13039 | 0.13216 | 0.13396 |  | 0% | 0% | 0% | 85606 | [7 empty] | 0.1 | 0.012376
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
STRATHLEVEN |  |  | 132/33 | 1 x 60 |  |  |  | 1 |  | Diverse | 0 | 9.7955 | 9.801 | 9.8067 | 9.8123 | 9.8181 | 9.824 | 9.8299 | 9.8359 | 9.842 | 9.8481 | 9.8544 | 9.8607 | 9.8671 | #DIV/0! | 0% | 0% | 0% | 41033
|  |  |  | 1 x 87 | [5 empty] | Aggregate | 9.79 | 9.7955 | 9.801 | 9.8067 | 9.8123 | 9.8181 | 9.824 | 9.8299 | 9.8359 | 9.842 | 9.8481 | 9.8544 | 9.8607 | 9.8671 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 0 | 9.7171 | 9.7226 | 9.7282 | 9.7338 | 9.7396 | 9.7454 | 9.7513 | 9.7572 | 9.7632 | 9.7694 | 9.7756 | 9.7818 | 9.7882
| 206 | ABERFOYLE | 33/11 | 1 x 6.9 |  | 2019-01-26 | 2.4 | 1 | 0 | 0 | 2.4 | 2.4 | 2.4001 | 2.4001 | 2.4002 | 2.4002 | 2.4003 | 2.4003 | 2.4004 | 2.4004 | 2.4004 | 2.4005 | 2.4005 | 2.4006 |  | 0% | 0% | 0% | 85711 | [7 empty] | 2.3525 | 0.047463
[6 empty] | 19:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 220 | BLAIRLINNANS | 33/11 | 1 x 2.5 |  | 2018-04-04 | 0.39 | 1 | M | M | 0.39 | 0.39531 | 0.40068 | 0.40614 | 0.41166 | 0.41726 | 0.42294 | 0.42869 | 0.43452 | 0.44044 | 0.44643 | 0.4525 | 0.45866 | 0.4649 |  | 0% | 0% | 5.128% | 85715 | [7 empty] | 0.39495 | -0.0049502
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.02 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 203 | DRYMEN | 33/11 | 1 x 6 |  | 2018-12-15 | 2.4 | 1 | 0 | 0 | 2.4 | 2.4 | 2.4001 | 2.4001 | 2.4002 | 2.4002 | 2.4003 | 2.4003 | 2.4004 | 2.4004 | 2.4004 | 2.4005 | 2.4005 | 2.4006 |  | 0% | 0% | 10% | 85714 | [7 empty] | 2.7015 | -0.30145
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.24 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 205 | KEPCULLOCH | 33/11 | 2 x 6.25 |  | 2019-02-01 | 2.75 | 1 | 0 | 0 | 2.75 | 2.7501 | 2.7501 | 2.7502 | 2.7502 | 2.7503 | 2.7503 | 2.7504 | 2.7504 | 2.7505 | 2.7505 | 2.7506 | 2.7506 | 2.7507 |  | 0% | 0% | 2.545% | 85712 | [7 empty] | 3.08 | -0.33
[6 empty] | 7:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.07 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 204 | KILLEARN | 33/11 | 1 x 6.25 |  | 2019-01-23 | 1.85 | 1 | 0 | 0 | 1.85 | 1.85 | 1.8501 | 1.8501 | 1.8501 | 1.8502 | 1.8502 | 1.8502 | 1.8503 | 1.8503 | 1.8503 | 1.8504 | 1.8504 | 1.8504 |  | 0% | 0% | 20% | 85718 | [7 empty] | 2.11 | -0.26
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.37 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
STRICHEN | 949 |  | 132/33 | 2 x 90 |  |  | 16.6 | 1 |  | Diverse | 16.6 | 16.6003 | 16.6006 | 16.6009 | 16.6012 | 16.6015 | 16.6018 | 16.6021 | 16.6024 | 16.6027 | 16.603 | 16.6033 | 16.6036 | 16.6039 | Diversity/Losses: 0.965 | 0% | 0% | 6.627% | 19530
[10 empty] | Aggregate | 16.0222 | 16.0225 | 16.0228 | 16.0231 | 16.0234 | 16.0237 | 16.024 | 16.0243 | 16.0246 | 16.0248 | 16.0251 | 16.0254 | 16.0257 | 16.026 |  |  |  | 1.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 16.4672 | 16.4675 | 16.4678 | 16.4681 | 16.4684 | 16.4687 | 16.469 | 16.4693 | 16.4696 | 16.4699 | 16.4702 | 16.4705 | 16.4708 | 16.4711
| 863 | HATTON | 33/11 | 2 x 5 |  | 2018-12-25 | 3.04 | 1 | 0 | 0 | 3.04 | 3.0401 | 3.0401 | 3.0402 | 3.0402 | 3.0403 | 3.0403 | 3.0404 | 3.0404 | 3.0405 | 3.0406 | 3.0406 | 3.0407 | 3.0407 |  | 0% | 0% | 11.51% | 85813 | [7 empty] | 2.991 | 0.049021
[6 empty] | 13:30 |  |  |  |  | 16.4672: Committed new connections: |  |  |  | 0.35 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 16.469: Generation at time of peak:; 0 16.4693: 0
| 901 | MAUD | 33/11 | 2 x 8 |  | 2019-01-31 | 2.51 | 1 | 0 | 0 | 2.51 | 2.51 | 2.5101 | 2.5101 | 2.5102 | 2.5102 | 2.5103 | 2.5103 | 2.5104 | 2.5104 | 2.5105 | 2.5105 | 2.5105 | 2.5106 |  | 0% | 0% | 0% | 85817 | [7 empty] | 2.6708 | -0.16076
[6 empty] | 20:30 |  |  |  |  | 16.4672: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 16.469: Generation at time of peak:; 0 16.4693: 0
| 909 | MINTLAW | 33/11 | 2 x 15 |  | 2019-01-24 | 5.791 | 1 | 0 | 0 | 5.791 | 5.7911 | 5.7912 | 5.7913 | 5.7914 | 5.7915 | 5.7916 | 5.7917 | 5.7918 | 5.792 | 5.7921 | 5.7922 | 5.7923 | 5.7924 |  | 0% | 0% | 0% | 85807 | [7 empty] | 5.9915 | -0.20049
[6 empty] | 16:30 |  |  |  |  | 16.4672: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 16.469: Generation at time of peak:; 0 16.4693: 0
| 913 | NEW PITSLIGO | 33/11 | 2 x 2.5 |  | 2019-02-01 | 1.6212 | 1 | 0 | 0 | 1.6212 | 1.6212 | 1.6213 | 1.6213 | 1.6213 | 1.6214 | 1.6214 | 1.6214 | 1.6214 | 1.6215 | 1.6215 | 1.6215 | 1.6216 | 1.6216 |  | 0% | 0% | 0.4632% | 85802 | [7 empty] | 2.9168 | -1.2956
[6 empty] | 20:00 |  |  |  |  | 16.4672: Committed new connections: |  |  |  | 0.0075093 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 16.469: Generation at time of peak:; 0 16.4693: 0
| 950 | STRICHEN | 33/11 | 2 x 10 |  | 2019-01-31 | 3.06 | 1 | 0 | 0 | 3.06 | 3.0601 | 3.0601 | 3.0602 | 3.0602 | 3.0603 | 3.0603 | 3.0604 | 3.0604 | 3.0605 | 3.0606 | 3.0606 | 3.0607 | 3.0607 |  | 0% | 0% | 0% | 85804 | [7 empty] | 3.2535 | -0.19345
[6 empty] | 17:00 |  |  |  |  | 16.4672: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Generation at time of BSP peak: 16.469: Generation at time of peak:; 0 16.4693: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
TARLAND | 470 |  | 132/33 | 2 x 30 |  |  | 20.3 | 1 |  | Diverse | 20.3 | 20.3318 | 20.3645 | 20.398 | 20.4324 | 20.4677 | 20.5039 | 20.5411 | 20.5793 | 20.6185 | 20.6588 | 20.7001 | 20.7425 | 20.7861 | Diversity/Losses: 0.945 | 0% | 0% | 22.17% | 21430
[10 empty] | Aggregate | 19.1896 | 19.2196 | 19.2505 | 19.2822 | 19.3147 | 19.3481 | 19.3823 | 19.4175 | 19.4536 | 19.4907 | 19.5287 | 19.5678 | 19.6079 | 19.6491 |  |  |  | 4.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 20.1376 | 20.1691 | 20.2015 | 20.2348 | 20.2689 | 20.3039 | 20.3399 | 20.3768 | 20.4147 | 20.4536 | 20.4935 | 20.5345 | 20.5766 | 20.6198
| 801 | ABOYNE | 33/11 | 2 x 15 |  | 2019-01-31 | 6.11 | 1 | 0 | 0 | 6.11 | 6.1101 | 6.1102 | 6.1103 | 6.1104 | 6.1106 | 6.1107 | 6.1108 | 6.1109 | 6.111 | 6.1111 | 6.1112 | 6.1113 | 6.1115 |  | 0% | 0% | 19.48% | 86704 | [7 empty] | 6.54 | -0.43
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.19 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 806 | BALLATER | 33/11 | 2 x 15 |  | 2019-01-31 | 5.44 | 1 | 0 | 0 | 5.44 | 5.4401 | 5.4402 | 5.4403 | 5.4404 | 5.4405 | 5.4406 | 5.4407 | 5.4408 | 5.4409 | 5.441 | 5.4411 | 5.4412 | 5.4413 |  | 0% | 0% | 19.49% | 86708 | [7 empty] | 5.8078 | -0.36781
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.06 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 911 | MOSSAT | 33/11 | 2 x 2.5 |  | 2019-01-31 | 1.7096 | 1 | 0 | 0 | 1.7096 | 1.7096 | 1.7096 | 1.7097 | 1.7097 | 1.7097 | 1.7098 | 1.7098 | 1.7098 | 1.7098 | 1.7099 | 1.7099 | 1.7099 | 1.71 |  | 0% | 0% | 0.397% | 86711 | [7 empty] | 1.6501 | 0.05942
[6 empty] | 19:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.0067865 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 951 | STRATHDON | 33/11 | 1 x 2 |  | 2019-01-02 | 1.11 | 1 | H | H | 1.11 | 1.1397 | 1.1703 | 1.2016 | 1.2338 | 1.2669 | 1.3008 | 1.3356 | 1.3714 | 1.4081 | 1.4459 | 1.4846 | 1.5244 | 1.5652 |  | 0% | 0% | 12.61% | 86715 | [7 empty] | 1.1029 | 0.0070911
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.14 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 981 | WHITEHOUSE | 33/11 | 2 x 8 |  | 2019-01-31 | 4.82 | 1 | 0 | 0 | 4.82 | 4.8201 | 4.8202 | 4.8203 | 4.8204 | 4.8204 | 4.8205 | 4.8206 | 4.8207 | 4.8208 | 4.8209 | 4.821 | 4.8211 | 4.8211 |  | 0% | 0% | 16.39% | 86717 | [7 empty] | 4.8897 | -0.069691
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.79 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
TAYNUILT | 303 |  | 132/33 | 2 x 90 |  |  | 33.8 | 1 |  | Diverse | 33.8 | 34.0786 | 34.3617 | 34.6492 | 34.9412 | 35.2378 | 35.5392 | 35.8453 | 36.1562 | 36.4721 | 36.7931 | 37.1191 | 37.4504 | 37.787 | Diversity/Losses: 1.031 | 0% | 0% | 18.64% | 19730
[10 empty] | Aggregate | 34.8475 | 35.1348 | 35.4266 | 35.723 | 36.0241 | 36.3299 | 36.6406 | 36.9562 | 37.2768 | 37.6025 | 37.9334 | 38.2695 | 38.6111 | 38.9581 |  |  |  | 6.3 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 33.5296 | 33.806 | 34.0868 | 34.372 | 34.6617 | 34.9559 | 35.2548 | 35.5585 | 35.867 | 36.1804 | 36.4987 | 36.8222 | 37.1508 | 37.4847
| 327 | BARCALDINE | 33/11 | 1 x 15 |  | 2019-02-02 | 2.2706 | 1 | 0 | 0 | 2.2706 | 2.2706 | 2.2707 | 2.2707 | 2.2708 | 2.2708 | 2.2708 | 2.2709 | 2.2709 | 2.271 | 2.271 | 2.271 | 2.2711 | 2.2711 |  | 0% | 0% | 13.37% | 85910 | [7 empty] | 3.4378 | -1.1672
[6 empty] | 43080.724 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.30361 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 328 | BONAWE | 33/11 | 1 x 0.5 |  |  | 0.0028094 | 1 | 0 | 0 | 0.0028094 | 0.0028095 | 0.0028095 | 0.0028096 | 0.0028096 | 0.0028097 | 0.0028097 | 0.0028098 | 0.0028098 | 0.0028099 | 0.0028099 | 0.00281 | 0.00281 | 0.0028101 |  | 0% | 0% | 0% | 85905 | [7 empty] | 0.02 | -0.017191
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 306 | CONNEL | 33/11 | 1 x 8 |  | 2019-01-31 | 1.61 | 1 | 0 | 0 | 1.61 | 1.61 | 1.6101 | 1.6101 | 1.6101 | 1.6101 | 1.6102 | 1.6102 | 1.6102 | 1.6103 | 1.6103 | 1.6103 | 1.6104 | 1.6104 |  | 0% | 0% | 13.66% | 85912 | [7 empty] | 1.77 | -0.16
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.22 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 348 | DALMALLY | 33/11 | 1 x 1 |  |  | 0.23599 | 1 | 0 | 0 | 0.23599 | 0.23599 | 0.236 | 0.236 | 0.23601 | 0.23601 | 0.23602 | 0.23602 | 0.23602 | 0.23603 | 0.23603 | 0.23604 | 0.23604 | 0.23605 |  | 0% | 0% | 0% | 85955 | [7 empty] | 0.257 | -0.02101
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 346 | DERVAIG | 33/11 | 1 x 8 |  | 2018-04-01 | 3.56 | 1 | 0 | 0 | 3.56 | 3.5601 | 3.5601 | 3.5602 | 3.5603 | 3.5603 | 3.5604 | 3.5605 | 3.5605 | 3.5606 | 3.5606 | 3.5607 | 3.5608 | 3.5608 |  | 0% | 0% | 0.2809% | 85939 | [7 empty] | 3.64 | -0.080021
[6 empty] | 4:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.01 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 324 | EREDINE | 33/11 | 1 x 0.2 |  |  | 0.1208 | 1 | 0 | 0 | 0.1208 | 0.12081 | 0.12081 | 0.12081 | 0.12081 | 0.12082 | 0.12082 | 0.12082 | 0.12082 | 0.12082 | 0.12083 | 0.12083 | 0.12083 | 0.12083 |  | 0% | 0% | 0% | 85972 | [7 empty] | 0.1 | 0.020805
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 329 | KENMORE | 33/11 | 1 x 1.5 |  |  | 0.30342 | 1 | 0 | 0 | 0.30342 | 0.30342 | 0.30343 | 0.30343 | 0.30344 | 0.30344 | 0.30345 | 0.30345 | 0.30346 | 0.30347 | 0.30347 | 0.30348 | 0.30348 | 0.30349 |  | 0% | 0% | 0% | 85908 | [7 empty] | 0.32 | -0.016584
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 335 | KERRERA | 33/11 | 1 x 0.3 |  |  | 0.09552 | 1 | 0 | 0 | 0.09552 | 0.095522 | 0.095523 | 0.095525 | 0.095527 | 0.095529 | 0.09553 | 0.095532 | 0.095534 | 0.095536 | 0.095537 | 0.095539 | 0.095541 | 0.095543 |  | 0% | 0% | 0% | 85926 | [7 empty] | 0.11 | -0.01448
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 323 | KILCHRENAN | 33/11 | 1 x 1 |  | 2018-04-02 | 0.67 | 1 | 0 | 0 | 0.67 | 0.67001 | 0.67002 | 0.67004 | 0.67005 | 0.67006 | 0.67007 | 0.67009 | 0.6701 | 0.67011 | 0.67012 | 0.67013 | 0.67015 | 0.67016 |  | 0% | 0% | 2.985% | 85945 | [7 empty] | 0.82 | -0.15
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.02 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 304 | KILMELFORD PS | 33/11 | 1 x 2 |  | 2018-10-10 | 1.96 | 1 | 0 | 0 | 1.96 | 1.96 | 1.9601 | 1.9601 | 1.9601 | 1.9602 | 1.9602 | 1.9603 | 1.9603 | 1.9603 | 1.9604 | 1.9604 | 1.9604 | 1.9605 |  | 0% | 0% | 29.08% | 85986 | [7 empty] | 1.89 | 0.07
[6 empty] | 15:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.57 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 322 | KILNINVER | 33/11 | 1 x 2.5 |  | 2018-04-05 | 2.06 | 1 | M | M | 2.06 | 2.088 | 2.1164 | 2.1452 | 2.1744 | 2.204 | 2.234 | 2.2644 | 2.2952 | 2.3264 | 2.3581 | 2.3901 | 2.4227 | 2.4556 |  | 0% | 0% | 0.04854% | 85920 | [7 empty] | 2.2 | -0.14
[6 empty] | 3:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.001 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 333 | KINLOCH | 33/11 | 1 x 2.5 |  | 2018-04-03 | 1.74 | 1 | H | H | 1.74 | 1.7866 | 1.8345 | 1.8836 | 1.9341 | 1.9859 | 2.0391 | 2.0937 | 2.1498 | 2.2074 | 2.2665 | 2.3272 | 2.3895 | 2.4536 |  | 0% | 0% | 16.09% | 85935 | [7 empty] | 1.59 | 0.15
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.28 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 317 | LOCHDONHEAD | 33/11 | 1 x 1 |  | 2018-04-03 | 0.99 | 1 | 0 | 0 | 0.99 | 0.99002 | 0.99004 | 0.99005 | 0.99007 | 0.99009 | 0.99011 | 0.99013 | 0.99014 | 0.99016 | 0.99018 | 0.9902 | 0.99022 | 0.99023 |  | 0% | 0% | 22.22% | 85929 | [7 empty] | 1.04 | -0.05
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.22 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 307 | OBAN | 33/11 | 2 x 24 |  | 2019-01-23 | 15.6094 | 1 | M | M | 15.6094 | 15.8217 | 16.037 | 16.2552 | 16.4763 | 16.7005 | 16.9277 | 17.158 | 17.3914 | 17.628 | 17.8678 | 18.1109 | 18.3573 | 18.6071 |  | 0% | 0% | 23.26% | 85916 | [7 empty] | 16.9744 | -1.3651
[6 empty] | 13:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.6302 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 315 | SALEN | 33/11 | 2 x 6.3 |  | 2018-12-07 | 2.1577 | 1 | 0 | 0 | 2.1577 | 2.1578 | 2.1578 | 2.1579 | 2.1579 | 2.1579 | 2.158 | 2.158 | 2.1581 | 2.1581 | 2.1581 | 2.1582 | 2.1582 | 2.1583 |  | 0% | 0% | 13.01% | 85936 | 85990 | [6 empty] | 2.1434 | 0.014349
[6 empty] | 18:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.28077 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 340 | SCAMMADALE | 33/11 | 1 x 0.1 |  |  | 0.078663 | 1 | 0 | 0 | 0.078663 | 0.078665 | 0.078666 | 0.078668 | 0.078669 | 0.078671 | 0.078672 | 0.078673 | 0.078675 | 0.078676 | 0.078678 | 0.078679 | 0.078681 | 0.078682 |  | 0% | 0% | 0% | 85923 | [7 empty] | 0.08 | -0.0013366
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 347 | TAYNUILT | 33/11 | 1 x 1.8 |  | 2019-02-01 | 1.318 | 1 | 0 | 0 | 1.318 | 1.318 | 1.318 | 1.3181 | 1.3181 | 1.3181 | 1.3181 | 1.3182 | 1.3182 | 1.3182 | 1.3182 | 1.3183 | 1.3183 | 1.3183 |  | 0% | 0% | 16.46% | 85902 | [7 empty] | 1.5057 | -0.18774
[6 empty] | 4:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.217 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 342 | TIRORAN BRIDGE | 33/11 | 1 x 0.05 |  |  | 0.064616 | 1 | 0 | 0 | 0.064616 | 0.064618 | 0.064619 | 0.06462 | 0.064621 | 0.064622 | 0.064623 | 0.064625 | 0.064626 | 0.064627 | 0.064628 | 0.064629 | 0.064631 | 0.064632 |  | 0% | 0% | 0% | 85933 | [7 empty] | 0.06 | 0.0046164
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
THURSO | 593 |  | 132/33 | 2 x 120 |  |  | 41.4 | 1 |  | Diverse | 41.4 | 41.4111 | 41.4224 | 41.4339 | 41.4457 | 41.4577 | 41.4699 | 41.4824 | 41.4951 | 41.5081 | 41.5213 | 41.5348 | 41.5486 | 41.5627 | Diversity/Losses: 1.047 | 0% | 0% | 16.91% | 19930
[10 empty] | Aggregate | 43.3287 | 43.3403 | 43.3522 | 43.3642 | 43.3765 | 43.3891 | 43.4019 | 43.4149 | 43.4283 | 43.4419 | 43.4557 | 43.4699 | 43.4843 | 43.499 |  |  |  | 7 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 41.0688 | 41.0798 | 41.091 | 41.1025 | 41.1141 | 41.126 | 41.1381 | 41.1505 | 41.1631 | 41.176 | 41.1892 | 41.2026 | 41.2162 | 41.2302
| 701 | BURGARHILL | 33/11 | 1 x 8 |  | 2018-11-29 | 1.63 | 1 | 0 | 0 | 1.63 | 1.63 | 1.6301 | 1.6301 | 1.6301 | 1.6301 | 1.6302 | 1.6302 | 1.6302 | 1.6303 | 1.6303 | 1.6303 | 1.6304 | 1.6304 |  | 0% | 0% | 3.067% | 86109 | [7 empty] | 2.35 | -0.72
[6 empty] | 14:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 675 | EDAY | 33/11 | 1 x 1 |  | 2018-12-04 | 0.22 | 1 | 0 | 0 | 0.22 | 0.22 | 0.22001 | 0.22001 | 0.22002 | 0.22002 | 0.22002 | 0.22003 | 0.22003 | 0.22004 | 0.22004 | 0.22004 | 0.22005 | 0.22005 |  | 0% | 0% | 4.545% | 86116 | [7 empty] | 0.21262 | 0.0073779
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.01 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 680 | FLOTTA | 33/11 | 1 x 8 |  | 2018-10-27 | 0.23 | 1 | H | H | 0.23 | 0.23616 | 0.24249 | 0.24898 | 0.25565 | 0.2625 | 0.26953 | 0.27675 | 0.28417 | 0.29178 | 0.29959 | 0.30762 | 0.31586 | 0.32432 |  | 0% | 0% | 0% | 86136 | [7 empty] | 0.24084 | -0.010836
[6 empty] | 0:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 597 | HALKIRK | 33/11 | 1 x 2.5 |  | 2019-01-23 | 2.09 | 1 | 0 | 0 | 2.09 | 2.09 | 2.0901 | 2.0901 | 2.0902 | 2.0902 | 2.0902 | 2.0903 | 2.0903 | 2.0903 | 2.0904 | 2.0904 | 2.0905 | 2.0905 |  | 0% | 0% | 21.53% | 86017 | [7 empty] | 2.2038 | -0.1138
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.45 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 582 | HASTIGROW | 33/11 | 1 x 5 |  | 2018-12-05 | 2.59 | 1 | 0 | 0 | 2.59 | 2.59 | 2.5901 | 2.5901 | 2.5902 | 2.5902 | 2.5903 | 2.5903 | 2.5904 | 2.5904 | 2.5905 | 2.5905 | 2.5906 | 2.5906 |  | 0% | 0% | 6.564% | 86002 | [7 empty] | 2.5392 | 0.050845
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.17 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 677 | KIRKWALL | 33/11 | 2 x 24 |  | 2019-01-24 | 15.01 | 1 | 0 | 0 | 15.01 | 15.0103 | 15.0105 | 15.0108 | 15.0111 | 15.0114 | 15.0116 | 15.0119 | 15.0122 | 15.0125 | 15.0127 | 15.013 | 15.0133 | 15.0136 |  | 0% | 0% | 8.195% | 86124 | 86125 | 86142 | [5 empty] | 16.26 | -1.25
[6 empty] | 8:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.23 | 33.3% | 33.3% | 33.3% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 682 | LYNESS | 33/11 | 1 x 1 |  | 2018-12-25 | 0.67193 | 1 | 0 | 0 | 0.67193 | 0.67194 | 0.67196 | 0.67197 | 0.67198 | 0.67199 | 0.67201 | 0.67202 | 0.67203 | 0.67204 | 0.67206 | 0.67207 | 0.67208 | 0.67209 |  | 0% | 0% | 7.687% | 86133 | [7 empty] | 0.72879 | -0.056855
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.05165 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 585 | MOUNT PLEASANT | 33/11 | 1 x 7.5/15 |  | 2019-01-29 | 4.6052 | 1 | 0 | 0 | 4.6052 | 4.6053 | 4.6053 | 4.6054 | 4.6055 | 4.6056 | 4.6057 | 4.6058 | 4.6059 | 4.6059 | 4.606 | 4.6061 | 4.6062 | 4.6063 |  | 0% | 0% | 23.98% | 86011 | [7 empty] | 4.97 | -0.36482
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.1043 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 681 | NORTH HOY | 33/11 | 1 x 0.2 |  |  | 0.10957 | 1 | 0 | 0 | 0.10957 | 0.10957 | 0.10957 | 0.10957 | 0.10957 | 0.10958 | 0.10958 | 0.10958 | 0.10958 | 0.10958 | 0.10959 | 0.10959 | 0.10959 | 0.10959 |  | 0% | 0% | 0% | 86130 | [7 empty] | 0.12 | -0.010433
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 587 | ORMLIE | 33/11 | 1 x 7.5 |  | 2018-12-14 | 5.4591 | 1 | 0 | 0 | 5.4591 | 5.4592 | 5.4593 | 5.4594 | 5.4595 | 5.4596 | 5.4597 | 5.4598 | 5.4599 | 5.46 | 5.4601 | 5.4602 | 5.4603 | 5.4604 |  | 0% | 0% | 21.07% | 86007 | [7 empty] | 5.132 | 0.3271
[6 empty] | 16:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.15 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 498 | ROUSAY | 33/11 | 1 x 2.5 |  | 2019-02-02 | 0.34269 | 1 | M | M | 0.34269 | 0.34735 | 0.35208 | 0.35687 | 0.36172 | 0.36664 | 0.37163 | 0.37669 | 0.38181 | 0.38701 | 0.39227 | 0.39761 | 0.40302 | 0.4085 |  | 0% | 0% | 0.01254% | 86112 | [7 empty] | 1.98 | -1.6373
[6 empty] | 43178.7861 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4.2961e-05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 685 | SANDAY | 33/11 | 1 x 1 |  | 2019-01-23 | 0.79039 | 1 | 0 | 0 | 0.79039 | 0.79041 | 0.79042 | 0.79043 | 0.79045 | 0.79046 | 0.79048 | 0.79049 | 0.79051 | 0.79052 | 0.79054 | 0.79055 | 0.79056 | 0.79058 |  | 0% | 0% | 0% | 86118 | [7 empty] | 0.8184 | -0.028012
[6 empty] | 43161.5474 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 683 | SHAPINSAY | 33/11 | 1 x 1 |  | 2018-12-23 | 0.42 | 1 | 0 | 0 | 0.42 | 0.42001 | 0.42002 | 0.42002 | 0.42003 | 0.42004 | 0.42005 | 0.42005 | 0.42006 | 0.42007 | 0.42008 | 0.42008 | 0.42009 | 0.4201 |  | 0% | 0% | 4.762% | 86122 | [7 empty] | 0.45553 | -0.03553
[6 empty] | 11:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.02 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 679 | ST MARYS | 33/11 | 1 x 4 |  | 2018-12-10 | 2.43 | 1 | 0 | 0 | 2.43 | 2.43 | 2.4301 | 2.4301 | 2.4302 | 2.4302 | 2.4303 | 2.4303 | 2.4304 | 2.4304 | 2.4304 | 2.4305 | 2.4305 | 2.4306 |  | 0% | 0% | 3.292% | 86127 | [7 empty] | 2.4728 | -0.042778
[6 empty] | 19:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.08 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 678 | STROMNESS | 33/11 | 2 x 15 |  | 2019-01-29 | 5.21 | 1 | 0 | 0 | 5.21 | 5.2101 | 5.2102 | 5.2103 | 5.2104 | 5.2105 | 5.2106 | 5.2107 | 5.2108 | 5.2109 | 5.211 | 5.211 | 5.2111 | 5.2112 |  | 0% | 0% | 2.303% | 86103 | 86105 | [6 empty] | 5.3613 | -0.15128
[6 empty] | 21:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.12 | 50% | 50% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 684 | STRONSAY | 33/11 | 1 x 1 |  | 2019-01-31 | 0.44 | 1 | 0 | 0 | 0.44 | 0.44001 | 0.44002 | 0.44002 | 0.44003 | 0.44004 | 0.44005 | 0.44006 | 0.44006 | 0.44007 | 0.44008 | 0.44009 | 0.4401 | 0.4401 |  | 0% | 0% | 0% | 86120 | [7 empty] | 0.42475 | 0.015254
[6 empty] | 19:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 674 | WESTRAY | 33/11 | 1 x 4 |  | 2019-01-24 | 1.0799 | 1 | 0 | 0 | 1.0799 | 1.0799 | 1.0799 | 1.0799 | 1.0799 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.0801 | 1.0801 | 1.0801 | 1.0801 |  | 0% | 0% | 0.0008539% | 86114 | [7 empty] | 1.7948 | -0.71498
[6 empty] | 7:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 9.2214e-06 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
TUMMEL BRIDGE | 260 |  | 132/11 | 2 x 21 |  |  | 13.8 | 1 |  | Diverse | 13.8 | 13.802 | 13.804 | 13.8061 | 13.8082 | 13.8104 | 13.8126 | 13.8149 | 13.8172 | 13.8196 | 13.8221 | 13.8246 | 13.8271 | 13.8298 | Diversity/Losses: 1.13 | 0% | 0% | 28.26% | 20130
[10 empty] | Aggregate | 15.5909 | 15.5932 | 15.5955 | 15.5978 | 15.6002 | 15.6027 | 15.6052 | 15.6078 | 15.6104 | 15.6131 | 15.6159 | 15.6187 | 15.6216 | 15.6246 |  |  |  | 3.9 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 13.6896 | 13.6916 | 13.6936 | 13.6956 | 13.6977 | 13.6999 | 13.7021 | 13.7044 | 13.7067 | 13.7091 | 13.7115 | 13.714 | 13.7165 | 13.7191
| 267 | ABERFELDY | 33/11 | 2 x 8 |  | 2019-02-01 | 3.84 | 1 | 0 | 0 | 3.84 | 3.8401 | 3.8401 | 3.8402 | 3.8403 | 3.8404 | 3.8404 | 3.8405 | 3.8406 | 3.8406 | 3.8407 | 3.8408 | 3.8408 | 3.8409 |  | 0% | 0% | 11.72% | 86236 | [7 empty] | 3.6876 | 0.15245
[6 empty] | 19:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.45 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 266 | BONSKEID | 33/11 | 1 x 5 |  | 2019-01-30 | 3.44 | 1 | 0 | 0 | 3.44 | 3.4401 | 3.4401 | 3.4402 | 3.4403 | 3.4403 | 3.4404 | 3.4404 | 3.4405 | 3.4406 | 3.4406 | 3.4407 | 3.4408 | 3.4408 |  | 0% | 0% | 21.51% | 86212 | [7 empty] | 3.7561 | -0.31613
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.74 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 265 | CALVINE | 33/11 | 1 x 2.5 |  | 2018-04-01 | 1.19 | 1 | 0 | 0 | 1.19 | 1.19 | 1.19 | 1.1901 | 1.1901 | 1.1901 | 1.1901 | 1.1902 | 1.1902 | 1.1902 | 1.1902 | 1.1902 | 1.1903 | 1.1903 |  | 0% | 0% | 17.65% | 86222 | [7 empty] | 1.18 | 0.01
[6 empty] | 9:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.21 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 268 | COSHIEVILLE | 33/11 | 1 x 2.5 |  | 2019-01-03 | 1.75 | 1 | 0 | 0 | 1.75 | 1.75 | 1.7501 | 1.7501 | 1.7501 | 1.7502 | 1.7502 | 1.7502 | 1.7503 | 1.7503 | 1.7503 | 1.7504 | 1.7504 | 1.7504 |  | 0% | 0% | 5.714% | 86229 | [7 empty] | 1.96 | -0.21
[6 empty] | 20:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 276 | FINCASTLE | 33/11 | 1 x 0.1 |  |  | 0.073045 | 1 | H | H | 0.073045 | 0.075001 | 0.07701 | 0.079073 | 0.081191 | 0.083366 | 0.0856 | 0.087893 | 0.090247 | 0.092664 | 0.095147 | 0.097695 | 0.10031 | 0.103 |  | 0% | 0% | 0% | 86220 | [7 empty] | 0.04 | 0.033045
|  | No PI | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 262 | KINLOCH RANNOCH | 33/11 | 1 x 2.5 |  | 2018-09-11 | 0.99521 | 1 | 0 | 0 | 0.99521 | 0.99523 | 0.99525 | 0.99526 | 0.99528 | 0.9953 | 0.99532 | 0.99534 | 0.99535 | 0.99537 | 0.99539 | 0.99541 | 0.99543 | 0.99545 |  | 0% | 0% | 0% | 86225 | [7 empty] | 1.223 | -0.22779
[6 empty] | 6:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 263 | PITLOCHRY | 33/11 | 2 x 5 |  | 2019-02-01 | 3.6427 | 1 | 0 | 0 | 3.6427 | 3.6427 | 3.6428 | 3.6429 | 3.6429 | 3.643 | 3.6431 | 3.6431 | 3.6432 | 3.6433 | 3.6433 | 3.6434 | 3.6435 | 3.6435 |  | 0% | 0% | 6.479% | 86216 | [7 empty] | 3.68 | -0.037324
[6 empty] | 7:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.236 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 260 | TUMMEL BRIDGE | 33/11 | 1 x 2.5 |  | 2018-04-04 | 0.66 | 1 | 0 | 0 | 0.66 | 0.66001 | 0.66002 | 0.66004 | 0.66005 | 0.66006 | 0.66007 | 0.66008 | 0.6601 | 0.66011 | 0.66012 | 0.66013 | 0.66014 | 0.66016 |  | 0% | 0% | 13.64% | 86241
[6 empty] | 9:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.09 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
WILLOWDALE | 983 |  | 132/33 | 2 x 60 |  |  | 36.4 | 1 |  | Diverse | 36.4 | 36.4007 | 36.4013 | 36.402 | 36.4027 | 36.4033 | 36.404 | 36.4047 | 36.4053 | 36.406 | 36.4066 | 36.4073 | 36.408 | 36.4086 | Diversity/Losses: 1.098 | 0% | 0% | 27.75% | 20230
[10 empty] | Aggregate | 39.9593 | 39.96 | 39.9608 | 39.9615 | 39.9622 | 39.963 | 39.9637 | 39.9644 | 39.9652 | 39.9659 | 39.9666 | 39.9673 | 39.9681 | 39.9688 |  |  |  | 10.1 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 36.1088 | 36.1095 | 36.1101 | 36.1108 | 36.1114 | 36.1121 | 36.1128 | 36.1134 | 36.1141 | 36.1147 | 36.1154 | 36.1161 | 36.1167 | 36.1174
| 841 | DENBURN | 33/11 | 2 x 21 |  | 2019-02-01 | 14.72 | 1 | 0 | 0 | 14.72 | 14.7203 | 14.7205 | 14.7208 | 14.7211 | 14.7213 | 14.7216 | 14.7219 | 14.7222 | 14.7224 | 14.7227 | 14.723 | 14.7232 | 14.7235 |  | 0% | 0% | 27.11% | 86320 | [7 empty] | 15.6428 | -0.92279
[6 empty] | 11:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 3.99 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 861 | GREYFRIARS | 33/11 | 2 x 24 |  | 2018-11-26 | 8.3 | 1 | 0 | 0 | 8.3 | 8.3002 | 8.3003 | 8.3005 | 8.3006 | 8.3008 | 8.3009 | 8.3011 | 8.3012 | 8.3014 | 8.3015 | 8.3017 | 8.3018 | 8.302 |  | 0% | 0% | 25.42% | 86314 | [7 empty] | 9.726 | -1.426
[6 empty] | 19:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.11 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 867 | HAYTON | 33/11 | 2 x 23 |  | 2019-01-22 | 5.5 | 1 | 0 | 0 | 5.5 | 5.5001 | 5.5002 | 5.5003 | 5.5004 | 5.5005 | 5.5006 | 5.5007 | 5.5008 | 5.5009 | 5.501 | 5.5011 | 5.5012 | 5.5013 |  | 0% | 0% | 16.55% | 86302 | [7 empty] | 4.9053 | 0.59468
[6 empty] | 18:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.91 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 917 | NORTHFIELD | 33/11 | 2 x 15 |  | 2018-12-17 | 4.6688 | 1 | 0 | 0 | 4.6688 | 4.6689 | 4.669 | 4.6691 | 4.6691 | 4.6692 | 4.6693 | 4.6694 | 4.6695 | 4.6696 | 4.6697 | 4.6697 | 4.6698 | 4.6699 |  | 0% | 0% | 19.71% | 86305 | [7 empty] | 4.7912 | -0.12242
[6 empty] | 17:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 0.92 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 958 | ST NICHOLAS | 33/11 | 2 x 12.5 |  | 2018-12-05 | 6.7705 | 1 | 0 | 0 | 6.7705 | 6.7706 | 6.7708 | 6.7709 | 6.771 | 6.7711 | 6.7712 | 6.7714 | 6.7715 | 6.7716 | 6.7717 | 6.7719 | 6.772 | 6.7721 |  | 0% | 0% | 22.12% | 86324 | [7 empty] | 11.31 | -4.5395
[6 empty] | 15:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.4976 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
Average Cold Spell (ACS) (MVA)
GSP | NRN | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MW) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2026/27 | 2027/28 | 2028/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
WOODHILL | 986 |  | 132/33 | 2 x 90 |  |  | 33.4 | 1 |  | Diverse | 33.4 | 33.5679 | 33.7381 | 33.9106 | 34.0854 | 34.2627 | 34.4423 | 34.6243 | 34.8089 | 34.9959 | 35.1855 | 35.3776 | 35.5724 | 35.7698 | Diversity/Losses: 1.293 | 0% | 0% | 31.44% | 20330
[10 empty] | Aggregate | 43.1821 | 43.3991 | 43.6192 | 43.8422 | 44.0682 | 44.2974 | 44.5296 | 44.765 | 45.0035 | 45.2454 | 45.4905 | 45.7389 | 45.9907 | 46.2459 |  |  |  | 10.5 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 33.1328 | 33.2994 | 33.4682 | 33.6393 | 33.8128 | 33.9886 | 34.1667 | 34.3473 | 34.5304 | 34.7159 | 34.904 | 35.0946 | 35.2878 | 35.4836
| 932 | QUEENS LANE NORTH | 33/11 | 2 x 12.5 |  | 2019-01-31 | 12.9621 | 1 | 0 | 0 | 12.9621 | 12.9623 | 12.9625 | 12.9628 | 12.963 | 12.9632 | 12.9635 | 12.9637 | 12.9639 | 12.9642 | 12.9644 | 12.9647 | 12.9649 | 12.9651 |  | 0% | 0% | 19.98% | 86400 | [7 empty] | 12.25 | 0.71205
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 2.59 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 943 | SPRINGHILL | 33/11 | 2 x 21 |  | 2019-01-21 | 15.92 | 1 | M | M | 15.92 | 16.1366 | 16.3561 | 16.5786 | 16.8042 | 17.0328 | 17.2645 | 17.4994 | 17.7375 | 17.9788 | 18.2234 | 18.4713 | 18.7226 | 18.9774 |  | 0% | 0% | 26.95% | 86405 | [7 empty] | 14.7968 | 1.1232
[6 empty] | 17:30 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 4.29 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0
| 986 | WOODHILL | 33/11 | 2 x 24 |  | 2019-02-26 | 14.3 | 1 | 0 | 0 | 14.3 | 14.3003 | 14.3005 | 14.3008 | 14.301 | 14.3013 | 14.3016 | 14.3018 | 14.3021 | 14.3023 | 14.3026 | 14.3029 | 14.3031 | 14.3034 |  | 0% | 0% | 9.93% | 86403 | [7 empty] | 13.9463 | 0.35367
[6 empty] | 12:00 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  | 1.42 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2024/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2025/26: 0

## GSP Template
Average Cold Spell (ACS) (MVA)
GSP | ED3 | Name | Voltage Ratio | TX Details | Firm Capacity | Date & time of Peak | 2018/19 Peak (MVA) | ACS Corr. Factor | Historic Trend | Forecasting | 2018/19 | 2018/20 | 2018/21 | 2018/22 | 2018/23 | 2018/24 | 2018/25 | 2018/26 | 2018/27 | 2018/28 | 2018/29 | Commentary | Spring/ Autumn | Summer | Minimum Demand | PSS/E Bus #1 | PSS/E Bus #2 | PSS/E Bus #3 | PSS/E Bus #4 | PSS/E Bus #5 | PSS/E Bus #6 | PSS/E Bus #7 | PSS/E Bus #8
GSP Name |  |  | 132/33 |  |  |  |  | #N/A |  | Diverse | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0% | 0% | 0%
[10 empty] | Aggregate | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Generation at BSP: | [7 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of BSP peak:; Average Cold Spell (ACS) (MVA) 2018/26: 17.5992
[6 empty] | Power Factor: | 0.992 |  |  | Div. (MW) | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | #N/A | 33/11 |  |  | 2017-12-11 | 17.235 | - | - | L | 0 | 0.4 | 1.2 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 |  | 0% | 0% | 0%
[6 empty] | 43080.724 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections:; Average Cold Spell (ACS) (MVA) 2018/20: 0.4; Average Cold Spell (ACS) (MVA) 2018/21: 0.8; Average Cold Spell (ACS) (MVA) 2018/22: 0.4 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 0
|  | #N/A | 33/11 |  |  | 2018-03-01 | 23.9241 | - | - | M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0%
[6 empty] | 43160.7658 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 0
|  | #N/A | 33/11 |  |  | 2018-03-19 | 6.77 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0%
[5 empty] | (a) | 43178.7861 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 0
|  | #N/A | 33/11 |  |  | 2018-03-02 | 14.5252 | - | - | L | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0%
[6 empty] | 43161.5474 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 0
|  | #N/A | 33/11 |  |  | 2018-03-02 | 11.7772 | - | - | L | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0%
[6 empty] | 43161.7498 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 0
|  | #N/A | 33/11 |  |  | 2018-03-01 | 15.8703 | - | - | M | 0 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 |  | 0% | 0% | 0%
[6 empty] | 43160.7765 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections:; Average Cold Spell (ACS) (MVA) 2018/20: 0.425 |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 12.5172
|  | #N/A | 33/11 |  |  | 2018-02-07 | 17.9378 | - | - | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0% | 0% | 0%
[6 empty] | 43138.3546 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections:; Average Cold Spell (ACS) (MVA) 2018/21: #REF!; Average Cold Spell (ACS) (MVA) 2018/22: #REF! |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 2.5636
|  | #N/A | 33/11 |  |  | 2018-03-02 | 15.6548 | - | - | L | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0% | 0% | 0%
[6 empty] | 43161.4773 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections:; Average Cold Spell (ACS) (MVA) 2018/20: #REF! |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 0
|  | #N/A | 33/11 |  |  | 2018-02-21 | 4.092 | - | - | L | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0%
[6 empty] | 43152.3286 |  |  |  |  | Average Cold Spell (ACS) (MVA) 2018/19: Committed new connections: |  |  |  |  | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Generation at this s/stn: | [8 empty] | Average Cold Spell (ACS) (MVA) 2018/25: Generation at time of peak:; Average Cold Spell (ACS) (MVA) 2018/26: 0
Note on F8: SB31586: To be added with 33 kV TF CBs for CHHE and HUNS: (('CHHE~E7L5~AMPS~AI'+'BILS~E9L5~AMPS~AI'+'BILS~E10L5~AMPS~AI'+'BILS~E11L5~AMPS~AI')*1.732*11/1000) + (('OVPV~C1L5~AMPS~AI'+'DCPV~C1L5~AMPS~AI'+'HRPV~C1L5~AMPS~AI')*1.732*33/1000) Embedded with load and so should not be added- CHHE E5L5 (3.75 MW), ROSG E5L5 and E2L5 (5 + 3.3 MW), HUNS E6L5 (2 MW)
Note on K26: Beharrysingh, Shiva: Changed from high to medium growth rate - as previous years were either low or medium.

## GSP List
GSP | GSP Name | GSP NRN | Primary Nrn | Primary Name | GSP Name
ABNE | Abernethy | 241 | 241 | ABERNETHY GRID | Abernethy
ABNE | Abernethy | 241 | 242 | ABERNETHY | Abernethy
ABNE | Abernethy | 241 | 247 | HARBOUR | Abernethy
ABNE | Abernethy | 241 | 251 | MILNATHORT | Abernethy
ABNE | Abernethy | 241 | 252 | RUMBLING BRIDGE | Abernethy
ABNE | Abernethy | 241 | 254 | ERROL | Abernethy
ABNE | Abernethy | 241 | 255 | BALBEGGIE | Abernethy
ABNE | Abernethy | 241 | 271 | SCONE | Abernethy
ABNE | Abernethy | 241 | 273 | GLENDEVON | Abernethy
ABNE | Abernethy | 241 | 279 | BRIDGE OF EARN | Abernethy
ABNE | Abernethy | 241 | 284 | BINN HILL LANDFILL | Abernethy
ALNE | Alness | 502 | 502 | ALNESS GRID | Alness
ALNE | Alness | 502 | 522 | GLASTULLICH | Alness
ALNE | Alness | 502 | 541 | CONTULLICH | Alness
ALNE | Alness | 502 | 546 | TAIN | Alness
ALNE | Alness | 502 | 551 | CROSSHILLS | Alness
ALNE | Alness | 502 | 552 | BALALDIE | Alness
ALNE | Alness | 502 | 553 | PEDDIESTON | Alness
ALNE | Alness | 502 | 554 | NIGG | Alness
ALNE | Alness | 502 | 559 | INVERGORDON | Alness
ALNE | Alness | 502 | 576 | LEALTY | Alness
ANSU | AN SUIDHE | 353 | 353 | AN SUIDHE GRID | AN SUIDHE
ARBR | Arbroath | 61 | 61 | ARBROATH GRID | Arbroath
ARBR | Arbroath | 61 | 62 | CHARLES AVENUE | Arbroath
ARBR | Arbroath | 61 | 64 | CARNOUSTIE | Arbroath
ARBR | Arbroath | 61 | 66 | REDFORD | Arbroath
ARBR | Arbroath | 61 | 67 | HUME STREET | Arbroath
ARBR | Arbroath | 61 | 68 | ELLIOT DEPOT | Arbroath
ARDK | Ardkinglas | 354 | 354 | BUNARKAIG | Ardkinglas
ARMO |  | 622 | 622 | ARDMORE GRID
ARMO | 0 | 622 | 644 | DRIMORE | 0
ARMO | 0 | 622 | 645 | STORNOWAY GRID | 0
ARMO | 0 | 622 | 647 | HARRIS GRID | 0
ARMO | 0 | 622 | 648 | GISLA | 0
ARMO | 0 | 622 | 650 | MAARUIG | 0
ARMO | 0 | 622 | 651 | BARVAS | 0
ARMO | 0 | 622 | 652 | BATTERY POINT | 0
ARMO | 0 | 622 | 653 | CLACHAN | 0
ARMO | 0 | 622 | 657 | LAXAY | 0
ARMO | 0 | 622 | 658 | STOCKINISH | 0
ARMO | 0 | 622 | 659 | BARRA G S | 0
ARMO | 0 | 622 | 660 | POLLACHAR | 0
ARMO | 0 | 622 | 662 | TARBERT | 0
ARMO | 0 | 622 | 663 | FROBOST REGULATOR | 0
ARMO | 0 | 622 | 664 | RODIL PMR | 0
ARMO | 0 | 622 | 665 | LOCH CARNAN | 0
ARMO | 0 | 622 | 666 | EOLIGARRY PMR | 0
ARMO | 0 | 622 | 667 | NORTHBAY PMR | 0
ARMO | 0 | 622 | 669 | ARNISH | 0
ARMO | 0 | 622 | 670 | CALLANISH | 0
ARMO | 0 | 622 | 671 | AIRD | 0
ARMO | 0 | 622 | 672 | COLL | 0
BEAU | Beauly | 506 | 501 | AIGAS | Beauly
BEAU | Beauly | 506 | 506 | BEAULY GRID | Beauly
BEAU | Beauly | 506 | 509 | BLACKSTAND | Beauly
BEAU | Beauly | 506 | 513 | CONON BRIDGE | Beauly
BEAU | Beauly | 506 | 515 | DINGWALL | Beauly
BEAU | Beauly | 506 | 520 | KILTARLITY | Beauly
BEAU | Beauly | 506 | 538 | MARYBANK | Beauly
BEAU | Beauly | 506 | 542 | MUIREND | Beauly
BEAU | Beauly | 506 | 547 | MUIR OF ORD | Beauly
BEAU | Beauly | 506 | 558 | NORTH KESSOCK | Beauly
BERB | Berryburn | 893 | 893 | BERRYBURN GRID | Berryburn
BOAG | Boat of Garten | 707 | 704 | AVIEMORE | Boat of Garten
BOAG | Boat of Garten | 707 | 706 | BALLINDALLOCH | Boat of Garten
BOAG | Boat of Garten | 707 | 707 | BOAT OF GARTEN GRID | Boat of Garten
BOAG | Boat of Garten | 707 | 708 | BOAT OF GARTEN 11 kV | Boat of Garten
BOAG | Boat of Garten | 707 | 722 | GRANTOWN | Boat of Garten
BOAG | Boat of Garten | 707 | 727 | KINGUSSIE | Boat of Garten
BOAG | Boat of Garten | 707 | 738 | TOMATIN | Boat of Garten
BOAG | Boat of Garten | 707 | 777 | DALWHINNIE | Boat of Garten
BRAC | Braco | 201 | 201 | BRACO GRID | Braco
BRAC | Braco | 201 | 207 | GLENEAGLES | Braco
BRAC | Braco | 201 | 208 | CRIEFF | Braco
BRAC | Braco | 201 | 209 | DUNBLANE | Braco
BRAC | Braco | 201 | 210 | CALLANDER | Braco
BRAC | Braco | 201 | 211 | KIPPEN | Braco
BRAC | Braco | 201 | 253 | FORTEVIOT | Braco
BRCW2 | Braco West | 290 | 290 | BRACO WEST GRID | Braco West
BRID | Bridge of Dun | 71 | 71 | BRIDGE OF DUN GRID | Bridge of Dun
BRID | Bridge of Dun | 71 | 72 | BRIDGE OF DUN 11kV | Bridge of Dun
BRID | Bridge of Dun | 71 | 73 | BRECHIN | Bridge of Dun
BRID | Bridge of Dun | 71 | 74 | MONTROSE NORTH | Bridge of Dun
BRID | Bridge of Dun | 71 | 75 | MILL RD MONTROSE | Bridge of Dun
BRID | Bridge of Dun | 71 | 76 | INCHBARE | Bridge of Dun
BRID | Bridge of Dun | 71 | 77 | LOGIE PERT | Bridge of Dun
BRID | Bridge of Dun | 71 | 78 | x Use in T&C - CHECK DEPO | Bridge of Dun
BRID | Bridge of Dun | 71 | 278 | x Use in T&C - CHECK DEPO | Bridge of Dun
BRID | Bridge of Dun | 71 | 281 | x Use in T&C - CHECK DEPO | Bridge of Dun
BRID | Bridge of Dun | 71 | 952 | ST CYRUS | Bridge of Dun
BROA | Broadford | 627 | 623 | LOWER OLLACH | Broadford
BROA | Broadford | 627 | 624 | ACHINTEE | Broadford
BROA | Broadford | 627 | 627 | BROADFORD GRID | Broadford
BROA | Broadford | 627 | 633 | KISHORNHILL | Broadford
BROA | Broadford | 627 | 634 | KYLE | Broadford
BROA | Broadford | 627 | 636 | NOSTIE BRIDGE | Broadford
BROA | Broadford | 627 | 637 | BROADFORD | Broadford
BROA | Broadford | 627 | 639 | SKULAMUS | Broadford
BROA | Broadford | 627 | 641 | SHIELDAIG | Broadford
BROR | Brora | 510 | 510 | BRORA GRID | Brora
BROR | Brora | 510 | 524 | BENBRAGGIE MAST | Brora
BROR | Brora | 510 | 525 | GOLSPIE | Brora
BROR | Brora | 510 | 550 | BRORA | Brora
BROR | Brora | 510 | 557 | DORNOCH | Brora
BROR | Brora | 510 | 560 | HELMSDALE | Brora
BUMU | Burghmuir | 245 | 245 | BURGHMUIR GRID | Burghmuir
BUMU | Burghmuir | 245 | 246 | BURGHMUIR | Burghmuir
BUMU | Burghmuir | 245 | 248 | THIMBLEROW | Burghmuir
BUMU | Burghmuir | 245 | 249 | GOODLYBURN | Burghmuir
BUMU | Burghmuir | 245 | 270 | REDGORTON | Burghmuir
BUMU | Burghmuir | 245 | 272 | NORTH MUIRTON | Burghmuir
CAAD | Carradale | 302 | 302 | CARRADALE GRID | Carradale
CAAD | Carradale | 302 | 312 | CAMPBELTOWN | Carradale
CAAD | Carradale | 302 | 318 | BALLURE | Carradale
CAAD | Carradale | 302 | 336 | DIPPEN | Carradale
CAAD | Carradale | 302 | 338 | CLAONAIG | Carradale
CAAD | Carradale | 302 | 349 | WESTPARK FERGUS | Carradale
CAAD | Carradale | 302 | 370 | BRODICK | Carradale
CAAD | Carradale | 302 | 371 | WHITING BAY | Carradale
CAAD | Carradale | 302 | 372 | BALLIEKINE | Carradale
CAAD | Carradale | 302 | 373 | MACHRIE | Carradale
CASS | Cassley | 512 | 511 | CANNICH | Cassley
CASS | Cassley | 512 | 512 | CASSLEY GRID | Cassley
CASS | Cassley | 512 | 544 | RHICONICH | Cassley
CASS | Cassley | 512 | 563 | OVERSCAIG | Cassley
CEAN | Ceannacroc | 711 | 711 | CEANNACROC GRID | Ceannacroc
CHAR | Charleston | 1 | 1 | CHARLESTON GRID | Charleston
CHAR | Charleston | 1 | 2 | CHARLESTON | Charleston
CHAR | Charleston | 1 | 3 | MENZIESHILL | Charleston
CHAR | Charleston | 1 | 4 | GOURDIE | Charleston
CHAR | Charleston | 1 | 5 | BUTTARS LOAN | Charleston
CHAR | Charleston | 1 | 6 | NINEWELLS | Charleston
CLAC | Clachan | 311 | 311 | CLACHAN GRID | Clachan
CLAC | Clachan | 311 | 321 | INVERARAY | Clachan
CLAC | Clachan | 311 | 369 | LOCHGOILHEAD | Clachan
CLAC | Clachan | 311 | 382 | STRACHUR | Clachan
CLAC | Clachan | 311 | 387 | BUTTERBRIDGE | Clachan
CLAC | Clachan | 311 | 388 | DOUGLAS PIER | Clachan
CLAY | Clayhills | 823 | 808 | BALNAGASK | Clayhills
CLAY | Clayhills | 823 | 823 | CLAYHILLS GRID | Clayhills
CLAY | Clayhills | 823 | 826 | CLAYHILLS | Clayhills
CLAY | Clayhills | 823 | 827 | COMMERCE STREET | Clayhills
CLAY | Clayhills | 823 | 832 | CRAIGINCHES | Clayhills
COUA | Coupar Angus | 243 | 90 | LEOCH | Coupar Angus
COUA | Coupar Angus | 243 | 243 | COUPAR ANGUS GRID | Coupar Angus
COUA | Coupar Angus | 243 | 244 | COUPAR ANGUS | Coupar Angus
COUA | Coupar Angus | 243 | 256 | CAPUTH | Coupar Angus
COUA | Coupar Angus | 243 | 257 | BLAIRGOWRIE | Coupar Angus
COUA | Coupar Angus | 243 | 258 | ALYTH | Coupar Angus
COUA | Coupar Angus | 243 | 259 | DALRULZION | Coupar Angus
CRAI | Craigiebuckler | 829 | 829 | CRAIGIEBUCKLER GRID | Craigiebuckler
CRAI | Craigiebuckler | 829 | 830 | CRAIGIEBUCKLER | Craigiebuckler
CRAI | Craigiebuckler | 829 | 834 | CRAIGTON | Craigiebuckler
CRAI | Craigiebuckler | 829 | 836 | CULTER | Craigiebuckler
CRAI | Craigiebuckler | 829 | 939 | RUTHRIESTON | Craigiebuckler
DAAS | Dallas | 473 | 473 | DALLAS | Dallas
DOUN1 | Dounreay | 598 | 598 | DOUNREAY | Dounreay
DUDH | Dudhope | 31 | 31 | DUDHOPE GRID | Dudhope
DUDH | Dudhope | 31 | 32 | CONSTABLE STREET | Dudhope
DUDH | Dudhope | 31 | 33 | ROSEBANK STREET | Dudhope
DUDH | Dudhope | 31 | 595 | DUNBEATH GRID | Dudhope
DUGR | 0 | 638 | 629 | DRYNOCH | 0
DUGR | 0 | 638 | 632 | PORTREE | 0
DUGR | 0 | 638 | 638 | DUNVEGAN GRID | 0
DUGR | 0 | 638 | 640 | UIG | 0
DUNO | Dunoon | 380 | 362 | ROTHESAY | Dunoon
DUNO | Dunoon | 380 | 363 | DUNOON | Dunoon
DUNO | Dunoon | 380 | 364 | SANDBANK | Dunoon
DUNO | Dunoon | 380 | 365 | BRUCHAG | Dunoon
DUNO | Dunoon | 380 | 366 | KAMES | Dunoon
DUNO | Dunoon | 380 | 375 | OTTER FERRY | Dunoon
DUNO | Dunoon | 380 | 376 | ARDYNE POINT | Dunoon
DUNO | Dunoon | 380 | 379 | INNELLAN | Dunoon
DUNO | Dunoon | 380 | 380 | DUNOON GRID | Dunoon
DUNO | Dunoon | 380 | 383 | GLENDARUEL | Dunoon
DUNO | Dunoon | 380 | 384 | NEWTON | Dunoon
DUNO | Dunoon | 380 | 385 | COLINTRAIVE | Dunoon
DYCE | Dyce | 843 | 807 | BALMEDIE | Dyce
DYCE | Dyce | 843 | 843 | DYCE GRID | Dyce
DYCE | Dyce | 843 | 844 | DYCE NORTH | Dyce
DYCE | Dyce | 843 | 849 | ELLON 11 kV | Dyce
DYCE | Dyce | 843 | 884 | KINGSEAT | Dyce
DYCE | Dyce | 843 | 947 | STONEYWOOD T3 | Dyce
EDIN | 0 | 0 | 355 | EDINBANE GRID | 0
ELGI | Elgin | 456 | 453 | KINLOSS | Elgin
ELGI | Elgin | 456 | 454 | BURGHEAD | Elgin
ELGI | Elgin | 456 | 455 | LOSSIEMOUTH | Elgin
ELGI | Elgin | 456 | 456 | ELGIN GRID | Elgin
ELGI | Elgin | 456 | 457 | CUMMING STREET | Elgin
ELGI | Elgin | 456 | 458 | ASHGROVE | Elgin
ELGI | Elgin | 456 | 482 | ELGIN | Elgin
ELGI | Elgin | 456 | 487 | FOCHABERS | Elgin
ELGI | Elgin | 456 | 488 | LHANBRYDE | Elgin
ELGI | Elgin | 456 | 499 | BILBOHALL | Elgin
FAAR | 0 | 0 | 503 | FARR | 0
FASN | Fasnakyle | 521 | 519 | FASNAKYLE PRIMARY | Fasnakyle
FASN | Fasnakyle | 521 | 521 | FASNAKYLE GRID | Fasnakyle
FAUG | Fort Augustus | 716 | 396 | GLEN LAOGH | Fort Augustus
FAUG | Fort Augustus | 716 | 517 | DRUMNADROCHIT | Fort Augustus
FAUG | Fort Augustus | 716 | 709 | FARR GRID | Fort Augustus
FAUG | Fort Augustus | 716 | 710 | ABERCHALDER | Fort Augustus
FAUG | Fort Augustus | 716 | 716 | FORT AUGUSTUS GRID | Fort Augustus
FAUG | Fort Augustus | 716 | 742 | MARKETHILL | Fort Augustus
FAUG | Fort Augustus | 716 | 745 | BUNOICH | Fort Augustus
FAUG | Fort Augustus | 716 | 766 | INVERGARRY | Fort Augustus
FAUG | Fort Augustus | 716 | 781 | GLENDOE PRIMARY | Fort Augustus
FETT | Fetteresso | 989 | 989 | FETTERSSO GRID | Fetteresso
FIDD | Fiddes | 851 | 847 | EDZELL | Fiddes
FIDD | Fiddes | 851 | 851 | FIDDES | Fiddes
FIDD | Fiddes | 851 | 873 | INVERBERVIE | Fiddes
FIDD | Fiddes | 851 | 890 | LAURENCEKIRK | Fiddes
FIDD | Fiddes | 851 | 945 | STONEHAVEN | Fiddes
FRAS | Fraserburgh | 853 | 821 | CAIRNBULG | Fraserburgh
FRAS | Fraserburgh | 853 | 853 | FRASERBURGH GRID | Fraserburgh
FRAS | Fraserburgh | 853 | 854 | FRASERBURGH | Fraserburgh
FWIL | Fort William | 715 | 395 | FISHNISH | Fort William
FWIL | Fort William | 715 | 702 | ANNAT | Fort William
FWIL | Fort William | 715 | 714 | GLENSANDA | Fort William
FWIL | Fort William | 715 | 715 | FORT WILLIAM GRID | Fort William
FWIL | Fort William | 715 | 720 | DAILBEG | Fort William
FWIL | Fort William | 715 | 721 | LIDDESDALE | Fort William
FWIL | Fort William | 715 | 724 | INVERLOCHY | Fort William
FWIL | Fort William | 715 | 730 | LOCHAILORT REGULATOR | Fort William
FWIL | Fort William | 715 | 731 | MALLAIG | Fort William
FWIL | Fort William | 715 | 732 | RAHOY | Fort William
FWIL | Fort William | 715 | 734 | PINEGROVE | Fort William
FWIL | Fort William | 715 | 740 | ARISAIG | Fort William
FWIL | Fort William | 715 | 744 | CORRAN | Fort William
FWIL | Fort William | 715 | 747 | LOCHALINE | Fort William
FWIL | Fort William | 715 | 749 | SALEN 2 | Fort William
FWIL | Fort William | 715 | 751 | STRONTIAN | Fort William
FWIL | Fort William | 715 | 753 | POOR HOUSE | Fort William
FWIL | Fort William | 715 | 754 | KINLOCHMOIDART | Fort William
FWIL | Fort William | 715 | 755 | SHONA BEAG | Fort William
FWIL | Fort William | 715 | 756 | GLENUIG | Fort William
FWIL | Fort William | 715 | 771 | KINGAIRLOCH | Fort William
FWIL | Fort William | 715 | 782 | CARNOCH REGULATOR | Fort William
GLAG | Glenagnes | 21 | 21 | GLENAGNES GRID | Glenagnes
GLAG | Glenagnes | 21 | 24 | OVERGATE | Glenagnes
GLAG | Glenagnes | 21 | 25 | WALTON | Glenagnes
GRIF | 0 | 0 | 287 | GRIFFIN WINDFARM | 0
GRUB | Grudie Bridge | 526 | 504 | AULTBEA | Grudie Bridge
GRUB | Grudie Bridge | 526 | 505 | ACHILTIBUIE | Grudie Bridge
GRUB | Grudie Bridge | 526 | 507 | LETTEREWE | Grudie Bridge
GRUB | Grudie Bridge | 526 | 514 | CONON FALLS | Grudie Bridge
GRUB | Grudie Bridge | 526 | 518 | DRUMRUNIE | Grudie Bridge
GRUB | Grudie Bridge | 526 | 526 | GRUDIE BRIDGE | Grudie Bridge
GRUB | Grudie Bridge | 526 | 527 | INVERBROOM | Grudie Bridge
GRUB | Grudie Bridge | 526 | 531 | KERRY FALLS | Grudie Bridge
GRUB | Grudie Bridge | 526 | 532 | KINLOCHEWE | Grudie Bridge
GRUB | Grudie Bridge | 526 | 535 | BIDEN CLAN RAONAILD | Grudie Bridge
GRUB | Grudie Bridge | 526 | 549 | ULLAPOOL | Grudie Bridge
GRUB | Grudie Bridge | 526 | 556 | LOCHINVER | Grudie Bridge
GRUB | Grudie Bridge | 526 | 562 | COMRIE | Grudie Bridge
GRUB | Grudie Bridge | 526 | 564 | MINOR GRUDIE | Grudie Bridge
GRUB | Grudie Bridge | 526 | 567 | GARBAT FOREST | Grudie Bridge
GRUB | Grudie Bridge | 526 | 568 | LOCH GLASCARNOCH | Grudie Bridge
GRUB | Grudie Bridge | 526 | 569 | GARVE | Grudie Bridge
GRUB | Grudie Bridge | 526 | 573 | CUILEIG POWER STATION | Grudie Bridge
GRUB | Grudie Bridge | 526 | 798 | ACHNASHEEN | Grudie Bridge
GRUB | Grudie Bridge | 526 | 799 | LOCH DUBH P S | Grudie Bridge
INNE | Inverness | 725 | 712 | CULLODEN | Inverness
INNE | Inverness | 725 | 713 | DALNEIGH | Inverness
INNE | Inverness | 725 | 718 | FOYERS | Inverness
INNE | Inverness | 725 | 725 | INVERNESS GRID | Inverness
INNE | Inverness | 725 | 726 | INVERNESS 11 kV | Inverness
INNE | Inverness | 725 | 735 | RAIGMORE | Inverness
INNE | Inverness | 725 | 741 | WATERLOO PLACE | Inverness
INNE | Inverness | 725 | 750 | HILTON | Inverness
INNE | Inverness | 725 | 757 | INVERARNIE | Inverness
INNE | Inverness | 725 | 761 | ERROGIE | Inverness
INNE | Inverness | 725 | 763 | WESTER DRUMMOND | Inverness
KEIT | Keith | 463 | 401 | MARNOCH | Keith
MACD | #N/A | 405 | 405 | MACDUFF | #N/A
MACD | #N/A | 405 | 406 | MACDUFF NEW | #N/A
KEIT | Keith | 463 | 435 | PORTSOY | Keith
KEIT | Keith | 463 | 459 | ROTHES | Keith
KEIT | Keith | 463 | 460 | ABERLOUR | Keith
KEIT | Keith | 463 | 461 | DUFFTOWN | Keith
KEIT | Keith | 463 | 462 | BUCKIE | Keith
KEIT | Keith | 463 | 463 | KEITH GRID | Keith
KEIT | Keith | 463 | 464 | KEITH | Keith
KEIT | Keith | 463 | 465 | LIMEHILLOCKS | Keith
KEIT | Keith | 463 | 469 | CULLEN | Keith
KEIT | Keith | 463 | 869 | HUNTLY | Keith
KEIT | Keith | 463 | 871 | INSCH | Keith
KEIT | Keith | 463 | 964 | TURRIFF | Keith
KIIN | Killin | 214 | 214 | KILLIN GRID | Killin
KIIN | Killin | 214 | 217 | LOCHEARNHEAD | Killin
KIIN | Killin | 214 | 219 | KILLIN TOWN | Killin
KIIN | Killin | 214 | 221 | LUBNAIG | Killin
KIIN | Killin | 214 | 269 | CASHLIE | Killin
KILO | Kinlochleven | 729 | 330 | GLENCOE | Kinlochleven
KILO | Kinlochleven | 729 | 729 | KINLOCHLEVEN | Kinlochleven
KINT | Kintore | 887 | 810 | BANCHORY | Kintore
KINT | Kintore | 887 | 856 | FYVIE | Kintore
KINT | Kintore | 887 | 875 | INVERURIE | Kintore
KINT | Kintore | 887 | 881 | KEMNAY | Kintore
KINT | Kintore | 887 | 886 | KINTORE SUPERGRID | Kintore
KINT | Kintore | 887 | 887 | KINTORE GRID | Kintore
KINT | Kintore | 887 | 903 | METHLICK | Kintore
KINT | Kintore | 887 | 907 | MIDMAR | Kintore
KINT | Kintore | 887 | 921 | OLDMELDRUM | Kintore
KINT | Kintore | 887 | 923 | PARK | Kintore
KINT | Kintore | 887 | 941 | SKENE | Kintore
KINT | Kintore | 887 | 962 | TORRYBURN | Kintore
LAIR | Lairg | 534 | 534 | LAIRG GRID | Lairg
LAIR | Lairg | 534 | 540 | TORBOLL | Lairg
LAIR | Lairg | 534 | 548 | TRESSADY | Lairg
LUNA | Lunanhead | 81 | 81 | LUNANHEAD GRID | Lunanhead
LUNA | Lunanhead | 81 | 82 | LUNANHEAD | Lunanhead
LUNA | Lunanhead | 81 | 83 | LOCHSIDE | Lunanhead
LUNA | Lunanhead | 81 | 84 | MARYTON | Lunanhead
LUNA | Lunanhead | 81 | 87 | INVERARITY | Lunanhead
LUNA | Lunanhead | 81 | 89 | FRIOCKHEIM | Lunanhead
LYND | Lyndhurst | 11 | 11 | LYNDHURST GRID | Lyndhurst
LYND | Lyndhurst | 11 | 12 | LYNDHURST | Lyndhurst
LYND | Lyndhurst | 11 | 13 | LOCHEE | Lyndhurst
LYND | Lyndhurst | 11 | 14 | MACALPINE ROAD | Lyndhurst
LYND | Lyndhurst | 11 | 15 | WEST KIRKTON | Lyndhurst
MACD | MacDuff | 405 | 405 | MACDUFF | MacDuff
MILC | Milton of Craigie | 51 | 51 | MILTON OF CRAIGIE GRID | Milton of Craigie
MILC | Milton of Craigie | 51 | 52 | MILTON OF CRAIGIE | Milton of Craigie
MILC | Milton of Craigie | 51 | 53 | OLD CRAIGIE ROAD | Milton of Craigie
MILC | Milton of Craigie | 51 | 54 | LONGHAUGH | Milton of Craigie
MILC | Milton of Craigie | 51 | 55 | ASHLUDIE | Milton of Craigie
MILC | Milton of Craigie | 51 | 56 | BALDOVIE | Milton of Craigie
MILC | Milton of Craigie | 51 | 57 | BROUGHTY FERRY | Milton of Craigie
MILC | Milton of Craigie | 51 | 58 | EDZELL STREET | Milton of Craigie
MILW | 0 | 352 | 352 | MILLENNIUM WIND GRID | 0
MILW | 0 | 0 | 356 | MILLENNIUM WINDFARM AUX | 0
MILW | 0 | 0 | 728 | MILLENNIUM WINDFARM AUX | 0
MYBS | Mybster | 586 | 581 | COLDBACKIE | Mybster
MYBS | Mybster | 586 | 584 | LATHERON | Mybster
MYBS | Mybster | 586 | 586 | MYBSTER GRID | Mybster
MYBS | Mybster | 586 | 590 | MELVICH | Mybster
MYBS | Mybster | 586 | 591 | BETTYHILL | Mybster
MYBS | Mybster | 586 | 594 | WICK | Mybster
NAIR | Nairn | 733 | 452 | FORRES | Nairn
NAIR | Nairn | 733 | 703 | LETHEN | Nairn
NAIR | Nairn | 733 | 723 | NAIRN CENTRAL | Nairn
NAIR | Nairn | 733 | 733 | NAIRN GRID | Nairn
NAIR | Nairn | 733 | 752 | DALCROSS | Nairn
NAIR | Nairn | 733 | 779 | ARDERSIER | Nairn
ORRI | Orrin | 565 | 565 | ORRIN | Orrin
PAUH | 0 | 0 | 474 | GLENFARCLAS | 0
PEHG | Peterhead Grange | 927 | 927 | PETERHEAD GRANGE 33kV | Peterhead Grange
PEHG | Peterhead Grange | 927 | 928 | PETERHEAD GRANGE 11kV | Peterhead Grange
PEHG | Peterhead Grange | 927 | 929 | PHEAD NORTH ST | Peterhead Grange
PEHS | Peterhead Shell | 926 | 926 | PETERHEAD SHELL | Peterhead Shell
PERS | Persley | 925 | 475 | STONEYHILL | Persley
PERS | Persley | 925 | 476 | STONEYHILL BIOMASS | Persley
PERS | Persley | 925 | 814 | BRIDGE OF DON | Persley
PERS | Persley | 925 | 865 | HAUDAGAIN | Persley
PERS | Persley | 925 | 912 | MUGIEMOSS MILLS | Persley
PERS | Persley | 925 | 917 | NORTHFIELD | Persley
PERS | Persley | 925 | 924 | PERSLEY SUPERGRID | Persley
PERS | Persley | 925 | 925 | PERSLEY GRID | Persley
PERS | Persley | 925 | 947 | STONEYWOOD T1&T2 | Persley
PERS | Persley | 925 | 956 | ST MACHAR | Persley
PERS | Persley | 925 | 982 | WHITESTRIPES | Persley
PORA | Port Ann | 301 | 301 | PORT ANN GRID | Port Ann
PORA | Port Ann | 301 | 305 | CRINAN | Port Ann
PORA | Port Ann | 301 | 308 | LOCHGILPHEAD | Port Ann
PORA | Port Ann | 301 | 309 | INVERNEIL | Port Ann
PORA | Port Ann | 301 | 310 | TARBERT LOCH FYNE | Port Ann
PORA | Port Ann | 301 | 313 | BOWMORE | Port Ann
#N/A | #N/A | #N/A | 319 | AIRIGH-NA-BRODAIG | #N/A
PORA | Port Ann | 301 | 331 | PORT ELLEN | Port Ann
PORA | Port Ann | 301 | 332 | FURNACE QUARRY | Port Ann
PORA | Port Ann | 301 | 334 | PORT ASKAIG | Port Ann
PORA | Port Ann | 301 | 339 | LUSSAGIVEN | Port Ann
PORA | Port Ann | 301 | 341 | TARBERT JURA | Port Ann
PORA | Port Ann | 301 | 391 | TAYVALLICH | Port Ann
PORA | Port Ann | 301 | 397 | STONEFIELD | Port Ann
#N/A | #N/A | #N/A | 748 | QUOICH PRIMARY | #N/A
RANN | Rannoch | 261 | 218 | TYNDRUM | Rannoch
RANN | Rannoch | 261 | 261 | RANNOCH GRID | Rannoch
RANN | Rannoch | 261 | 274 | BRIDGE OF GAUR | Rannoch
RANN | Rannoch | 261 | 343 | BLACKMOUNT | Rannoch
RANN | Rannoch | 261 | 345 | GLENETIVE | Rannoch
REDM | Redmoss | 934 | 813 | BP NETHERLEY | Redmoss
REDM | Redmoss | 934 | 882 | KINCORTH | Redmoss
REDM | Redmoss | 934 | 915 | NEWTONHILL | Redmoss
REDM | Redmoss | 934 | 934 | REDMOSS GRID | Redmoss
REDM | Redmoss | 934 | 935 | REDMOSS | Redmoss
SFEG | St Fergus Gas | 955 | 955 | ST FERGUS GAS TERM | St Fergus Gas
SFER | 0 | 0 | 957 | ST FERGUS VSD | 0
SFIL | St Fillans | 213 | 212 | DALCHONZIE | St Fillans
SFIL | St Fillans | 213 | 213 | ST FILLANS P S | St Fillans
SHIN | Shin | 545 | 523 | GLEDFIELD | Shin
SHIN | Shin | 545 | 536 | SHIN | Shin
SHIN | Shin | 545 | 545 | SHIN GRID | Shin
SLOY | Sloy | 367 | 139 | SLOY POWER STATION | Sloy
SLOY | Sloy | 367 | 367 | SLOY GRID | Sloy
SLOY | Sloy | 367 | 377 | ARROCHAR | Sloy
STHA | 0 | 0 | 202 | STRATHLEVEN | 0
STHA | 0 | 0 | 203 | DRYMEN | 0
STHA | 0 | 0 | 204 | KILLEARN | 0
STHA | 0 | 0 | 205 | KEPCULLOCH | 0
STHA | 0 | 0 | 206 | ABERFOYLE | 0
STHA | 0 | 0 | 220 | BLAIRLINNANS | 0
STHA | 0 | 0 | 239 | ROSS PRIORY PUMPING STAT. | 0
STHA | 0 | 0 | 285 | AUCHENCARROCH | 0
STRB | 0 | 0 | 580 | STRATHBRORA | 0
STRI | Strichen | 949 | 812 | BODDAM | Strichen
STRI | Strichen | 949 | 863 | HATTON | Strichen
STRI | Strichen | 949 | 901 | MAUD | Strichen
STRI | Strichen | 949 | 909 | MINTLAW | Strichen
STRI | Strichen | 949 | 913 | NEW PITSLIGO | Strichen
STRI | Strichen | 949 | 949 | STRICHEN GRID | Strichen
STRI | Strichen | 949 | 950 | STRICHEN | Strichen
TARL | Tarland | 470 | 470 | TARLAND GRID | Tarland
TARL | Tarland | 470 | 801 | ABOYNE | Tarland
TARL | Tarland | 470 | 806 | BALLATER | Tarland
TARL | Tarland | 470 | 911 | MOSSAT | Tarland
TARL | Tarland | 470 | 951 | STRATHDON | Tarland
TARL | Tarland | 470 | 981 | WHITEHOUSE | Tarland
TAYN | Taynuilt | 303 | 303 | TAYNUILT GRID | Taynuilt
TAYN | Taynuilt | 303 | 304 | KILMELFORD PS | Taynuilt
TAYN | Taynuilt | 303 | 306 | CONNEL | Taynuilt
TAYN | Taynuilt | 303 | 307 | OBAN | Taynuilt
TAYN | Taynuilt | 303 | 314 | TIREE | Taynuilt
TAYN | Taynuilt | 303 | 315 | SALEN | Taynuilt
TAYN | Taynuilt | 303 | 316 | STRAND REGULATOR | Taynuilt
TAYN | Taynuilt | 303 | 317 | LOCHDONHEAD | Taynuilt
TAYN | Taynuilt | 303 | 322 | KILNINVER | Taynuilt
TAYN | Taynuilt | 303 | 323 | KILCHRENAN | Taynuilt
TAYN | Taynuilt | 303 | 324 | EREDINE | Taynuilt
TAYN | Taynuilt | 303 | 327 | BARCALDINE | Taynuilt
TAYN | Taynuilt | 303 | 328 | BONAWE | Taynuilt
TAYN | Taynuilt | 303 | 329 | KENMORE | Taynuilt
TAYN | Taynuilt | 303 | 333 | KINLOCH | Taynuilt
TAYN | Taynuilt | 303 | 335 | KERRERA | Taynuilt
TAYN | Taynuilt | 303 | 340 | SCAMMADALE | Taynuilt
TAYN | Taynuilt | 303 | 342 | TIRORAN BRIDGE | Taynuilt
TAYN | Taynuilt | 303 | 344 | ARDTUN REGULATOR | Taynuilt
TAYN | Taynuilt | 303 | 346 | DERVAIG | Taynuilt
TAYN | Taynuilt | 303 | 347 | TAYNUILT | Taynuilt
TAYN | Taynuilt | 303 | 348 | DALMALLY | Taynuilt
TAYN | Taynuilt | 303 | 351 | BLARGHOUR | Taynuilt
TAYN | Taynuilt | 303 | 381 | CRAIGAGOUL | Taynuilt
TAYN | Taynuilt | 303 | 394 | BEOCHLICH | Taynuilt
THSO | Thurso | 592 | 489 | RACKWICK PRIMARY | Thurso
THSO | Thurso | 592 | 492 | EDAY TIDAL STREAM | Thurso
THSO | Thurso | 592 | 498 | ROUSAY | Thurso
THSO | Thurso | 592 | 571 | LAREL | Thurso
THSO | Thurso | 592 | 582 | HASTIGROW | Thurso
THSO | Thurso | 592 | 583 | FORSS | Thurso
THSO | Thurso | 592 | 585 | MOUNT PLEASANT | Thurso
THSO | Thurso | 592 | 587 | ORMLIE | Thurso
THSO | Thurso | 592 | 592 | THURSO GRID | Thurso
THSO | Thurso | 592 | 597 | HALKIRK | Thurso
THSO | Thurso | 592 | 673 | SCORRADALE | Thurso
THSO | Thurso | 592 | 674 | WESTRAY | Thurso
THSO | Thurso | 592 | 675 | EDAY | Thurso
THSO | Thurso | 592 | 677 | KIRKWALL | Thurso
THSO | Thurso | 592 | 678 | STROMNESS | Thurso
THSO | Thurso | 592 | 679 | ST MARYS | Thurso
THSO | Thurso | 592 | 680 | FLOTTA | Thurso
THSO | Thurso | 592 | 681 | NORTH HOY | Thurso
THSO | Thurso | 592 | 682 | LYNESS | Thurso
THSO | Thurso | 592 | 683 | SHAPINSAY | Thurso
THSO | Thurso | 592 | 684 | STRONSAY | Thurso
THSO | Thurso | 592 | 685 | SANDAY | Thurso
THSO | Thurso | 592 | 701 | BURGARHILL | Thurso
TORA | 0 | 0 | 508 | TORR ACHILTY | 0
TUMB | Tummel Bridge | 260 | 260 | TUMMEL BRIDGE GRID | Tummel Bridge
TUMB | Tummel Bridge | 260 | 262 | KINLOCH RANNOCH | Tummel Bridge
TUMB | Tummel Bridge | 260 | 263 | PITLOCHRY | Tummel Bridge
TUMB | Tummel Bridge | 260 | 265 | CALVINE | Tummel Bridge
TUMB | Tummel Bridge | 260 | 266 | BONSKEID | Tummel Bridge
TUMB | Tummel Bridge | 260 | 267 | ABERFELDY | Tummel Bridge
TUMB | Tummel Bridge | 260 | 268 | COSHIEVILLE | Tummel Bridge
TUMB | Tummel Bridge | 260 | 276 | FINCASTLE | Tummel Bridge
WIOW | Willowdale | 983 | 841 | DENBURN | Willowdale
WIOW | Willowdale | 983 | 861 | GREYFRIARS | Willowdale
WIOW | Willowdale | 983 | 867 | HAYTON | Willowdale
WIOW | Willowdale | 983 | 958 | ST NICHOLAS | Willowdale
WIOW | Willowdale | 983 | 983 | WILLOWDALE | Willowdale
WOHI | 0 | 0 | 932 | QUEENS LANE NORTH | 0
WOHI | 0 | 0 | 943 | SPRINGHILL | 0
WOHI | 0 | 0 | 985 | WOODHILL GRID | 0
WOHI | 0 | 0 | 986 | WOODHILL | 0
|  |  | 240 | INVERALMOND

## 1718
NRN | MD
252 | 0
710 | 0.07
267 | 3.6876
206 | 2.3525
460 | 5.3524
242 | 3.08
0.06
801 | 6.54
505 | 0.55
624 | 0.08
501 | 0.3
671 | 2.92
35 | 0.08
0.4
258 | 2.77 | 2.44 | 2.0786 | 2.328
702 | 2.9068 | -0.81838 | -0.49593 | -0.48019
779 | 2.4016 | 3.3398 | 3.0639 | 3.043
319 | 0.15 | 2.8816 | 2.3434 | 2.6435
740 | 0.68138 | 4.0196 | 3.0368 | 4.134
669 | 0.03 | 0.34335 | 0.656 | 0.83885
0.15
458 | 7.3287
55 | 9.8113
504 | 2.0051
704 | 9.5524
46.736
552 | 3.0968
255 | 4.2162
56 | 12.5248
806 | 5.8078
372 | 0.76294
706 | 3.888
318 | 1.2354
807 | 3.78
808 | 4.8235
810 | 10.648
327 | 3.4378
651 | 2.7951
652 | 13.8912
0.74
591 | 0.79994
535 | 0.1
499 | 4.0358
343 | 0.39
509 | 2.9061
257 | 8.7914
220 | 0.39495
708 | 3.6769
0.28
812 | 6.2622
328 | 0.02
266 | 3.7561
313 | 3.2
0.05
813 | 2.138
0.14
699 | 2.88
73 | 7.33
814 | 16.68
72 | 0.61
279 | 3.62
274 | 0.321
637 | 1.69
0.26
370 | 5.99
550 | 3.34
0.007
57 | 8.53
365 | 3.83
3.168
462 | 11.19
745 | 0.2
701 | 2.35
454 | 7.21
246 | 9.53
0.001
5 | 0
387 | 0.015
210 | 4.62
670 | 1.85
265 | 1.18
312 | 7.55
256 | 5.59
64 | 8.16
1.08
269 | 0.33
0.24
0.92
140 | 0.1
62 | 9.71
2 | 8.86
653 | 1.98
1.07
338 | 0.22
826 | 16.3
581 | 0.84
385 | 0.21
672 | 2.13
827 | 15.4
562 | 0.03
306 | 1.77
513 | 3.71
514 | 0.34
32 | 13
541 | 0.04
744 | 1.34
268 | 1.96
244 | 6.96
0.006
830 | 3.58
832 | 13.31
834 | 9.3
208 | 9.674
305 | 1.06
326 | 1
551 | 6.659
0
469 | 2.446
712 | 9.845
836 | 5.887
457 | 12.719
720 | 0.03
212 | 1.92
752 | 8.332
348 | 0.257
713 | 9.311
259 | 1.965
777 | 0.767
841 | 15.6428
346 | 3.64
515 | 10.0235
336 | 1.01
557 | 4.0642
388 | 1.4666
598 | 5.5058
644 | 1.0977
517 | 2.7259
518 | 0.35
203 | 2.7015
629 | 1.3375
461 | 5.1755
1.61
2.17
209 | 10.6592
363 | 7.9401
0.6
2.3935
844 | 15.7585
675 | 0.21262
847 | 2.6561
58 | 2.9715
482 | 4.5242
0.13
68 | 5.3959
849 | 11.6381
324 | 0.1
761 | 0.2
254 | 4.5778
519 | 0.52394
0.31
276 | 0.04
692 | 1.3518
680 | 0.24084
2.6
487 | 6.1754
452 | 9.2029
583 | 0.85414
0.77
1.7
253 | 1.8857
718 | 0.38835
854 | 19.5522
1.575
89 | 4.5724
332 | 0.31
856 | 3.9736
567 | 0.01
648 | 0.99387
522 | 1.42
2.915
523 | 1.5401
345 | 0.14
396 | 0.01
330 | 2.0774
383 | 0.28
273 | 1.7
781 | 0.95271
207 | 11.4835
714 | 6.5761
756 | 0.06
525 | 2.1877
249 | 9.6474
4 | 2.6439
722 | 6.5342
696 | 17.8859
861 | 9.726
1.38
695 | 0.93616
597 | 2.2038
991 | 0.64697
647
582 | 2.5392
863 | 2.991
865 | 6.8173
867 | 4.9053
560 | 1.4909
750 | 11.1998
67 | 9.4316
869 | 6.1889
76 | 1.1293
379 | 1.1985
871 | 6.4555
321 | 0.94139
87 | 0.62612
757 | 0.84996
873 | 3.1963
527 | 0.23
766 | 0.55
559 | 9.9898
724 | 10.6882
309 | 1.1117
726 | 7.3038
1.15
875 | 14.0183
0.5
366 | 0.56
464 | 6.75
0.13
881 | 2.33
329 | 0.32
205 | 3.08
335 | 0.11
531 | 2.04
323 | 0.82
204 | 2.11
1.125
219 | 1.26
304 | 1.89
322 | 2.2
520 | 3.88
882 | 9.67
771 | 0.06
884 | 3.92
0.03
727 | 5.04
333 | 1.59
262 | 1.223
532 | 0.95
729 | 1.46
754 | 0.12
453 | 3.31
0.08
211 | 4.71
677 | 16.26
633 | 1.38
634 | 2.54
1.18
2.15
584 | 1.81
890 | 5.09
657 | 1.72
576 | 0.09
90 | 2.88
703 | 1.97
507 | 0.01
488 | 1.83
721 | 0.86
465 | 1.44
665 | 0.51
568 | 0.01
221 | 0.03
1.599
747 | 0.85
317 | 1.04
217 | 1.66
13 | 5.97
308 | 8.39
369 | 0.4
556 | 1.4958
83 | 14.2278
77 | 1.1689
54 | 8.8519
455 | 6.6348
623 | 0.59761
82 | 6.9852
339 | 0.04
12 | 5.645
682 | 0.72879
650 | 0.1
14 | 7.6292
406 | 13.8115
373 | 2.0365
731 | 1.8719
742
401 | 3.8121
538 | 1.3883
84 | 6.9818
901 | 2.6708
590 | 0.8365
3 | 11.6179
903 | 2.69
698 | 0.8529
907 | 2.7045
75 | 7.6311
251 | 11.4662
52 | 8.7792
564 | 8.6165
909 | 5.9915
74 | 7.7608
911 | 1.6501
585 | 4.97
912
547 | 13.2298
542 | 2.5844
0.26
0.99
0.3
723 | 9.2982
913 | 2.9168
384 | 0.48413
915 | 10.4353
554 | 1.5493
6 | 5.3525
681 | 0.12
558 | 1.3676
272 | 7.3212
14.4902
917 | 4.7912
636 | 2.4089
307 | 16.9744
53 | 6.263
921 | 4.4956
587 | 5.132
375 | 1.5966
24 | 16.056
563 | 0.04
923 | 2.42
0.3
553 | 1.76
247 | 10.24
928 | 13.5466
926 | 9.7258
734 | 6.88
263 | 3.68
660 | 1.9171
753 | 0.03
1.64
334 | 1.2269
331 | 3.2188
632 | 4.93
435 | 2.3238
932 | 12.25
748 | 0.85
732 | 0.05
735 | 15.84
0.27
66 | 2.84
270 | 4.37
935 | 19.8011
544 | 1.75
33 | 17.04
4.162
459 | 4.5782
362 | 4.73
498 | 1.98
939 | 11.15
749 | 2.86
315 | 2.1434
685 | 0.8184
364 | 3.8817
700 | 4.707
340 | 0.08
271 | 4.4032
5.015
2.992
683 | 0.45553
0.09
641 | 0.72032
536 | 0.39289
0.32
755 | 0.05
941 | 13.58
639 | 2.7185
139 | 3.55
943 | 14.7968
952 | 2.1226
10.6468
10
0.11
956 | 8.089
679 | 2.4728
958 | 11.31
658 | 0.75947
397 | 0.03
945 | 10.2704
947 | 6.7964
947 | 11.2658
1.09
645
382 | 0.88168
951 | 1.1029
950 | 3.2535
678 | 5.3613
684 | 0.42475
751 | 0.92456
2.2728
546 | 6.5718
662 | 1.7109
341 | 0.04
310 | 3.1065
347 | 1.5057
3.21
248 | 20.1261
0.03
342 | 0.06
738 | 0.71196
540 | 0.02
962 | 9.4835
548 | 0.71
2.4739
0.71223
0.92
964 | 9.3045
218 | 1.7449
640 | 1.2752
549 | 2.5079
791 | 1.6549
687 | 3.7038
25 | 5.7401
741 | 15.4639
15 | 9.2362
349 | 0.65293
763 | 0.08
674 | 1.7948
981 | 4.8897
982 | 7.0476
371 | 2.441
594 | 9.1682
986 | 13.9463

## Growth Rates
Growth Rates
Name | Menu Dropdown
0 | 0 | 1
L | L | 1.0055
M | M | 1.0136
H | H | 1.0268
No PI
Per Cust | 2.8094 | kVA
Note on D267: Mills, David: Due to measurement point for generation it is not possible to distinguish between load and generation at this site

## Manual Calculation
GSP | PRIMARY | Comment | Max | Max Date/Time | Min | Min Date/Time | Assumed Proportion of Max
Abernethy | Abernethy |  | 3.2556 | 2019-11-22 08:00 | 0.010901 | 2019-09-24 18:30 | 20%
Abernethy | Errol |  | 4.5323 | 2020-01-20 07:30 | 1.1132 | 2019-07-16 02:00
Abernethy | Glendevon |  | 1.8314 | 2019-11-12 17:30 | 0 | 2019-06-11 18:30
Abernethy | Milnathort |  | 11.4965 | 2019-11-19 17:30 | 2.2559 | 2019-07-01 05:00
Alness | Glastullich |  | 1.4999 | 2020-01-16 08:30 | 0.030142 | 2019-06-03 12:30
Alness | Invergordon |  | 5.7607 | 2020-01-28 16:30 | 1.1261 | 2019-07-21 01:30
Ardmore | Coll |  | 2.6259 | 2020-02-11 20:30 | 0.056396 | 2019-06-29 03:30
Ardmore | Gisla |  | 1.4718 | 2019-09-03 23:00 | 0.21922 | 2019-06-25 02:30
Beauly | Dingwall |  | 8.8249 | 2019-11-19 11:00 | 0.28814 | 2019-07-23 04:30
Braco West | Callander |  | 4.5924 | 2019-11-19 15:00 | 0.090126 | 2019-08-31 23:30
Bridge of Dun | St Cyrus |  | 1.302 | 2019-12-25 15:00 | 0.16303 | 2019-08-25 03:00
Carradale | Ballure |  | 1.3194 | 2020-02-24 13:30 | 0.2018 | 2019-07-26 01:30
Dyce | Balmedie |  | 3.6439 | 2020-01-29 17:00 | 0.73072 | 2019-07-26 04:00
Fiddes | Edzell |  | 2.4908 | 2019-11-19 15:00 | 0.53824 | 2019-08-06 03:30
Fiddes | Stonehaven |  | 8.9406 | 2019-11-13 17:00 | 1.7226 | 2019-06-03 03:00
Fort Augustus | Drumnadrochit |  | 2.8469 | 2019-12-30 02:00 | 0.50861 | 2019-08-26 02:30
Grudie Bridge | Kerry Falls |  | 1.8126 | 2019-05-05 20:00 | 0.20033 | 2019-04-26 08:00
Keith | Buckie |  | 13.081 | 2019-11-14 16:30 | 5.8352 | 2019-06-24 04:00
Keith | Huntly |  | 5.9826 | 2019-12-16 16:30 | 1.2241 | 2019-07-01 04:00
Keith | Insch |  | 6.2616 | 2020-01-09 17:30 | 0.20197 | 2019-07-25 14:30
Keith | Limehillocks |  | 1.426 | 2019-12-25 12:30 | 0.20506 | 2019-07-25 14:00
Keith | Marnoch | 401A Auchinderran Windfarm Generator not included in sheet. 401A incorrectly shown as Boyndie Wind Farm. Boyndie should be 405A. | 2.796 | 2020-03-12 11:30 | 0.49995 | 2019-08-26 01:30
Keith | Portsoy |  | 2.8729 | 2019-09-11 12:30 | 0.39765 | 2019-08-10 02:30
Killin | Lochearnhead |  | 1.3297 | 2019-12-01 09:00 | 0.32716 | 2019-07-01 01:30
Kintore | Methlick |  | 1.976 | 2019-12-24 16:30 | 0.27741 | 2019-08-06 02:30
Kintore | Oldmeldrum |  | 4.5255 | 2020-01-13 18:30 | 0.81053 | 2019-04-22 03:00
Kintore | Torryburn |  | 9.3845 | 2019-11-19 16:30 | 2.375 | 2019-07-07 04:30
Lunanhead | Lunanhead |  | 7.2255 | 2019-12-09 16:30 | 1.1496 | 2019-07-24 03:30
Lunanhead | Maryton |  | 6.3113 | 2019-11-19 17:00 | 0.98049 | 2019-08-11 04:00
Milton of Craigie | Longhaugh |  | 8.062 | 2019-11-19 17:00 | 2.0882 | 2019-06-30 05:30
Nairn | Dalcross |  | 3.1072 | 2020-03-06 08:30 | 0.11163 | 2019-05-14 00:30
Redmoss | Newtonhill |  | 10.3687 | 2019-12-11 17:30 | 2.9975 | 2019-08-26 03:30
Shetland | Gremista (Lerwick) |  | 17.3258 | 2020-01-30 16:30 | 5.0556 | 2019-08-01 04:30
Strathleven | Drymen |  | 2.4361 | 2020-01-28 17:00 | 0.22221 | 2019-09-11 02:30
Strathleven | Kepculloch |  | 3.8246 | 2020-01-28 17:30 | 0.79133 | 2019-08-27 02:00
Strichen | Maud |  | 2.5624 | 2019-11-19 20:00 | 0.053676 | 2019-05-29 14:30
Strichen | New Pitsligo |  | 1.4514 | 2019-11-13 20:00 | 0.42678 | 2019-06-19 10:30
Tarland | Ballater |  | 5.1068 | 2019-12-31 16:30 | 1.0896 | 2019-06-30 04:00
Tarland | Mossat |  | 1.6833 | 2019-11-11 11:00 | 0.083774 | 2019-07-01 01:30
Taynuilt | Dervaig |  | 3.8681 | 2020-02-13 13:30 | 0.037253 | 2020-01-05 22:30
Thurso | Forss |  | 0.82854 | 2019-12-09 17:00 | 0.10148 | 2019-05-15 15:30
Thurso | Lyness |  | 0.71401 | 2019-12-29 04:30 | 0.070643 | 2019-10-15 11:00
Tummel Bridge | Kinloch Rannoch |  | 0.96479 | 2019-11-19 11:30 | 0.17385 | 2019-07-26 01:30
Craigiebuckler | Craigiebuckler |  | 5.786 | 2019-11-11 18:00 | 1.9288 | 2019-07-14 05:00
Craigiebuckler | Craigton |  | 5.9035 | 2019-11-08 20:00 | 1.7081 | 2019-07-14 05:00
Craigiebuckler | Ruthrieston |  | 8.4907 | 2019-11-11 18:00 | 2.8793 | 2019-07-21 05:30
Bridge of Dun | GLAXO (33kV Customer) | 33kV Customer | 3.956 | 2019-09-09 08:00 | 0.7912 | No PI, assumed 20% of max
Macduff | MACDUFF NEW | Poor Data this year - Remove from manual and use auto calc for 2020 demands | 7.3738 | 2020-03-25 17:00 | 1.4748 | No PI, assumed 20% of max
Peterhead Shell | PETERHEAD SHELL |  | 2.6548 | 2020-01-18 16:30 | 0.53097 | No PI, assumed 20% of max
Quoich | QUOICH PRIMARY |  | 0.10234 | 2020-02-12 07:00 | 0.020468 | No PI, assumed 20% of max
Tummel Bridge | ABERFELDY | Poor Data this year - Remove from manual and use auto calc for 2020 demands | 2.3701 | 2020-02-29 09:30 | 0.30255 | 2020-02-20 21:00
Dounreay | DSRL |  | 5.3165 | 2019-11-19 10:30 | 2.6423 | 2019-09-28 12:30
Alness | CONTULLICH | No PI | 0.039332 | No PI | 0.0078663 | No PI, assumed 20% of max
Alness | LEALTY | No PI | 0 | No PI | 0 | No PI, assumed 20% of max
Beauly | AIGAS | No PI | 0.19104 | No PI | 0.038208 | No PI, assumed 20% of max
Grudie Bridge | COMRIE | No PI | 0.028094 | No PI | 0.0056188 | No PI, assumed 20% of max
Grudie Bridge | CONON FALLS | No PI | 0.35679 | No PI | 0.071359 | No PI, assumed 20% of max
Broadford | ACHINTEE | No PI | 0.084282 | No PI | 0.016856 | No PI, assumed 20% of max
Carradale | CLAONAIG | No PI | 0.20228 | No PI | 0.040455 | No PI, assumed 20% of max
Carradale | DIPPEN | No PI | 0.94958 | No PI | 0.18992 | No PI, assumed 20% of max
Cassley | OVERSCAIG | No PI | 0.030903 | No PI | 0.0061807 | No PI, assumed 20% of max
Clachan | BUTTERBRIDGE | No PI | 0.0084282 | No PI | 0.0016856 | No PI, assumed 20% of max
Dunoon | COLINTRAIVE | No PI | 0.26689 | No PI | 0.053379 | No PI, assumed 20% of max
Dunoon | GLENDARUEL | No PI | 0.35679 | No PI | 0.071359 | No PI, assumed 20% of max
Dunoon | NEWTON | No PI | 0.27813 | No PI | 0.055626 | No PI, assumed 20% of max
Fort Augustus | ABERCHALDER | No PI | 0.084282 | No PI | 0.016856 | No PI, assumed 20% of max
Fort Augustus | ARDOCHY | No PI | 0.022475 | No PI | 0.0044951 | No PI, assumed 20% of max
Fort Augustus | GLEN LAOGH | No PI | 0.0084282 | No PI | 0.0016856 | No PI, assumed 20% of max
Fort Augustus | INVERGARRY | No PI | 0.4776 | No PI | 0.09552 | No PI, assumed 20% of max
Inverness | WESTER DRUMMOND | No PI | 0.036522 | No PI | 0.0073045 | No PI, assumed 20% of max
Fort William | GLENUIG | No PI | 0.078663 | No PI | 0.015733 | No PI, assumed 20% of max
Fort William | KINGAIRLOCH | No PI | 0.081473 | No PI | 0.016295 | No PI, assumed 20% of max
Fort William | KINLOCHMOIDART | No PI | 0.070235 | No PI | 0.014047 | No PI, assumed 20% of max
Fort William | LIDDESDALE | No PI | 0.019666 | No PI | 0.0039332 | No PI, assumed 20% of max
Fort William | POOR HOUSE | No PI | 0.019666 | No PI | 0.0039332 | No PI, assumed 20% of max
Fort William | RAHOY | No PI | 0.042141 | No PI | 0.0084282 | No PI, assumed 20% of max
Fort William | SHONA BEAG | No PI | 0.028094 | No PI | 0.0056188 | No PI, assumed 20% of max
Grudie Bridge | BIDEN CLAN RAONAILD | No PI | 0.0028094 | No PI | 0.00056188 | No PI, assumed 20% of max
Grudie Bridge | DRUMRUNIE | No PI | 0.32589 | No PI | 0.065178 | No PI, assumed 20% of max
Grudie Bridge | GARBAT FOREST | No PI | 0.0056188 | No PI | 0.0011238 | No PI, assumed 20% of max
Grudie Bridge | INVERBROOM | No PI | 0.22194 | No PI | 0.044389 | No PI, assumed 20% of max
Grudie Bridge | KINLOCHEWE | No PI | 0.9243 | No PI | 0.18486 | No PI, assumed 20% of max
Grudie Bridge | LETTEREWE | No PI | 0.011238 | No PI | 0.0022475 | No PI, assumed 20% of max
Grudie Bridge | LOCH GLASCARNOCH | No PI | 0.0028094 | No PI | 0.00056188 | No PI, assumed 20% of max
Grudie Bridge | MINOR GRUDIE | No PI | 0.0056188 | No PI | 0.0011238 | No PI, assumed 20% of max
Inverness | ERROGIE | No PI | 0.20228 | No PI | 0.040455 | No PI, assumed 20% of max
Inverness | DUNMAGLASS | No PI | 0.036522 | No PI | 0.0073045 | No PI, assumed 20% of max
Killin | CASHLIE | No PI | 0.20509 | No PI | 0.041017 | No PI, assumed 20% of max
Killin | LUBNAIG | No PI | 0.022475 | No PI | 0.0044951 | No PI, assumed 20% of max
Lairg | TORBOLL | No PI | 0.016856 | No PI | 0.0033713 | No PI, assumed 20% of max
Lairg | TRESSADY | No PI | 0.68269 | No PI | 0.13654 | No PI, assumed 20% of max
Loch Carnan | LOCH CARNAN | No PI | 0.50569 | No PI | 0.10114 | No PI, assumed 20% of max
Port Ann | AIRIGH-NA-BRODAIG | No PI | 0.075854 | No PI | 0.015171 | No PI, assumed 20% of max
Port Ann | LUSSAGIVEN | No PI | 0.036522 | No PI | 0.0073045 | No PI, assumed 20% of max
Port Ann | STONEFIELD | No PI | 0.053379 | No PI | 0.010676 | No PI, assumed 20% of max
Port Ann | TARBERT JURA | No PI | 0.025285 | No PI | 0.0050569 | No PI, assumed 20% of max
Rannoch | BLACKMOUNT | No PI | 0.039332 | No PI | 0.0078663 | No PI, assumed 20% of max
Rannoch | BRIDGE OF GAUR | No PI | 0.33432 | No PI | 0.066864 | No PI, assumed 20% of max
Rannoch | GLENETIVE | No PI | 0.087092 | No PI | 0.017418 | No PI, assumed 20% of max
Sloy | SLOY POWER STATION | No PI | 1.7053 | No PI | 0.34106 | No PI, assumed 20% of max
Stornoway | MAARUIG | No PI | 0.11519 | No PI | 0.023037 | No PI, assumed 20% of max
Taynuilt | BONAWE | No PI | 0.0028094 | No PI | 0.00056188 | No PI, assumed 20% of max
Taynuilt | DALMALLY | No PI | 0.23599 | No PI | 0.047198 | No PI, assumed 20% of max
Taynuilt | EREDINE | No PI | 0.118 | No PI | 0.023599 | No PI, assumed 20% of max
Taynuilt | KENMORE | No PI | 0.31465 | No PI | 0.062931 | No PI, assumed 20% of max
Taynuilt | KERRERA | No PI | 0.098329 | No PI | 0.019666 | No PI, assumed 20% of max
Taynuilt | SCAMMADALE | No PI | 0.078663 | No PI | 0.015733 | No PI, assumed 20% of max
Taynuilt | TIRORAN BRIDGE | No PI | 0.064616 | No PI | 0.012923 | No PI, assumed 20% of max
Thurso | NORTH HOY | No PI | 0.10957 | No PI | 0.021913 | No PI, assumed 20% of max
Tummel Bridge | FINCASTLE | No PI | 0.075854 | No PI | 0.015171 | No PI, assumed 20% of max
St Fillans | ST FILLANS 33/LV |  | 0.10608 | No PI | 0.021216 | No PI, assumed 20% of max
Milton of Craigie | Milton of Craigie | Unreliable peaky data | 7.27 | 2019-07-27 18:00 | 1.454 | No PI, assumed 20% of max
HELENSBURGH (SP) |  | No PI | 0 | No PI | 0 | No PI, assumed 20% of max

## SubstationLoad_Max_Primaries
GSP | PRIMARY | NRN | If PI is in Amp and there is DG | PI Expression | Load - Filtered Data (Maximum Net of Generation) |  |  |  | Time of Maximum for Filtered Data |  |  |  | Generation at time of Maximum |  |  |  | Percentage of Overall Filtered Data | Maximum Demand Overall | Time of Maximum Demand Overall | Generation at time of Maximum Demnad Overall
[5 empty] | Maximum Spring | Maximum Summer | Maximum Autumn | Maximum Winter | Maximum Spring | Maximum Summer | Maximum Autumn | Maximum Winter | Maximum Spring | Maximum Summer | Maximum Autumn | Maximum Winter
Abernethy | Abernethy | 242 | TRUE | ('241~T1~AMPS~AI')*1.732*0.011 | 2.0776 | 2.1037 | 2.4601 | 3.5231 | 2019-04-16 14:20 | 2019-07-26 08:44 | 2019-10-02 19:35 | 2019-11-22 12:18 | 0.018606 | 0.036282 | 0.0046515 | 0.026979 | 6.044% | 3.5231 | 2019-11-22 12:18 | 0.026979
Abernethy | Balbeggie | 255 | FALSE | -('255~T1~MW~AI') | 3.4408 | 3.2069 | 3.5595 | 4.061 | 2019-04-17 08:13 | 2019-06-13 08:24 | 2019-10-31 17:07 | 2019-11-20 17:10 | 0 | 0.55272 | 0.17586 | 0.17773 | 3.571% | 4.061 | 2019-11-20 17:10 | 0.17773
Abernethy | Binn Hill Landfill | 284 | FALSE | ('284~CS1~MW~AI') | 3.4025 | 3.3858 | 2.717 | 3.2562 | 2019-05-28 10:15 | 2019-06-21 10:10 | 2019-10-15 08:20 | 2019-11-20 11:33 | 0 | 0 | 0 | 0 | 2.747% | 3.4025 | 2019-05-28 10:15 | 0
Abernethy | Bridge Of Earn | 279 | FALSE | ('279~003~AMPS~AI'+'279~004~AMPS~AI')*1.732*0.011 | 2.6482 | 2.1672 | 3.0197 | 3.2865 | 2019-04-16 20:09 | 2019-06-13 17:23 | 2019-10-30 17:23 | 2019-11-19 17:48 | 0 | 0 | 0 | 0 | 2.747% | 3.2865 | 2019-11-19 17:48 | 0
Abernethy | Errol | 254 | TRUE | ('254~SUMM~AMPS~AI')*1.732*0.011 | 3.8693 | 3.1839 | 4.0382 | 4.5342 | 2019-04-03 11:31 | 2019-08-30 17:23 | 2019-10-31 17:05 | 2019-11-19 18:08 | 0.00794 | 0.082154 | 0.056765 | 0.051883 | 2.473% | 4.5342 | 2019-11-19 18:08 | 0.051883
Abernethy | Glendevon | 273 | TRUE | ('273~11KV~AMPS~AI')*1.732*0.011 | 0.45874 | 0.47316 | 0.67182 | 0.91887 | 2019-04-06 19:22 | 2019-08-29 18:38 | 2019-10-29 18:01 | 2020-01-03 13:55 | 0.34428 | 0 | 0.33405 | 0.482 | 12.91% | 0.91887 | 2020-01-03 13:55 | 0.482
Abernethy | Harbour | 247 | FALSE | ('247~T1_T2~AMPS~AI')*1.732*0.011 | 7.8336 | 6.762 | 7.9062 | 9.8876 | 2019-04-03 11:40 | 2019-06-24 12:02 | 2019-10-30 17:22 | 2019-12-18 14:43 | 0 | 0 | 0 | 0 | 3.297% | 9.8876 | 2019-12-18 14:43 | 0
Abernethy | Milnathort | 251 | TRUE | ('251~011~AMPS~AI'+'251~4L5~AMPS~AI')*1.732*0.011 | 8.8741 | 8.0255 | 10.5974 | 11.5567 | 2019-04-16 20:11 | 2019-06-12 17:44 | 2019-10-28 17:24 | 2019-11-20 17:30 | 0.50526 | 0.34894 | 0.062343 | 0.15074 | 1.648% | 11.5567 | 2019-11-20 17:30 | 0.15074
Abernethy | Rumbling Bridge | 252 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Abernethy | Scone | 271 | FALSE | ('271~common~AMPS~AI')*1.732*0.011 | 3.1847 | 2.4758 | 3.7097 | 4.0753 | 2019-04-04 20:32 | 2019-08-11 17:21 | 2019-10-27 17:29 | 2019-12-01 17:14 | 0 | 0 | 0 | 0 | 2.473% | 4.0753 | 2019-12-01 17:14 | 0
Alness | Balaldie | 552 | FALSE | ('552~097~AMPS~AI'+'552~098~AMPS~AI'+'552~099~AMPS~AI')*1.732*0.011 | 2.1872 | 1.8253 | 2.6374 | 3.0002 | 2019-04-01 20:04 | 2019-06-13 17:22 | 2019-10-29 20:06 | 2019-12-25 11:07 | 0 | 0 | 0 | 0 | 1.923% | 3.0002 | 2019-12-25 11:07 | 0
Alness | Contullich | 541 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Alness | Crosshills | 551 | FALSE | ('551~T1_T2~AMPS~AI')*1.732*0.011 | 6.7815 | 5.6596 | 6.4047 | 6.9127 | 2019-04-04 12:12 | 2019-06-06 12:10 | 2019-10-30 17:04 | 2020-01-15 13:48 | 0 | 0 | 0 | 0 | 1.648% | 6.9127 | 2020-01-15 13:48 | 0
Alness | Glastullich | 522 | TRUE | ('522~11KV~AMPS~AI')*1.732*0.011 | 1.1191 | 0.91815 | 1.2754 | 1.4623 | 2019-04-01 20:01 | 2019-08-21 20:21 | 2019-10-31 20:17 | 2020-02-02 12:05 | 0 | 0 | 0 | 0 | 6.044% | 1.4623 | 2020-02-02 12:05 | 0
Alness | Invergordon | 559 | TRUE | ('559~T1_T2~AMPS~AI')*1.732*0.011 | 12.0092 | 12.161 | 11.586 | 11.8467 | 2019-05-30 02:15 | 2019-08-28 00:20 | 2019-10-23 06:09 | 2019-12-28 04:52 | 6.985 | 6.975 | 7.36 | 7.23 | 4.67% | 12.161 | 2019-08-28 00:20 | 6.975
Alness | Lealty | 576 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Alness | Nigg | 554 | FALSE | ('554~TR1~AMPS~AI')*1.732*0.011 | 1.6605 | 1.2642 | 1.0521 | 1.5014 | 2019-04-03 13:54 | 2019-06-10 10:52 | 2019-10-25 08:00 | 2019-12-13 08:02 | 0 | 0 | 0 | 0 | 4.121% | 1.6605 | 2019-04-03 13:54 | 0
Alness | Peddieston | 553 | FALSE | ('553~T1~AMPS~AI'+'553~T2~AMPS~AI')*1.732*0.011 | 1.408 | 1.0841 | 1.5134 | 1.8654 | 2019-04-01 07:10 | 2019-08-23 18:47 | 2019-10-27 20:04 | 2019-12-17 20:07 | 0 | 0 | 0 | 0 | 2.198% | 1.8654 | 2019-12-17 20:07 | 0
Alness | Tain | 546 | FALSE | ('546~T1_T2~AMPS~AI')*1.732*0.011 | 5.2313 | 3.8858 | 4.3296 | 6.359 | 2019-04-03 12:08 | 2019-06-13 20:04 | 2019-10-25 20:05 | 2019-11-19 20:26 | 0 | 0 | 0 | 0 | 3.571% | 6.359 | 2019-11-19 20:26 | 0
Arbroath | Carnoustie | 64 | FALSE | -('064~TR1~MW~AI'+'064~TR2~MW~AI') | 6.5262 | 5.6144 | 6.982 | 7.5459 | 2019-04-01 17:54 | 2019-06-24 17:38 | 2019-10-28 17:24 | 2019-12-18 17:26 | 0 | 0 | 0 | 0 | 1.648% | 7.5459 | 2019-12-18 17:26 | 0
Arbroath | Charles Avenue | 62 | FALSE | ('062~T1_T2_11~AMPS~AI')*1.732*0.011 | 8.2006 | 7.5252 | 8.5243 | 9.4341 | 2019-05-08 16:47 | 2019-06-13 10:50 | 2019-10-30 17:15 | 2019-11-19 17:16 | 0 | 0 | 0 | 0 | 1.923% | 9.4341 | 2019-11-19 17:16 | 0
Arbroath | Elliot Depot | 68 | FALSE | ('068~T1_11~AMPS~AI')*1.732*0.011 | 5.0682 | 5.0291 | 5.1351 | 5.4142 | 2019-05-09 12:16 | 2019-08-27 11:19 | 2019-10-17 09:42 | 2019-12-10 14:33 | 0 | 0 | 0 | 0 | 1.648% | 5.4142 | 2019-12-10 14:33 | 0
Arbroath | Hume Street | 67 | FALSE | ('067~T1_T2_11~AMPS~AI')*1.732*0.011 | 8.1841 | 6.4635 | 7.6594 | 8.7981 | 2019-04-03 11:49 | 2019-06-13 11:30 | 2019-10-30 16:47 | 2019-11-19 16:29 | 0 | 0 | 0 | 0 | 2.473% | 8.7981 | 2019-11-19 16:29 | 0
Arbroath | Redford | 66 | FALSE | -('066~T1~MW~AI') | 2.2912 | 1.8556 | 2.7523 | 2.8973 | 2019-04-06 18:09 | 2019-06-03 12:01 | 2019-10-31 17:23 | 2019-11-06 17:30 | 0.47861 | 0.48643 | 0.1632 | 0.030399 | 4.121% | 2.8973 | 2019-11-06 17:30 | 0.030399
Ardmore | Aird | 671 | FALSE | ('671~T1_T2~AMPS~AI')*1.732*0.011 | 2.1453 | 1.7866 | 2.0671 | 2.4928 | 2019-04-09 07:38 | 2019-06-13 07:22 | 2019-10-29 18:34 | 2020-01-14 13:09 | 0 | 0 | 0 | 0 | 1.923% | 2.4928 | 2020-01-14 13:09 | 0
Ardmore | Arnish | 669 | FALSE | ('669~TR1~MW~AI') | 0.2567 | 0.12835 | 0.77009 | 1.5402 | 2019-04-02 15:50 | 2019-06-22 | 2019-10-04 | 2019-11-16 | 0 | 0 | 0 | 0 | 36.54% | 1.5402 | 2019-11-16 | 0
Ardmore | Barra G S | 659 | FALSE | ('659~TOTAL~MW~AI') | No Data | No Data | No Data | 0.0015625 | Missing Data | Missing Data | Missing Data | 2020-02-15 06:35 | 0 | 0 | 0 | 0 | 75.27% | 0.0015625 | 2020-02-15 06:35 | 0
Stornoway | Barvas | 651 | FALSE | ('651~T1_T2~AMPS~AI')*1.732*0.011 | 2.4858 | 1.7552 | 2.347 | 2.6066 | 2019-04-09 21:54 | 2019-06-13 09:27 | 2019-10-30 18:34 | 2019-12-16 16:48 | 0 | 0 | 0 | 0 | 2.473% | 2.6066 | 2019-12-16 16:48 | 0
Stornoway | Battery Point | 652 | FALSE | ('652~T1~MW~AI'+'652~T1~MW~AI'+'652~T1~MW~AI') | 12.1538 | 10.1868 | 11.6923 | 13.3187 | 2019-04-04 11:18 | 2019-08-07 17:35 | 2019-10-31 17:11 | 2019-11-18 16:09 | 0 | 0 | 0 | 0 | 2.198% | 13.3187 | 2019-11-18 16:09 | 0
Stornoway | Callanish | 670 | FALSE | ('670~011~AMPS~AI')*1.732*0.011 | 1.6323 | 1.52 | 1.6868 | 1.9296 | 2019-04-10 20:58 | 2019-06-13 20:11 | 2019-10-29 18:49 | 2019-12-24 18:59 | 0 | 0 | 0 | 0 | 2.747% | 1.9296 | 2019-12-24 18:59 | 0
Ardmore | Clachan | 653 | FALSE | ('653~TR2~AMPS~AI')*1.732*0.011 | 1.943 | 1.6213 | 1.862 | 2.1501 | 2019-04-01 18:43 | 2019-06-14 08:36 | 2019-10-29 19:13 | 2020-02-24 18:52 | 0 | 0 | 0 | 0 | 3.297% | 2.1501 | 2020-02-24 18:52 | 0
Stornoway | Coll | 672 | TRUE | ('672~TR1~AMPS~AI')*1.732*0.011 | 2.2885 | 1.6594 | 2.0423 | 2.7639 | 2019-04-03 20:40 | 2019-06-03 19:01 | 2019-10-25 18:21 | 2020-01-13 18:49 | 0.91087 | 0.92454 | 0.9431 | 0.89914 | 3.846% | 2.7639 | 2020-01-13 18:49 | 0.89914
Ardmore | Drimore | 644 | FALSE | ('644~T1~AMPS~AI')*1.732*0.011 | 0.90936 | 0.74981 | 0.90127 | 1.0403 | 2019-04-04 12:47 | 2019-08-30 09:32 | 2019-10-29 18:49 | 2020-03-05 19:07 | 0 | 0 | 0 | 0 | 3.571% | 1.0403 | 2020-03-05 19:07 | 0
Ardmore | Eoligarry Pmr | 666 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Ardmore | Frobost Regulator | 663 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Stornoway | Gisla | 648 | TRUE | ('648~1H0~AMPS~AI')*1.732*0.033 | 1.0625 | 0.89906 | 0.68216 | 0.33383 | 2019-05-09 09:34 | 2019-07-12 18:32 | 2019-09-27 21:38 | 2019-11-19 10:10 | 0 | 0 | 0 | 0.188 | 35.71% | 1.0625 | 2019-05-09 09:34 | 0
Ardmore | Harris Grid | 647 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Stornoway | Laxay | 657 | FALSE | ('657~T1~AMPS~AI')*1.732*0.011 | 1.5291 | 1.1885 | 1.5197 | 1.7488 | 2019-04-03 18:58 | 2019-06-12 17:41 | 2019-10-28 18:44 | 2020-02-12 18:34 | 0 | 0 | 0 | 0 | 2.198% | 1.7488 | 2020-02-12 18:34 | 0
Ardmore | Loch Carnan | 665 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Stornoway | Maaruig | 650 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Ardmore | Northbay Pmr | 667 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Ardmore | Pollachar | 660 | FALSE | -('660~Tr1~mw~AI'+'660~Tr2~mw~AI') | 2.6292 | 2.0293 | 2.2175 | 2.7797 | 2019-04-07 20:05 | 2019-06-06 18:47 | 2019-10-26 20:00 | 2020-02-16 21:08 | 0.41319 | 0.11331 | 0.88547 | 0.8757 | No Data | 2.7797 | 2020-02-16 21:08 | 0.8757
Ardmore | Rodil Pmr | 664 | TRUE | [5 empty] | 2018-05-08 19:37 | 2018-06-21 10:31 | 2018-10-08 19:35 | 2018-03-02 03:37 | 0 | 0 | 0 | 0
Harris | Stockinish | 658 | FALSE | ('658~MW~MW~AI') | 0.61538 | 0.60073 | 0.52015 | 0.65201 | 2019-05-29 19:16 | 2019-06-06 19:19 | 2019-10-25 09:17 | 2019-12-17 20:36 | 0 | 0 | 0 | 0 | 16.48% | 0.65201 | 2019-12-17 20:36 | 0
Ardmore | Stornoway Grid | 645 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Harris | Tarbert | 662 | FALSE | ('662~T1_T2~AMPS~AI')*1.732*0.011 | 0.81302 | 0.68462 | 0.80465 | 0.94353 | 2019-04-03 21:04 | 2019-06-13 08:58 | 2019-10-28 21:04 | 2020-02-12 18:44 | 0 | 0 | 0 | 0 | 3.846% | 0.94353 | 2020-02-12 18:44 | 0
Beauly | Aigas | 501 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Beauly | Blackstand | 509 | FALSE | ('509~TR1~AMPS~AI')*1.732*0.011 | 2.3599 | 1.9149 | 2.2971 | 2.7951 | 2019-04-03 20:04 | 2019-06-24 17:36 | 2019-10-29 18:14 | 2019-12-25 11:04 | 0 | 0 | 0 | 0 | 2.747% | 2.7951 | 2019-12-25 11:04 | 0
Beauly | Conon Bridge | 513 | FALSE | -('513~TR1~MW~AI'+'513~TR2~MW~AI') | No Data | 3.408 | 4.912 | 5.76 | Missing Data | 2019-07-01 17:45 | 2019-10-30 17:47 | 2019-11-19 17:36 | 0 | 0 | 0 | 0 | 21.7% | 5.76 | 2019-11-19 17:36 | 0
Beauly | Dingwall | 515 | TRUE | ('515~T1~AMPS~AI'+'515~T2~AMPS~AI')*1.732*0.011 | 7.2204 | 6.0578 | 7.7692 | 8.9665 | 2019-04-02 08:06 | 2019-06-24 16:54 | 2019-10-31 11:04 | 2019-11-19 11:32 | 0.1861 | 0.16842 | 0.18796 | 0.16284 | 2.473% | 8.9665 | 2019-11-19 11:32 | 0.16284
Beauly | Kiltarlity | 520 | FALSE | ('520~001~AMPS~AI'+'520~002~AMPS~AI')*1.732*0.011 | 1.2474 | 0.81692 | 1.2168 | 1.4349 | 2019-04-03 20:03 | 2019-08-19 19:02 | 2019-10-31 20:03 | 2019-11-19 19:06 | 0 | 0 | 0 | 0 | 4.945% | 1.4349 | 2019-11-19 19:06 | 0
Beauly | Marybank | 538 | FALSE | ('538~TR1~AMPS~AI')*1.732*0.011 | 1.1967 | 0.90366 | 1.0868 | 1.3677 | 2019-04-09 07:09 | 2019-06-06 08:10 | 2019-10-31 07:56 | 2019-12-25 12:10 | 0 | 0 | 0 | 0 | 4.121% | 1.3677 | 2019-12-25 12:10 | 0
Beauly | Muir Of Ord | 547 | FALSE | ('547~T1_T2~AMPS~AI')*1.732*0.011 | 11.3029 | 10.6052 | 12.2015 | 12.6313 | 2019-05-07 07:23 | 2019-06-05 18:16 | 2019-10-30 20:17 | 2019-12-18 20:06 | 0 | 0 | 0 | 0 | 1.648% | 12.6313 | 2019-12-18 20:06 | 0
Beauly | Muirend | 542 | FALSE | ('542~TR1~AMPS~AI')*1.732*0.011 | 2.0522 | 1.621 | 2.2978 | 2.6198 | 2019-04-04 07:20 | 2019-06-05 18:14 | 2019-10-29 18:19 | 2019-12-25 11:04 | 0 | 0 | 0 | 0 | 1.923% | 2.6198 | 2019-12-25 11:04 | 0
Beauly | North Kessock | 558 | FALSE | ('558~TR1~AMPS~AI')*1.732*0.011 | 1.1767 | 0.92974 | 1.1614 | 1.3474 | 2019-04-03 18:56 | 2019-06-05 18:19 | 2019-10-29 17:58 | 2020-01-13 17:40 | 0 | 0 | 0 | 0 | 4.396% | 1.3474 | 2020-01-13 17:40 | 0
Boat of Garten | Aviemore | 704 | FALSE | ('704~TR1~AMPSA~AI'+'704~TR2~AMPSA~AI')*1.741*0.011 | 8.1595 | 5.9257 | 7.7872 | 9.0437 | 2019-04-03 10:32 | 2019-06-12 17:27 | 2019-10-30 19:46 | 2020-02-13 19:36 | 0 | 0 | 0 | 0 | 1.648% | 9.0437 | 2020-02-13 19:36 | 0
Boat of Garten | Ballindalloch | 706 | FALSE | -('706~TR1~MW~AI'+'706~TR2~MW~AI') | 3.84 | 2.512 | 3.808 | 4.08 | 2019-04-01 19:38 | 2019-06-13 09:39 | 2019-10-31 07:54 | 2019-11-18 16:52 | 0 | 0 | 0 | 0 | 2.198% | 4.08 | 2019-11-18 16:52 | 0
Boat of Garten | Boat Of Garten 11 Kv | 708 | FALSE | -('707~T1~MW~AI'+'707~T2~MW~AI') | 3.0562 | 2.4875 | 2.6339 | 3.4541 | 2019-04-02 06:55 | 2019-06-06 07:11 | 2019-10-03 10:43 | 2020-02-18 11:06 | 0 | 0 | 0 | 0 | 3.846% | 3.4541 | 2020-02-18 11:06 | 0
Boat of Garten | Dalwhinnie | 777 | FALSE | ('777~011~AMPS~AI')*1.732*0.011 | 0.67182 | 0.56295 | 0.6895 | 0.78813 | 2019-04-03 07:19 | 2019-06-13 09:55 | 2019-10-11 07:11 | 2020-01-08 10:41 | 0 | 0 | 0 | 0 | 1.648% | 0.78813 | 2020-01-08 10:41 | 0
Boat of Garten | Grantown | 722 | FALSE | ('722~T1_T2~AMPS~AI')*1.732*0.011 | 4.8225 | 3.9183 | 5.109 | 6.2997 | 2019-04-04 10:34 | 2019-06-13 10:47 | 2019-10-31 03:37 | 2019-12-23 03:33 | 0 | 0 | 0 | 0 | 1.923% | 6.2997 | 2019-12-23 03:33 | 0
Boat of Garten | Kingussie | 727 | FALSE | -('727~1H0~MW~AI'+'727~2H0~MW~AI') | 3.416 | 2.804 | 3.62 | 4.696 | 2019-04-01 19:35 | 2019-06-12 19:36 | 2019-10-30 19:33 | 2019-12-01 11:03 | 0 | 0 | 0 | 0 | 2.473% | 4.696 | 2019-12-01 11:03 | 0
Boat of Garten | Tomatin | 738 | FALSE | ('738~1H0~AMPS~AI')*1.732*0.033 | 0.69967 | 0.55974 | 0.75564 | 0.86759 | 2019-04-03 13:20 | 2019-06-04 08:04 | 2019-10-30 08:40 | 2019-11-20 18:37 | 0 | 0 | 0 | 0 | 4.67% | 0.86759 | 2019-11-20 18:37 | 0
Braco West | Callander | 210 | TRUE | ('210~002~AMPS~AI'+'210~003~AMPS~AI'+'210~004~AMPS~AI'+'210~005~AMPS~AI'+'210~006~AMPS~AI'+'210~007~AMPS~AI')*1.732*0.011 | 4.184 | 3.6973 | 4.8275 | 5.2485 | 2019-04-15 08:16 | 2019-07-09 11:35 | 2019-10-28 08:31 | 2019-11-21 12:43 | 0 | 0.016749 | 0.072579 | 0 | 2.473% | 5.2485 | 2019-11-21 12:43 | 0
Braco West | Crieff | 208 | FALSE | ('208~T1_T2_SU~AMPS~AI')*1.732*0.011 | 5.9607 | 4.5653 | 6.2049 | 8.2143 | 2019-05-08 17:25 | 2019-06-03 17:26 | 2019-10-28 17:30 | 2020-03-02 18:51 | 0 | 0 | 0 | 0 | 3.846% | 8.2143 | 2020-03-02 18:51 | 0
Braco West | Dunblane | 209 | FALSE | ('209~SUMM~AMPS~AI')*1.732*0.011 | 7.5225 | 6.6126 | 8.5879 | 9.3825 | 2019-04-01 19:59 | 2019-06-12 18:01 | 2019-10-31 17:50 | 2019-12-02 17:40 | 0 | 0 | 0 | 0 | 2.473% | 9.3825 | 2019-12-02 17:40 | 0
Braco West | Forteviot | 253 | FALSE | -('253~TR1~MW~AI') | 1.4685 | 1.2337 | 1.5719 | 1.8505 | 2019-04-03 12:23 | 2019-06-05 18:05 | 2019-10-28 17:39 | 2019-11-19 18:02 | 0 | 0 | 0 | 0 | 1.923% | 1.8505 | 2019-11-19 18:02 | 0
Braco West | Gleneagles | 207 | FALSE | ('207~T1_11~AMPS~AI'+'207~T2_11~AMPS~AI')*1.732*0.011 | 9.4888 | 8.7818 | 10.1586 | 11.4052 | 2019-04-07 12:12 | 2019-06-12 18:03 | 2019-10-30 17:25 | 2020-01-09 17:27 | 0 | 0 | 0 | 0 | 2.747% | 11.4052 | 2020-01-09 17:27 | 0
Braco West | Kippen | 211 | FALSE | ('211~11KV~AMPS~AI')*1.732*0.011 | 3.4777 | 2.6149 | 3.9091 | 4.579 | 2019-04-04 07:16 | 2019-06-12 17:22 | 2019-10-30 17:19 | 2019-11-19 07:18 | 0 | 0 | 0 | 0 | 1.923% | 4.579 | 2019-11-19 07:18 | 0
Bridge of Dun | Brechin | 73 | FALSE | -('073~TR1~MW~AI'+'073~TR2~MW~AI') | 5.8713 | 4.8238 | 6.3497 | 7.1433 | 2019-04-03 11:34 | 2019-06-24 16:45 | 2019-10-30 16:59 | 2019-11-19 17:00 | 0.22327 | 0.026979 | 0.00093031 | 0.00093031 | 1.648% | 7.1433 | 2019-11-19 17:00 | 0.00093031
Bridge of Dun | Bridge Of Dun 11Kv | 72 | FALSE | ('072~T1_11~AMPS~AI')*1.732*0.011 | 0.47539 | 0.72843 | 0.75169 | 0.64284 | 2019-04-17 20:02 | 2019-08-30 14:49 | 2019-09-09 18:07 | 2019-11-06 17:16 | 0 | 0 | 0 | 0 | 6.593% | 0.75169 | 2019-09-09 18:07 | 0
Bridge of Dun | Inchbare | 76 | FALSE | ('076~TR1~AMPS~AI')*1.732*0.011 | 0.97546 | 0.83829 | 1.0517 | 1.1126 | 2019-04-01 13:49 | 2019-06-24 09:48 | 2019-10-31 08:48 | 2019-11-19 15:53 | 0 | 0 | 0 | 0 | 2.473% | 1.1126 | 2019-11-19 15:53 | 0
Bridge of Dun | Logie Pert | 77 | FALSE | -('077~TR1~MW~AI') | 1.0117 | 1.4199 | 1.48 | 1.2937 | 2019-04-03 13:17 | 2019-08-28 16:01 | 2019-10-01 17:11 | 2019-11-15 14:19 | 0.14144 | 0.1526 | 0.14051 | 0.15074 | 3.846% | 1.48 | 2019-10-01 17:11 | 0.14051
Bridge of Dun | Mill Rd Montrose | 75 | FALSE | -('075~TR1~MW~AI'+'075~TR2~MW~AI') | 5.3901 | 5.0211 | 5.6949 | 6.5772 | 2019-04-06 11:37 | 2019-06-13 11:33 | 2019-10-30 16:51 | 2020-02-24 12:44 | 0 | 0 | 0 | 0 | 3.022% | 6.5772 | 2020-02-24 12:44 | 0
Bridge of Dun | Montrose North | 74 | FALSE | ('074~T1_T2_11~AMPS~AI')*1.732*0.011 | 7.224 | 5.9389 | 7.4027 | 8.318 | 2019-04-03 11:35 | 2019-08-20 17:25 | 2019-10-30 17:18 | 2019-12-16 17:01 | 0 | 0 | 0 | 0 | 2.747% | 8.318 | 2019-12-16 17:01 | 0
Bridge of Dun | St Cyrus | 952 | TRUE | ('952~common~AMPS~AI')*1.732*0.011 | 4.173 | 4.0656 | 4.0853 | 4.3589 | 2019-04-03 00:44 | 2019-08-29 13:28 | 2019-09-05 01:18 | 2020-02-20 00:24 | 2.1283 | 1.9637 | 1.9538 | 3.4724 | 13.74% | 4.3589 | 2020-02-20 00:24 | 3.4724
Broadford | Achintee | 624 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Broadford | Broadford | 637 | FALSE | -('627~T1~MW~AI') | 1.5483 | 1.2324 | 1.4976 | 1.638 | 2019-04-03 13:55 | 2019-06-06 18:58 | 2019-10-30 18:44 | 2020-03-16 15:04 | 0 | 0 | 0 | 0 | 2.747% | 1.638 | 2020-03-16 15:04 | 0
Broadford | Kishornhill | 633 | FALSE | ('633~1H0~AMPS~AI')*1.732*0.033 | 0.97943 | 0.75556 | 1.0354 | 1.3152 | 2019-04-09 03:32 | 2019-06-17 15:04 | 2019-10-21 12:04 | 2019-12-01 03:32 | 0 | 0 | 0 | 0 | 5.495% | 1.3152 | 2019-12-01 03:32 | 0
Broadford | Kyle | 634 | FALSE | ('634~T1_T2~AMPS~AI')*1.732*0.011 | 2.1335 | 1.9172 | 2.1768 | 2.4963 | 2019-04-03 14:58 | 2019-06-06 18:19 | 2019-10-30 18:54 | 2020-02-26 19:35 | 0 | 0 | 0 | 0 | 1.923% | 2.4963 | 2020-02-26 19:35 | 0
Broadford | Lower Ollach | 623 | FALSE | ('623~11KV~AMPS~AI')*1.732*0.011 | 0.85257 | 0.76327 | 0.88048 | 0.97187 | 2019-04-06 18:45 | 2019-06-05 20:43 | 2019-10-28 20:07 | 2020-02-12 19:04 | 0 | 0 | 0 | 0 | 2.473% | 0.97187 | 2020-02-12 19:04 | 0
Broadford | Nostie Bridge | 636 | FALSE | ('636~T1~AMPS~AI')*1.732*0.011 | 1.9162 | 0.91174 | 1.5284 | 2.17 | 2019-05-09 07:24 | 2019-07-01 19:06 | 2019-10-09 18:09 | 2019-12-01 13:42 | 0 | 0 | 0 | 0 | 22.53% | 2.17 | 2019-12-01 13:42 | 0
Broadford | Shieldaig | 641 | FALSE | ('641~11KV~AMPS~AI')*1.732*0.011 | 0.53108 | 0.70206 | 0.72649 | 0.72998 | 2019-04-03 | 2019-08-31 02:40 | 2019-09-02 02:29 | 2020-02-17 12:59 | 0 | 0 | 0 | 0 | 14.84% | 0.72998 | 2020-02-17 12:59 | 0
Broadford | Skulamus | 639 | FALSE | ('639~T1~AMPS~AI')*1.732*0.011 | 2.4776 | 1.8439 | 2.3066 | 2.6725 | 2019-04-03 20:04 | 2019-06-05 20:05 | 2019-10-30 18:33 | 2020-03-12 18:33 | 0 | 0 | 0 | 0 | 3.297% | 2.6725 | 2020-03-12 18:33 | 0
Brora | Benbraggie Mast | 524 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Brora | Brora | 550 | FALSE | -('550~T1_T2~MW~AI') | 1.94 | 1.3522 | 1.7428 | 2.1892 | 2019-04-03 07:22 | 2019-06-26 08:32 | 2019-10-31 20:19 | 2019-12-25 11:32 | 0 | 0 | 0 | 0 | 1.923% | 2.1892 | 2019-12-25 11:32 | 0
Brora | Dornoch | 557 | FALSE | ('557~T1~AMPS~AI')*1.732*0.011 | 3.784 | 2.8131 | 3.6671 | 4.0885 | 2019-04-03 12:40 | 2019-06-06 12:11 | 2019-10-31 07:12 | 2019-12-18 07:25 | 0 | 0 | 0 | 0 | 2.473% | 4.0885 | 2019-12-18 07:25 | 0
Brora | Golspie | 525 | FALSE | -('525~T1~MW~AI') | 1.8423 | 1.3237 | 1.564 | 2.0152 | 2019-04-03 12:07 | 2019-06-13 12:29 | 2019-10-31 11:05 | 2020-01-13 11:36 | 0 | 0 | 0 | 0 | 3.022% | 2.0152 | 2020-01-13 11:36 | 0
Brora | Helmsdale | 560 | FALSE | -('560~TR1~MW~AI') | 0.88142 | 0.72917 | 0.79328 | 1.0176 | 2019-04-07 12:43 | 2019-07-18 19:47 | 2019-10-27 11:23 | 2020-01-19 11:17 | 0 | 0 | 0 | 0 | 4.396% | 1.0176 | 2020-01-19 11:17 | 0
Burghmuir | Burghmuir | 246 | FALSE | ('246~T1_T2_11~AMPS~AI')*1.732*0.011 | 7.2132 | 6.4986 | 8.6425 | 9.2454 | 2019-04-17 10:46 | 2019-06-06 17:11 | 2019-10-30 17:19 | 2020-01-29 17:28 | 0 | 0 | 0 | 0 | 1.648% | 9.2454 | 2020-01-29 17:28 | 0
Burghmuir | Goodlyburn | 249 | FALSE | -('249~T1~MW~AI'+'249~T2~MW~AI') | 7.328 | 6.496 | 7.904 | 9.344 | 2019-04-01 11:42 | 2019-08-26 08:02 | 2019-10-29 17:53 | 2020-01-23 12:59 | 0 | 0 | 0 | 0 | 2.747% | 9.344 | 2020-01-23 12:59 | 0
Burghmuir | Inveralmond | 240 | FALSE | -('240~TR1~MW~AI'+'240~TR2~MW~AI') | No Data | No Data | No Data | 6.144 | Missing Data | Missing Data | Missing Data | 2019-11-25 13:48 | 0 | 0 | 0 | 0 | 58.79% | 6.144 | 2019-11-25 13:48 | 0
Burghmuir | Redgorton | 270 | FALSE | ('270~common~AMPS~AI')*1.732*0.011 | 3.3052 | 2.4963 | 3.4702 | 4.651 | 2019-04-16 17:10 | 2019-06-25 16:54 | 2019-10-30 17:27 | 2019-11-20 17:28 | 0 | 0 | 0 | 0 | 2.473% | 4.651 | 2019-11-20 17:28 | 0
Burghmuir | Thimblerow | 248 | FALSE | ('248~002~AMPS~AI'+'248~003~AMPS~AI'+'248~005~AMPS~AI'+'248~006~AMPS~AI'+'248~007~AMPS~AI'+'248~008~AMPS~AI'+'248~009~AMPS~AI'+'248~010~AMPS~AI'+'248~011~AMPS~AI')*1.732*0.011 | 11.45 | 9.4853 | 11.1874 | 13.0543 | 2019-04-03 12:16 | 2019-06-05 12:30 | 2019-10-30 12:01 | 2019-11-19 12:24 | 0 | 0 | 0 | 0 | 1.923% | 13.0543 | 2019-11-19 12:24 | 0
Carradale | Balliekine | 372 | FALSE | ('372~SS_LOAD~AMPS~AI')*1.732*0.011 | 0.59831 | 0.51084 | 0.51084 | 0.52852 | 2019-04-14 03:09 | 2019-06-04 09:24 | 2019-09-12 11:38 | 2020-03-04 19:10 | 0 | 0 | 0 | 0 | 10.16% | 0.59831 | 2019-04-14 03:09 | 0
Carradale | Ballure | 318 | TRUE | ('318~common~AMPS~AI')*1.732*0.011 | 1.0858 | 1.0137 | 1.0009 | 1.3811 | 2019-04-16 18:52 | 2019-06-03 01:56 | 2019-10-29 18:39 | 2020-02-24 14:11 | 0 | 0.31934 | 0.13623 | 0.3252 | 5.769% | 1.3811 | 2020-02-24 14:11 | 0.3252
Carradale | Brodick | 370 | FALSE | ('370~T1~MW~AI'+'370~T2~MW~AI') | 5.0759 | 3.3618 | 4.3844 | 5.0006 | 2019-04-15 08:10 | 2019-06-12 17:19 | 2019-10-30 18:35 | 2019-11-30 18:52 | 0 | 0 | 0 | 0 | 2.198% | 5.0759 | 2019-04-15 08:10 | 0
Carradale | Campbeltown | 312 | FALSE | -('312~TR1~MW~AI'+'312~TR2~MW~AI') | 5.9169 | 5.0041 | 5.216 | 6.7971 | 2019-04-04 09:49 | 2019-06-17 13:43 | 2019-10-30 18:44 | 2019-12-13 18:17 | 0 | 0 | 0 | 0 | 3.571% | 6.7971 | 2019-12-13 18:17 | 0
Carradale | Claonaig | 338 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Carradale | Dippen | 336 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Carradale | Machrie | 373 | FALSE | ('373~011~AMPS~AI')*1.732*0.011 | 1.5974 | 1.134 | 1.573 | 1.9066 | 2019-04-01 18:38 | 2019-06-03 18:35 | 2019-10-29 18:48 | 2019-12-31 19:00 | 0 | 0 | 0 | 0 | 2.747% | 1.9066 | 2019-12-31 19:00 | 0
Carradale | Westpark Fergus | 349 | FALSE | ('349~11KV_LOAD~AMPS~AI')*1.732*0.011 | 0.96601 | 0.90844 | 0.79838 | 0.75948 | 2019-05-31 11:30 | 2019-06-04 00:56 | 2019-09-11 08:50 | 2019-11-01 12:52 | 0 | 0 | 0 | 0 | 17.58% | 0.96601 | 2019-05-31 11:30 | 0
Carradale | Whiting Bay | 371 | FALSE | ('371~T1_11KV~AMPS~AI')*1.732*0.011 | 2.169 | 1.3776 | 1.9875 | 2.2416 | 2019-04-03 19:50 | 2019-06-05 08:12 | 2019-10-26 18:43 | 2020-02-17 18:36 | 0 | 0 | 0 | 0 | 3.846% | 2.2416 | 2020-02-17 18:36 | 0
Cassley | Cannich | 511 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Cassley | Overscaig | 563 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Cassley | Rhiconich | 544 | FALSE | ('544~T1_T2~AMPS~AI')*1.732*0.011 | 1.6526 | 1.4279 | 1.5144 | 1.8298 | 2019-04-08 20:23 | 2019-06-12 18:34 | 2019-10-29 20:06 | 2020-03-07 02:44 | 0 | 0 | 0 | 0 | 2.473% | 1.8298 | 2020-03-07 02:44 | 0
Charleston | Buttars Loan | 005 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Charleston | Charleston | 002 | FALSE | ('002~T1_T2_11~AMPS~AI')*1.732*0.011 | 5.4508 | 9.7357 | 8.9882 | 5.6126 | 2019-04-16 13:23 | 2019-07-24 15:56 | 2019-09-03 12:26 | 2019-11-19 12:09 | 0 | 0 | 0 | 0 | 2.198% | 9.7357 | 2019-07-24 15:56 | 0
Charleston | Gourdie | 004 | FALSE | ('004~TR1~MW~AI') | 2.2386 | 1.9434 | 2.6691 | 2.8044 | 2019-04-01 18:02 | 2019-08-10 18:26 | 2019-10-28 18:35 | 2019-11-20 18:37 | 0 | 0 | 0 | 0 | 2.198% | 2.8044 | 2019-11-20 18:37 | 0
Charleston | Menzieshill | 003 | FALSE | -('003~TR1~MW~AI'+'003~TR2~MW~AI') | 8.8306 | 5.2823 | 7.7319 | 9.8185 | 2019-05-02 12:35 | 2019-06-12 17:17 | 2019-10-18 07:23 | 2020-02-19 09:17 | 0 | 0 | 0 | 0 | 15.66% | 9.8185 | 2020-02-19 09:17 | 0
Charleston | Ninewells | 006 | FALSE | ('006~11~AMPS~AI')*1.732*0.011 | 5.0235 | 4.2197 | 4.9788 | 5.7491 | 2019-04-04 09:40 | 2019-08-09 11:13 | 2019-10-29 18:02 | 2019-11-19 17:02 | 0 | 0 | 0 | 0 | 2.198% | 5.7491 | 2019-11-19 17:02 | 0
Clachan | Butterbridge | 387 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Clachan | Douglas Pier | 388 | FALSE | ('388~TRANS~AMPS~AI')*1.732*0.011 | 1.0425 | 0.57597 | 0.79632 | 0.89882 | 2019-04-06 18:48 | 2019-07-05 13:19 | 2019-10-29 18:33 | 2019-11-18 18:44 | 0 | 0 | 0 | 0 | 7.143% | 1.0425 | 2019-04-06 18:48 | 0
Clachan | Inveraray | 321 | FALSE | -('321~TR1~MW~AI') | 0.896 | 0.664 | 0.896 | 0.872 | 2019-04-06 13:18 | 2019-06-01 13:46 | 2019-10-31 13:22 | 2020-02-28 14:02 | 0 | 0 | 0 | 0 | 1.923% | 0.896 | 2019-04-06 13:18 | 0
Clachan | Lochgoilhead | 369 | TRUE | ('369~T1~AMPS~AI')*1.732*0.033 | 0.52375 | 1.8232 | 1.7308 | 2.4153 | 2019-05-25 23:23 | 2019-08-20 00:06 | 2019-10-17 23:58 | 2020-01-16 08:49 | 0.34514 | 0.96473 | 0.97031 | 1.2745 | 39.29% | 2.4153 | 2020-01-16 08:49 | 1.2745
Clachan | Strachur | 382 | FALSE | ('382~11KV~AMPS~AI')*1.732*0.011 | 0.69718 | 0.43129 | 0.7216 | 0.90794 | 2019-04-04 03:41 | 2019-06-05 13:33 | 2019-10-30 03:34 | 2019-12-01 03:33 | 0 | 0 | 0 | 0 | 1.648% | 0.90794 | 2019-12-01 03:33 | 0
Clayhills | Balnagask | 808 | FALSE | -('808~TR1~MW~AI') | No Data | No Data | No Data | 4.6516 | Missing Data | Missing Data | Missing Data | 2019-12-13 14:23 | 0 | 0 | 0 | 0 | 61.26% | 4.6516 | 2019-12-13 14:23 | 0
Clayhills | Clayhills | 826 | FALSE | ('826~COMMON~AMPS~AI')*1.732*0.011 | 13.0276 | 11.4647 | 12.8657 | 14.5012 | 2019-04-03 11:33 | 2019-06-13 15:07 | 2019-10-30 16:58 | 2019-11-19 16:54 | 0 | 0 | 0 | 0 | 1.923% | 14.5012 | 2019-11-19 16:54 | 0
Clayhills | Commerce Street | 827 | FALSE | -('827~TR1~MW~AI'+'827~TR2~MW~AI') | 12.8485 | 11.9394 | 12.2424 | 14.101 | 2019-04-03 11:34 | 2019-06-12 11:39 | 2019-10-29 12:00 | 2019-12-11 15:06 | 0 | 0 | 0 | 0 | 1.648% | 14.101 | 2019-12-11 15:06 | 0
Clayhills | Craiginches | 832 | FALSE | -('832~TR1~MW~AI'+'832~TR2~MW~AI') | 15.36 | 14.412 | 12.216 | 12.264 | 2019-05-08 11:25 | 2019-06-05 11:24 | 2019-09-30 10:44 | 2019-11-19 11:00 | 0 | 0 | 0 | 0 | 4.396% | 15.36 | 2019-05-08 11:25 | 0
Coupar Angus | Alyth | 258 | FALSE | ('258~011~AMPS~AI')*1.732*0.011 | 2.4127 | 2.1052 | 2.7883 | 2.8774 | 2019-04-15 17:33 | 2019-06-13 17:06 | 2019-10-29 17:20 | 2019-12-31 17:22 | 0 | 0 | 0 | 0 | 3.297% | 2.8774 | 2019-12-31 17:22 | 0
Coupar Angus | Blairgowrie | 257 | FALSE | -('257~TR1~MW~AI'+'257~TR2~MW~AI') | No Data | No Data | No Data | 7.3016 | Missing Data | Missing Data | Missing Data | 2020-01-10 17:45 | 0 | 0 | 0 | 0.32283 | 70.6% | 7.3016 | 2020-01-10 17:45 | 0.32283
Coupar Angus | Caputh | 256 | FALSE | ('256~T1~MW~AI'+'256~T2~MW~AI') | 4.296 | 3.12 | 4.264 | 5.256 | 2019-04-03 11:58 | 2019-08-30 08:33 | 2019-10-28 19:31 | 2020-02-14 12:15 | 0 | 0 | 0 | 0 | 3.022% | 5.256 | 2020-02-14 12:15 | 0
Coupar Angus | Coupar Angus | 244 | FALSE | ('243~1H0~MW~AI'+'243~2H0~MW~AI') | 4.9462 | 5.5983 | 5.6789 | 5.6955 | 2019-04-04 15:24 | 2019-08-30 19:10 | 2019-10-30 17:03 | 2019-11-27 17:00 | 0.38616 | 0.090258 | 0.014888 | 0.01954 | 3.022% | 5.6955 | 2019-11-27 17:00 | 0.01954
Coupar Angus | Dalrulzion | 259 | FALSE | ('259~T1~AMPS~AI'+'259~T2~AMPS~AI')*1.732*0.011 | 1.8655 | 1.5867 | 1.8769 | 2.0385 | 2019-04-16 09:07 | 2019-08-30 08:21 | 2019-10-25 00:20 | 2020-01-16 11:52 | 0 | 0 | 0 | 0 | 12.09% | 2.0385 | 2020-01-16 11:52 | 0
Coupar Angus | Leoch | 90 | FALSE | -('090~TR1~MW~AI') | 1.9884 | 1.6929 | 2.2029 | 2.8261 | 2019-04-01 18:54 | 2019-06-12 09:33 | 2019-10-30 17:50 | 2019-12-22 17:35 | 0.07242 | 1.1329 | 0.03088 | 0.002081 | 2.747% | 2.8261 | 2019-12-22 17:35 | 0.002081
Craigiebuckler | Craigiebuckler | 830 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Craigiebuckler | Craigton | 834 | TRUE | [9 empty] | 0.93775 | 0.93775 | 0.93775 | 0.93775
Craigiebuckler | Culter | 836 | FALSE | -('836~TR1~MW~AI'+'836~TR2~MW~AI') | 4.4062 | 3.8477 | 5.0972 | 5.6948 | 2019-04-02 18:05 | 2019-06-12 18:24 | 2019-10-28 18:09 | 2019-11-19 17:42 | 0.15564 | 0.33498 | 0.01256 | 0.00864 | 2.198% | 5.6948 | 2019-11-19 17:42 | 0.00864
Craigiebuckler | Ruthrieston | 939 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Dudhope | Constable Street | 32 | FALSE | -('032~TR1~MW~AI'+'032~TR2~MW~AI') | 11.8093 | 10.6216 | 11.7973 | 14.7727 | 2019-04-04 11:48 | 2019-06-24 16:05 | 2019-10-18 14:40 | 2020-01-29 13:33 | 0 | 0 | 0 | 0 | 4.121% | 14.7727 | 2020-01-29 13:33 | 0
Dunbeath Dube | Dunbeath Grid | 595 | TRUE | [9 empty] | 2.508 | 2.508 | 2.508 | 2.508
Dudhope | Rosebank Street | 33 | FALSE | -('033~TR1~MW~AI'+'033~TR2~MW~AI') | 9.5192 | 8.0522 | 9.9756 | 12.0946 | 2019-04-04 12:03 | 2019-06-13 16:56 | 2019-10-29 18:32 | 2020-01-16 15:48 | 0 | 0 | 0 | 0 | 2.747% | 12.0946 | 2020-01-16 15:48 | 0
Dunvegan | Drynoch | 629 | FALSE | ('629~T1~AMPS~AI')*1.732*0.011 | 1.2717 | 1.0362 | 1.201 | 1.3437 | 2019-04-11 08:06 | 2019-08-11 20:25 | 2019-10-29 18:52 | 2019-11-30 16:31 | 0 | 0 | 0 | 0 | 3.022% | 1.3437 | 2019-11-30 16:31 | 0
Dunvegan | Portree | 632 | FALSE | ('632~T1~AMPS~AI'+'632~T2~AMPS~AI')*1.732*0.011 | 3.9185 | 3.5259 | 3.9389 | 4.525 | 2019-04-02 11:41 | 2019-06-06 11:36 | 2019-10-30 20:18 | 2019-11-14 12:25 | 0 | 0 | 0 | 0 | 3.846% | 4.525 | 2019-11-14 12:25 | 0
Dunvegan | Uig | 640 | FALSE | ('640~11KV~AMPS~AI')*1.732*0.011 | 1.3643 | 1.1557 | 1.2003 | 1.3134 | 2019-04-03 18:36 | 2019-06-06 18:30 | 2019-10-29 18:46 | 2020-02-18 18:43 | 0 | 0 | 0 | 0 | 3.022% | 1.3643 | 2019-04-03 18:36 | 0
Dunoon | Ardyne Point | 376 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Dunoon | Bruchag | 365 | FALSE | -('365~TR1~MW~AI'+'365~TR2~MW~AI') | 3.0409 | 1.8246 | 2.5288 | 3.3611 | 2019-04-06 18:34 | 2019-06-08 16:22 | 2019-10-26 18:37 | 2020-03-07 13:19 | 0 | 0 | 0 | 0 | 4.396% | 3.3611 | 2020-03-07 13:19 | 0
Dunoon | Colintraive | 385 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Dunoon | Dunoon | 363 | FALSE | ('363~SUMM~AMPS~AI')*1.732*0.011 | 5.8987 | 4.5746 | 6.0792 | 6.9258 | 2019-04-04 13:20 | 2019-08-30 17:21 | 2019-10-28 18:37 | 2019-11-18 18:34 | 0 | 0 | 0 | 0 | 2.747% | 6.9258 | 2019-11-18 18:34 | 0
Dunoon | Glendaruel | 383 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Dunoon | Innellan | 379 | FALSE | ('379~SUMM~AMPS~AI')*1.732*0.011 | 0.86792 | 0.65024 | Unreliable Data | Unreliable Data | 2019-04-03 18:51 | 2019-08-21 17:23 | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 2.198% | 0.86792 | 2019-04-03 18:51 | 0
Dunoon | Kames | 366 | FALSE | ('366~11KV_SS~AMPS~AI')*1.732*0.011 | 0.4913 | 0.27078 | 0.46339 | 0.59738 | 2019-04-05 03:42 | 2019-08-15 18:29 | 2019-10-26 18:31 | 2019-11-30 18:41 | 0 | 0 | 0 | 0 | 3.846% | 0.59738 | 2019-11-30 18:41 | 0
Dunoon | Newton | 384 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Dunoon | Otter Ferry | 375 | FALSE | ('375~11KV_SS~AMPS~AI')*1.732*0.011 | 1.1152 | 0.90724 | 1.0496 | 1.2897 | 2019-04-07 18:57 | 2019-06-18 18:17 | 2019-10-26 18:37 | 2020-01-01 14:08 | 0 | 0 | 0 | 0 | 2.747% | 1.2897 | 2020-01-01 14:08 | 0
Dunoon | Rothesay | 362 | FALSE | ('362~T1_T2~AMPS~AI')*1.732*0.011 | 3.8959 | 3.0977 | 4.094 | 4.8336 | 2019-04-04 12:38 | 2019-08-30 17:49 | 2019-10-30 17:50 | 2020-02-11 17:16 | 0 | 0 | 0 | 0 | 2.473% | 4.8336 | 2020-02-11 17:16 | 0
Dunoon | Sandbank | 364 | FALSE | -('364~T1~MW~AI'+'364~T2~MW~AI') | 3.1157 | 1.9813 | 3.0263 | 3.5504 | 2019-04-06 18:40 | 2019-07-11 16:47 | 2019-10-28 18:35 | 2019-11-30 18:38 | 0 | 0.28659 | 0.083745 | 0 | 2.198% | 3.5504 | 2019-11-30 18:38 | 0
Dyce | Balmedie | 807 | TRUE | ('807~common~AMPS~AI')*1.732*0.011 | 3.5503 | 3.0596 | 3.3968 | 3.8689 | 2019-04-16 08:43 | 2019-06-13 16:52 | 2019-10-28 17:22 | 2020-01-13 17:16 | 0.11208 | 0.29113 | 0.14463 | 0.10324 | 2.198% | 3.8689 | 2020-01-13 17:16 | 0.10324
Dyce | Dyce North | 844 | FALSE | ('843~1L5~MW~AI'+'843~2L5~MW~AI') | 13.9327 | 12.8439 | 14.1662 | 16.1486 | 2019-04-03 10:43 | 2019-06-12 12:14 | 2019-10-30 09:11 | 2019-12-12 09:15 | 0.33312 | 0.49596 | 0.013027 | 0.2624 | 2.198% | 16.1486 | 2019-12-12 09:15 | 0.2624
Dyce | Ellon 11 kV | 849 | FALSE | ('849A~TR1~AMPS~AI'+'849A~TR2~AMPS~AI')*1.732*0.011 | 8.878 | 8.2476 | 9.1818 | 10.8753 | 2019-04-15 17:15 | 2019-06-12 17:18 | 2019-10-31 16:59 | 2019-11-19 17:19 | 0 | 0 | 0 | 0 | 3.297% | 10.8753 | 2019-11-19 17:19 | 0
Dyce | Kingseat | 884 | FALSE | ('884~common~AMPS~AI')*1.732*0.011 | 2.6499 | 2.2908 | 3.2133 | 3.6877 | 2019-04-08 20:02 | 2019-06-24 17:52 | 2019-10-28 17:34 | 2019-12-25 15:07 | 0 | 0 | 0 | 0 | 3.571% | 3.6877 | 2019-12-25 15:07 | 0
Dyce | Stoneywood T3 | 947 | FALSE | -('947~TR3~MW~AI') | 5.3894 | 4.6497 | 5.3884 | 5.8044 | 2019-04-14 15:31 | 2019-08-16 00:18 | 2019-10-31 09:20 | 2020-03-10 11:02 | 0 | 0 | 4.1884 | 4.1884 | 35.44% | 5.8044 | 2020-03-10 11:02 | 4.1884
Elgin | Ashgrove | 458 | FALSE | ('458~T1_T2~AMPS~AI')*1.732*0.011 | 5.682 | 5.4327 | 6.2402 | 7.4309 | 2019-04-03 16:44 | 2019-07-27 09:52 | 2019-10-31 16:53 | 2019-11-19 16:42 | 0 | 0 | 0 | 0 | 5.22% | 7.4309 | 2019-11-19 16:42 | 0
Elgin | Bilbohall | 499 | FALSE | ('499~T1_T2~AMPS~AI')*1.732*0.011 | 3.6225 | 3.7286 | 3.8179 | 4.0579 | 2019-04-14 15:35 | 2019-06-04 15:05 | 2019-09-18 12:53 | 2019-11-18 14:26 | 0 | 0 | 0 | 0 | 9.341% | 4.0579 | 2019-11-18 14:26 | 0
Elgin | Burghead | 454 | FALSE | ('454~T1_T2~AMPS~AI')*1.732*0.011 | 5.8972 | 5.2421 | 6.2582 | 6.9821 | 2019-05-05 20:04 | 2019-08-09 17:44 | 2019-10-24 18:47 | 2020-01-14 16:56 | 0 | 0 | 0 | 0 | 3.571% | 6.9821 | 2020-01-14 16:56 | 0
Elgin | Cumming Street | 457 | FALSE | ('457~T1_T2~AMPS~AI')*1.732*0.011 | 11.7213 | 10.8394 | Unreliable Data | Unreliable Data | 2019-04-03 12:17 | 2019-07-05 12:22 | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 57.69% | 11.7213 | 2019-04-03 12:17 | 0
Elgin | Elgin | 482 | FALSE | ('482~T1_T2~AMPS~AI')*1.732*0.011 | 3.5259 | 3.2291 | 3.778 | 4.5139 | 2019-04-15 17:36 | 2019-06-12 17:32 | 2019-10-31 17:03 | 2020-01-12 17:23 | 0 | 0 | 0 | 0 | 4.945% | 4.5139 | 2020-01-12 17:23 | 0
Elgin | Fochabers | 487 | FALSE | ('487~11KV~AMPS~AI')*1.732*0.011 | 5.2588 | 5.4114 | 5.8433 | 6.4182 | 2019-05-03 08:26 | 2019-06-06 09:00 | 2019-10-30 07:46 | 2019-11-19 11:04 | 0 | 0 | 0 | 0 | 1.648% | 6.4182 | 2019-11-19 11:04 | 0
Elgin | Kinloss | 453 | FALSE | ('453~T1_T2~AMPS~AI')*1.732*0.011 | 2.0503 | 1.9982 | 2.6717 | 3.148 | 2019-04-02 09:16 | 2019-08-08 14:29 | 2019-10-28 17:41 | 2020-02-25 07:13 | 0 | 0 | 0 | 0 | 7.418% | 3.148 | 2020-02-25 07:13 | 0
Elgin | Lhanbryde | 488 | FALSE | ('488~T1_T2~AMPS~AI')*1.732*0.011 | 1.0121 | 0.86329 | 1.1984 | 1.3845 | 2019-04-11 11:16 | 2019-06-13 18:11 | 2019-10-27 17:24 | 2019-12-25 11:54 | 0 | 0 | 0 | 0 | 3.571% | 1.3845 | 2019-12-25 11:54 | 0
Elgin | Lossiemouth | 455 | FALSE | ('455~T1_T2~AMPS~AI')*1.732*0.011 | 5.3593 | 4.9351 | 5.817 | 6.997 | 2019-04-04 11:35 | 2019-06-13 17:35 | 2019-10-30 17:07 | 2019-12-16 16:49 | 0 | 0 | 0 | 0 | 2.198% | 6.997 | 2019-12-16 16:49 | 0
Fasnakyle | Fasnakyle Primary | 519 | FALSE | ('FASN~T5~AMPS~AI')*1.732*0.011 | 0.51977 | 0.3621 | 0.50233 | 0.51838 | 2019-04-16 08:10 | 2019-07-04 19:21 | 2019-10-31 07:23 | 2020-03-06 07:18 | 0 | 0 | 0 | 0 | 0.8242% | 0.51977 | 2019-04-16 08:10 | 0
Fiddes | Edzell | 847 | TRUE | ('847~common~AMPS~AI')*1.732*0.011 | 2.0525 | 1.9439 | 2.154 | 2.5977 | 2019-04-02 09:08 | 2019-08-28 08:11 | 2019-10-31 12:05 | 2019-11-19 12:05 | 0 | 0 | 0 | 0 | 3.022% | 2.5977 | 2019-11-19 12:05 | 0
Fiddes | Inverbervie | 873 | FALSE | -('873~TR1~MW~AI'+'873~TR2~MW~AI') | 2.6394 | 2.3915 | 3.1724 | 3.4527 | 2019-04-17 20:13 | 2019-08-20 19:29 | 2019-10-29 17:36 | 2019-12-24 17:43 | 0.4364 | 0.52623 | 0.58353 | 0.7432 | 2.473% | 3.4527 | 2019-12-24 17:43 | 0.7432
Fiddes | Laurencekirk | 890 | FALSE | -('890~TR1~MW~AI'+'890~TR2~MW~AI') | 4.112 | 3.3384 | 4.3796 | 5.0509 | 2019-04-09 12:25 | 2019-07-04 17:55 | 2019-10-31 17:34 | 2019-11-19 16:21 | 2 | 0.26638 | 0.15564 | 0 | 2.473% | 5.0509 | 2019-11-19 16:21 | 0
Fiddes | Stonehaven | 945 | TRUE | ('945~T1~AMPS~AI'+'945~T2~AMPS~AI')*1.732*0.011 | 9.5752 | 9.0395 | 9.9983 | 11.1723 | 2019-04-16 17:22 | 2019-06-24 17:26 | 2019-10-28 17:01 | 2019-11-13 17:16 | 2.5145 | 2.7672 | 2.4979 | 2.0473 | 2.473% | 11.1723 | 2019-11-13 17:16 | 2.0473
Fort Augustus | Aberchalder | 710 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort Augustus | Bunoich | 745 | FALSE | ('745~011~AMPS~AI')*1.732*0.011 | 0.18943 | 0.15085 | 0.1634 | 0.19315 | 2019-04-03 13:49 | 2019-06-02 13:51 | 2019-10-26 17:55 | 2020-01-03 18:39 | 0 | 0 | 0 | 0 | 2.198% | 0.19315 | 2020-01-03 18:39 | 0
Fort Augustus | Drumnadrochit | 517 | TRUE | ('517~TR1~AMPS~AI')*1.732*0.011 | 2.9042 | 2.0633 | 2.2343 | 3.0892 | 2019-04-07 02:37 | 2019-06-12 23:58 | 2019-10-31 20:13 | 2020-03-25 02:25 | 1.9233 | 1.5437 | 0.13399 | 1.942 | 18.41% | 3.0892 | 2020-03-25 02:25 | 1.942
Fort Augustus | Farr Grid | 709 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort Augustus | Glen Laogh | 396 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort Augustus | Glendoe Primary | 781 | FALSE | ('781~002~AMPS~AI'+'781~003~AMPS~AI')*1.732*0.011 | 0.82578 | 0.71993 | 0.74418 | 0.83059 | 2019-04-05 19:08 | 2019-06-05 18:00 | 2019-10-30 13:27 | 2019-12-31 18:34 | 0 | 0 | 0 | 0 | 2.473% | 0.83059 | 2019-12-31 18:34 | 0
Fort Augustus | Invergarry | 766 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort Augustus | Markethill | 742 | FALSE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | No Data
Quoich | Quoich Primary | 748 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Annat | 702 | FALSE | -('702~TR1~MW~AI') | 2.3853 | 1.9851 | 2.4334 | 2.7856 | 2019-04-03 13:44 | 2019-06-14 07:30 | 2019-10-31 08:11 | 2019-12-02 13:20 | 0 | 0 | 0 | 0 | 1.923% | 2.7856 | 2019-12-02 13:20 | 0
Fort William | Arisaig | 740 | FALSE | ('740~T1~AMPS~AI')*1.732*0.011 | 0.71044 | 0.56039 | 0.59599 | 0.68182 | 2019-04-06 13:50 | 2019-07-22 17:44 | 2019-10-30 18:47 | 2020-03-16 13:18 | 0 | 0 | 0 | 0 | 3.571% | 0.71044 | 2019-04-06 13:50 | 0
Fort William | Carnoch Regulator | 782 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Corran | 744 | FALSE | ('744~11KV~AMPS~AI')*1.732*0.011 | 1.2834 | 0.96558 | 1.1772 | 1.3234 | 2019-04-16 18:47 | 2019-06-15 08:15 | 2019-10-30 18:45 | 2020-02-16 18:38 | 0 | 0 | 0 | 0 | 3.022% | 1.3234 | 2020-02-16 18:38 | 0
Fort William | Dailbeg | 720 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Fishnish | 395 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Glensanda | 714 | FALSE | ('714~common~AMPS~AI')*1.732*0.011 | 6.052 | 6.2306 | 6.253 | 5.7952 | 2019-04-10 18:12 | 2019-06-06 13:19 | 2019-09-27 15:25 | 2019-11-15 17:54 | 0 | 0 | 0 | 0 | 11.54% | 6.253 | 2019-09-27 15:25 | 0
Fort William | Glenuig | 756 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Inverlochy | 724 | FALSE | -('724~TR1~MW~AI'+'724~TR2~MW~AI') | 7.8252 | 6.5972 | 7.2339 | 10.068 | 2019-04-16 13:25 | 2019-06-02 13:26 | 2019-10-29 17:21 | 2019-11-20 13:56 | 0.061413 | 0.86909 | 0.069787 | 0.15818 | 3.846% | 10.068 | 2019-11-20 13:56 | 0.15818
Fort William | Kingairloch | 771 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Kinlochmoidart | 754 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Liddesdale | 721 | FALSE | ('721~016~AMPS~AI')*1.732*0.011 | 0.68513 | 0.57768 | 0.69489 | 0.82466 | 2019-04-07 17:47 | 2019-06-24 17:57 | 2019-10-28 20:05 | 2020-02-18 20:15 | 0 | 0 | 0 | 0 | 1.923% | 0.82466 | 2020-02-18 20:15 | 0
Fort William | Lochailort Regulator | 730 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Lochaline | 747 | FALSE | ('747~T1_POWER~MVA~AI') | 1 | 0.625 | 0.7875 | 0.75 | 2019-04-03 14:20 | 2019-08-20 10:15 | 2019-10-02 07:27 | 2019-12-03 09:30 | 0 | 0 | 0 | 0 | 26.1% | 1 | 2019-04-03 14:20 | 0
Fort William | Mallaig | 731 | FALSE | ('731~TR1~AMPS~AI')*1.732*0.011 | 1.286 | 1.3241 | 1.0955 | 1.7052 | 2019-05-08 18:37 | 2019-06-18 18:37 | 2019-10-31 13:21 | 2019-12-08 03:44 | 0 | 0 | 0 | 0 | 6.319% | 1.7052 | 2019-12-08 03:44 | 0
Fort William | Pinegrove | 734 | FALSE | ('734~T1_T2~AMPS~AI')*1.732*0.011 | 5.5444 | 4.5471 | 5.6895 | 6.4709 | 2019-04-03 14:19 | 2019-06-03 13:19 | 2019-10-31 13:19 | 2019-12-01 13:21 | 0 | 0 | 0 | 0 | 1.648% | 6.4709 | 2019-12-01 13:21 | 0
Fort William | Poor House | 753 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Rahoy | 732 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Salen 2 | 749 | FALSE | ('749~T1~AMPS~AI')*1.732*0.011 | 2.8571 | 1.8759 | 2.3937 | 2.7692 | 2019-04-06 13:25 | 2019-07-03 21:19 | 2019-10-29 18:40 | 2019-11-13 18:36 | 0 | 0 | 0 | 0 | 2.473% | 2.8571 | 2019-04-06 13:25 | 0
Fort William | Shona Beag | 755 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Strontian | 751 | FALSE | ('751~11KV~AMPS~AI')*1.732*0.011 | 0.78581 | 0.5241 | 0.63367 | 0.94492 | 2019-04-03 13:55 | 2019-06-06 13:20 | 2019-10-03 07:54 | 2019-11-19 13:24 | 0 | 0 | 0 | 0 | 4.121% | 0.94492 | 2019-11-19 13:24 | 0
Fraserburgh | Cairnbulg | 821 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Fraserburgh | Fraserburgh | 854 | FALSE | -('854~TR1~MW~AI'+'854~TR3~MW~AI') | 14.7345 | 13.8851 | 16.2958 | 17.696 | 2019-04-03 11:51 | 2019-06-06 11:00 | 2019-10-29 17:01 | 2019-12-17 11:42 | 0 | 0 | 0.0078144 | 0 | 1.648% | 17.696 | 2019-12-17 11:42 | 0
Glenagnes | Overgate | 24 | FALSE | -('024~TR1~MW~AI'+'024~TR2~MW~AI'+'024~TR3~MW~AI') | 13.6517 | 12.8015 | 13.4913 | 15.4003 | 2019-05-09 09:43 | 2019-07-23 15:39 | 2019-10-22 12:09 | 2020-02-03 15:05 | 0 | 0 | 0 | 0 | 1.923% | 15.4003 | 2020-02-03 15:05 | 0
Glenagnes | Walton | 25 | FALSE | ('025~T2_T3_11~AMPS~AI')*1.732*0.011 | 4.1028 | 3.1755 | 4.0776 | 5.0991 | 2019-04-16 12:15 | 2019-06-13 12:23 | 2019-10-29 18:54 | 2019-12-17 12:02 | 0 | 0 | 0 | 0 | 2.198% | 5.0991 | 2019-12-17 12:02 | 0
Grudie Bridge | Achiltibuie | 505 | FALSE | ('505~T1~MVA~AI') | 0.81448 | 0.81262 | 0.80623 | 0.91987 | 2019-04-03 21:24 | 2019-08-19 10:00 | 2019-09-12 05:55 | 2020-02-14 16:52 | 0.96028 | 0.73882 | 0.73975 | 0.86071 | 7.143% | 0.91987 | 2020-02-14 16:52 | 0.86071
Grudie Bridge | Achnasheen | 798 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Aultbea | 504 | FALSE | -('504~T1~MW~AI') | 1.6506 | 1.2705 | 1.5204 | 1.5981 | 2019-04-03 11:11 | 2019-06-13 20:08 | 2019-10-31 07:19 | 2020-02-19 05:34 | 0 | 0 | 0 | 0 | 2.747% | 1.6506 | 2019-04-03 11:11 | 0
Grudie Bridge | Biden Clan Raonaild | 535 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Comrie | 562 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Conon Falls | 514 | TRUE |  | No Data | No Data | No Data | Unreliable Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 89.01%
Grudie Bridge | Cuileig Power Station | 573 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Drumrunie | 518 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Garbat Forest | 567 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Garve | 569 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Inverbroom | 527 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Kerry Falls | 531 | TRUE | ('531~TR1~TR1_AMPS~AI')*1.732*0.011 | 2.0879 | 2.763 | 2.7404 | 2.6835 | 2019-04-01 00:10 | 2019-08-31 02:18 | 2019-09-03 01:53 | 2020-02-03 02:40 | 1.4553 | 1.4925 | 1.4944 | 1.4786 | 9.89% | 2.763 | 2019-08-31 02:18 | 1.4925
Grudie Bridge | Kinlochewe | 532 | TRUE | [9 empty] | 0.22611 | 0.22611 | 0.22611 | 0.22611
Grudie Bridge | Letterewe | 507 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Loch Dubh P S | 799 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Loch Glascarnoch | 568 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Lochinver | 556 | FALSE | ('556~011~AMPS~AI')*1.732*0.011 | 1.5167 | 1.1259 | 1.2469 | 1.4423 | 2019-04-07 20:09 | 2019-07-01 20:09 | 2019-10-31 20:03 | 2020-02-27 20:10 | 0 | 0 | 0 | 0 | 4.121% | 1.5167 | 2019-04-07 20:09 | 0
Grudie Bridge | Minor Grudie | 564 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Ullapool | 549 | FALSE | ('549~071~AMPS~AI'+'549~072~AMPS~AI')*1.732*0.011 | 2.3588 | 1.8466 | 2.1927 | 2.3449 | 2019-04-07 11:07 | 2019-06-06 17:36 | 2019-10-30 20:06 | 2020-02-26 20:12 | 0 | 0 | 0 | 0 | 2.198% | 2.3588 | 2019-04-07 11:07 | 0
Inverness | Culloden | 712 | FALSE | ('712~T1~AMPS~AI'+'712~T2~AMPS~AI')*1.732*0.011 | 7.9955 | 7.2057 | 8.8885 | 9.7425 | 2019-04-01 20:05 | 2019-06-05 18:01 | 2019-10-28 17:45 | 2019-11-13 17:35 | 0 | 0 | 0 | 0 | 1.648% | 9.7425 | 2019-11-13 17:35 | 0
Inverness | Dalneigh | 713 | FALSE | ('713~T1_T2~AMPS~AI')*1.732*0.011 | 7.4266 | 6.7033 | 8.083 | 8.9488 | 2019-04-03 17:27 | 2019-06-05 17:47 | 2019-10-28 17:39 | 2019-12-16 17:36 | 0 | 0 | 0 | 0 | 4.121% | 8.9488 | 2019-12-16 17:36 | 0
Inverness | Errogie | 761 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Inverness | Foyers | 718 | FALSE | ('718~T1~AMPS~AI')*1.732*0.011 | 0.30118 | 0.28583 | 0.30304 | 0.37467 | 2019-05-29 08:22 | 2019-06-12 18:59 | 2019-10-30 17:40 | 2020-01-03 17:07 | 0 | 0 | 0 | 0 | 3.022% | 0.37467 | 2020-01-03 17:07 | 0
Inverness | Hilton | 750 | FALSE | ('750~T1_T2~AMPS~AI')*1.732*0.011 | 8.8662 | 8.2969 | 10.1694 | 11.4281 | 2019-04-04 20:28 | 2019-06-05 17:57 | 2019-10-28 17:28 | 2019-12-16 17:22 | 0 | 0 | 0 | 0 | 2.473% | 11.4281 | 2019-12-16 17:22 | 0
Inverness | Inverarnie | 757 | FALSE | ('757~011~AMPS~AI')*1.732*0.011 | 0.58412 | 0.61832 | 0.6902 | 0.63995 | 2019-05-03 08:47 | 2019-07-03 13:39 | 2019-09-26 07:30 | 2019-11-15 09:29 | 0 | 0 | 0 | 0 | 17.31% | 0.6902 | 2019-09-26 07:30 | 0
Inverness | Inverness 11 Kv | 726 | FALSE | ('725~T1_T2~AMPS~AI')*1.732*0.011 | 6.3344 | 5.5902 | 6.9414 | 8.389 | 2019-04-02 18:25 | 2019-06-12 17:21 | 2019-10-31 17:21 | 2019-11-26 15:05 | 0 | 0 | 0 | 0 | 3.022% | 8.389 | 2019-11-26 15:05 | 0
Inverness | Raigmore | 735 | FALSE | ('735~T1_T2~MW~AI') | 14.456 | 12.661 | 14.4928 | 13.7135 | 2019-04-03 11:07 | 2019-06-06 10:21 | 2019-10-31 13:04 | 2019-11-01 14:08 | 0 | 0 | 0 | 0 | 1.648% | 14.4928 | 2019-10-31 13:04 | 0
Inverness | Waterloo Place | 741 | FALSE | ('741~T1_T2~AMPS~AI')*1.732*0.011 | 13.9653 | 12.0843 | 13.9988 | 16.6055 | 2019-04-04 12:16 | 2019-06-06 12:20 | 2019-10-31 11:02 | 2019-11-26 12:21 | 0 | 0 | 0 | 0 | 1.923% | 16.6055 | 2019-11-26 12:21 | 0
Inverness | Wester Drummond | 763 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Keith | Aberlour | 460 | FALSE | ('460~T1_T2~AMPS~AI')*1.732*0.011 | 4.4429 | 4.3983 | 4.4876 | 5.0234 | 2019-04-03 12:41 | 2019-06-13 12:46 | 2019-10-29 08:45 | 2019-11-19 10:38 | 0 | 0 | 0 | 0 | 2.198% | 5.0234 | 2019-11-19 10:38 | 0
Keith | Buckie | 462 | TRUE | ('462~T1_T2~AMPS~AI')*1.732*0.011 | 12.2965 | 11.5909 | 12.0872 | 13.4463 | 2019-04-03 12:18 | 2019-08-28 16:56 | 2019-09-18 16:53 | 2019-11-14 16:57 | 3.2524 | 3.2468 | 3.2254 | 3.2486 | 2.747% | 13.4463 | 2019-11-14 16:57 | 3.2486
Keith | Cullen | 469 | FALSE | -('469~TR1~MW~AI') | 1.9459 | 1.8666 | 2.2448 | 2.6047 | 2019-04-04 09:20 | 2019-06-24 16:57 | 2019-10-29 17:31 | 2019-12-16 17:04 | 0 | 0 | 0 | 0 | 2.747% | 2.6047 | 2019-12-16 17:04 | 0
Keith | Dufftown | 461 | FALSE | ('461~T1_T2~AMPS~AI')*1.732*0.011 | 4.3547 | 4.0681 | 4.1984 | 4.6004 | 2019-05-10 15:50 | 2019-08-20 13:45 | 2019-10-22 18:03 | 2020-02-28 13:36 | 0 | 0 | 0 | 0 | 6.319% | 4.6004 | 2020-02-28 13:36 | 0
Keith | Huntly | 869 | TRUE | ('869~common~AMPS~AI')*1.732*0.011 | 5.2809 | 4.4617 | 5.4828 | 6.2913 | 2019-04-03 12:28 | 2019-06-13 17:02 | 2019-10-30 16:57 | 2019-11-19 16:53 | 0.036289 | 0.52015 | 0.033498 | 0.49223 | 2.473% | 6.2913 | 2019-11-19 16:53 | 0.49223
Keith | Insch | 871 | TRUE | ('871~common~AMPS~AI')*1.732*0.011 | 7.0403 | 6.2873 | 7.502 | 8.4749 | 2019-04-03 20:13 | 2019-06-05 18:02 | 2019-10-30 17:41 | 2020-01-08 17:11 | 2 | 2 | 2 | 2 | 1.923% | 8.4749 | 2020-01-08 17:11 | 2
Keith | Keith | 464 | FALSE | ('463~T1~AMPS~AI'+'463~T2~AMPS~AI')*1.732*0.011 | 5.6263 | 5.2523 | 5.8496 | 6.6533 | 2019-04-03 12:28 | 2019-06-19 20:13 | 2019-09-30 16:58 | 2019-12-16 16:49 | 0 | 0 | 0 | 0 | 1.923% | 6.6533 | 2019-12-16 16:49 | 0
Keith | Limehillocks | 465 | TRUE | ('465~11KV~AMPS~AI')*1.732*0.011 | 1.1399 | 1.1333 | 1.2664 | 1.5009 | 2019-04-03 20:05 | 2019-08-22 13:42 | 2019-10-31 18:11 | 2019-12-25 12:52 | 0.041872 | 0.49875 | 0.45129 | 0.025123 | 3.297% | 1.5009 | 2019-12-25 12:52 | 0.025123
Keith | Marnoch | 401 | TRUE | ('401~T1_T2~AMPS~AI')*1.732*0.011 | 5.2308 | 5.2315 | 5.3164 | 5.2148 | 2019-05-27 01:28 | 2019-08-30 13:35 | 2019-09-04 23:20 | 2020-01-07 23:17 | 3.4596 | 3.477 | 3.4836 | 3.4052 | 14.56% | 5.3164 | 2019-09-04 23:20 | 3.4836
Keith | Portsoy | 435 | TRUE | ('435~TR2~AMPS~AI')*1.732*0.011 | 2.768 | 2.6725 | 2.9504 | 3.0802 | 2019-04-01 21:28 | 2019-08-19 15:13 | 2019-09-16 12:17 | 2020-02-19 19:09 | 1.0152 | 1.0341 | 1.0071 | 0.98447 | 5.22% | 3.0802 | 2020-02-19 19:09 | 0.98447
Keith | Rothes | 459 | FALSE | ('459~T1_T2~AMPS~AI')*1.732*0.011 | 4.9075 | 4.0607 | 4.7102 | 5.3057 | 2019-04-04 11:37 | 2019-06-13 08:42 | 2019-10-30 07:33 | 2019-11-13 20:21 | 0 | 0 | 0 | 0 | 1.648% | 5.3057 | 2019-11-13 20:21 | 0
Keith | Turriff | 964 | FALSE | -('964~T1~MW~AI'+'964~T2~MW~AI') | 7.4438 | 10.7577 | 12.2641 | 13.4247 | 2019-04-02 10:00 | 2019-08-26 08:05 | 2019-10-30 17:42 | 2019-12-17 12:14 | 0.46167 | 4.4696 | 4.2954 | 4.6065 | 2.198% | 13.4247 | 2019-12-17 12:14 | 4.6065
Killin | Cashlie | 269 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Killin | Chaorach | 140 | FALSE | -('140~TR1~MW~AI') | 0.10431 | 0.051301 | 0.093272 | 0.26588 | 2019-05-25 12:24 | 2019-06-09 19:22 | 2019-10-15 18:59 | 2019-12-10 08:30 | 0.015815 | 0.7283 | 0.75257 | 0.26588 | 58.52% | 0.26588 | 2019-12-10 08:30 | 0.26588
Killin | Killin Town | 219 | FALSE | ('219~011~AMPS~AI')*1.732*0.011 | 0.87304 | 0.59878 | 0.99796 | 1.2345 | 2019-04-08 03:05 | 2019-07-05 15:13 | 2019-10-29 15:58 | 2019-11-19 03:02 | 0 | 0 | 0 | 0 | 1.923% | 1.2345 | 2019-11-19 03:02 | 0
Killin | Lochearnhead | 217 | TRUE | ('217~common~AMPS~AI')*1.732*0.011 | 1.548 | 2.0745 | 1.9511 | 2.6662 | 2019-04-01 21:27 | 2019-08-20 15:21 | 2019-10-24 01:28 | 2019-12-19 01:01 | 1.19 | 1.297 | 1.2658 | 1.7269 | 29.95% | 2.6662 | 2019-12-19 01:01 | 1.7269
Killin | Lubnaig | 221 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Kinlochleven | Glencoe | 330 | FALSE | ('330~001~MW~AI') | 1.697 | 1.3636 | 1.8182 | 2.0151 | 2019-04-01 18:33 | 2019-08-31 18:53 | 2019-10-28 18:42 | 2020-02-29 18:50 | 0 | 0 | 0 | 0 | 4.121% | 2.0151 | 2020-02-29 18:50 | 0
Kintore | Banchory | 810 | FALSE | -('810~T1~MW~AI'+'810~T2~MW~AI') | 7.9268 | 6.8216 | 8.1852 | 9.2841 | 2019-04-03 11:38 | 2019-06-13 16:47 | 2019-10-30 17:44 | 2019-11-19 16:40 | 0 | 0 | 0 | 0 | 2.198% | 9.2841 | 2019-11-19 16:40 | 0
Kintore | Fyvie | 856 | FALSE | -('856~T1~MW~AI'+'856~T2~MW~AI') | 3.742 | 3.7344 | 4.3666 | 4.3058 | 2019-04-18 07:26 | 2019-08-14 07:41 | 2019-10-31 07:13 | 2019-12-12 17:41 | 1.5171 | 1.3139 | 1.3898 | 1.0337 | 17.03% | 4.3666 | 2019-10-31 07:13 | 1.3898
Kintore | Inverurie | 875 | FALSE | -('875~T1~MW~AI'+'875~T2~MW~AI'+'875~TR3~MW~AI') | 11.2862 | 9.9812 | 10.6695 | 13.6242 | 2019-04-02 09:09 | 2019-06-29 21:48 | 2019-10-18 16:56 | 2019-12-16 16:54 | 0 | 4 | 0.0025 | 0.0092796 | 3.297% | 13.6242 | 2019-12-16 16:54 | 0.0092796
Kintore | Kemnay | 881 | FALSE | ('881~common~AMPS~AI')*1.732*0.011 | 3.1109 | 2.7313 | 3.1779 | 3.803 | 2019-04-15 17:08 | 2019-08-28 17:41 | 2019-10-31 16:54 | 2020-01-13 17:17 | 0 | 0 | 0 | 0 | 3.571% | 3.803 | 2020-01-13 17:17 | 0
Kintore | Kintore Supergrid | 886 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Kintore | Methlick | 903 | TRUE | ('903~TOTAL~AMPS~AI')*1.732*0.011 | 5.6165 | 5.5031 | 5.4326 | 5.6694 | 2019-04-03 01:47 | 2019-08-28 14:20 | 2019-09-06 15:27 | 2020-01-07 10:02 | 3.0706 | 2.9813 | 3.0492 | 2.651 | 23.63% | 5.6694 | 2020-01-07 10:02 | 2.651
Kintore | Midmar | 907 | FALSE | -('907~T1~MW~AI') | 2.233 | 2.0141 | 2.1597 | 2.6134 | 2019-04-04 11:40 | 2019-06-13 15:26 | 2019-10-30 08:25 | 2020-03-23 12:29 | 0.027915 | 0.35266 | 0 | 0.42617 | 23.9% | 2.6134 | 2020-03-23 12:29 | 0.42617
Kintore | Oldmeldrum | 921 | TRUE | ('921~common~AMPS~AI')*1.732*0.011 | 6.035 | 5.6676 | 6.5252 | 6.8892 | 2019-04-02 18:22 | 2019-08-21 17:44 | 2019-10-31 16:46 | 2020-02-24 17:36 | 3.2326 | 3.0772 | 2.6251 | 2.6728 | 1.923% | 6.8892 | 2020-02-24 17:36 | 2.6728
Kintore | Park | 923 | FALSE | ('923~TR1~AMPS~AI')*1.732*0.011 | 1.9204 | 1.5089 | 1.829 | 2.2405 | 2019-04-03 09:03 | 2019-06-24 15:10 | 2019-10-30 17:37 | 2019-11-11 08:03 | 0 | 0 | 0 | 0 | 2.198% | 2.2405 | 2019-11-11 08:03 | 0
Kintore | Skene | 941 | FALSE | -('941~TR1~MW~AI'+'941~TR2~MW~AI') | 11.392 | 10.064 | 11.696 | 13.52 | 2019-04-02 09:05 | 2019-06-13 12:07 | 2019-10-30 08:47 | 2020-01-10 08:12 | 0 | 0 | 0 | 0 | 1.648% | 13.52 | 2020-01-10 08:12 | 0
Kintore | Torryburn | 962 | TRUE | ('962~T1~AMPS~AI'+'962~T2~AMPS~AI')*1.732*0.011 | 8.1167 | 7.4404 | 8.4153 | 9.5819 | 2019-04-04 11:09 | 2019-06-13 08:36 | 2019-10-29 08:13 | 2019-11-19 16:42 | 0.056752 | 0.25678 | 0.020469 | 0.020469 | 1.648% | 9.5819 | 2019-11-19 16:42 | 0.020469
Lairg | Lairg | 534 | FALSE | ('534~TR1~AMPS~AI')*1.732*0.011 | 0.95888 | 0.77604 | 1.0587 | 1.2241 | 2019-04-10 20:23 | 2019-06-04 20:15 | 2019-10-31 20:04 | 2019-12-24 20:06 | 0 | 0 | 0 | 0 | 1.923% | 1.2241 | 2019-12-24 20:06 | 0
Lairg | Torboll | 540 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Lairg | Tressady | 548 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Lunanhead | Friockheim | 89 | FALSE | -('089~TR2~MW~AI') | 2.3926 | 2.3415 | 2.856 | 3.1827 | 2019-04-16 19:15 | 2019-08-22 17:46 | 2019-10-30 17:07 | 2019-12-18 18:12 | 0.57699 | 0.70948 | 0 | 0.95909 | 4.945% | 3.1827 | 2019-12-18 18:12 | 0.95909
Lunanhead | Inverarity | 87 | FALSE | -('087~TR1~MW~AI') | 0.56 | 0.36 | 0.36 | 0.6 | 2019-04-16 18:07 | 2019-06-05 18:02 | 2019-09-18 09:09 | 2020-03-05 18:12 | 0 | 0 | 0 | 0 | 5.769% | 0.6 | 2020-03-05 18:12 | 0
Lunanhead | Lochside | 83 | FALSE | ('083~T1_T2_11~AMPS~AI')*1.732*0.011 | 14.3542 | 12.3315 | 13.4877 | 14.9459 | 2019-04-03 16:49 | 2019-06-24 16:32 | 2019-10-30 17:14 | 2019-11-19 16:36 | 0 | 0 | 0 | 0 | 1.648% | 14.9459 | 2019-11-19 16:36 | 0
Lunanhead | Lunanhead | 82 | TRUE | ('082~T1_T2_11~AMPS~AI')*1.732*0.011 | 6.341 | 5.2105 | 6.8133 | 9.1605 | 2019-04-02 08:01 | 2019-08-31 10:03 | 2019-10-30 17:06 | 2020-02-14 12:18 | 0.011384 | 0.9294 | 0.087345 | 2.9537 | 2.747% | 9.1605 | 2020-02-14 12:18 | 2.9537
Lunanhead | Maryton | 84 | TRUE | ('084~T1_T2_11~AMPS~AI')*1.732*0.011 | 5.3011 | 4.2831 | 5.9412 | 6.4781 | 2019-04-15 18:05 | 2019-06-24 17:51 | 2019-10-28 17:18 | 2019-11-19 16:58 | 0.40477 | 0.0065135 | 0.0009305 | 0.013027 | 1.923% | 6.4781 | 2019-11-19 16:58 | 0.013027
Lyndhurst | Lochee | 13 | FALSE | -('013~TR1~MW~AI'+'013~TR2~MW~AI') | 4.2672 | 3.802 | 4.6201 | 6.3366 | 2019-04-03 12:00 | 2019-06-13 12:00 | 2019-10-29 17:10 | 2020-01-27 16:59 | 0 | 0 | 0 | 0 | 5.22% | 6.3366 | 2020-01-27 16:59 | 0
Lyndhurst | Lyndhurst | 12 | FALSE | ('012~001~AMPS~AI'+'012~002~AMPS~AI'+'012~003~AMPS~AI'+'012~004~AMPS~AI'+'012~005~AMPS~AI'+'012~006~AMPS~AI'+'012~007~AMPS~AI')*1.732*0.011 | 4.2153 | 3.7247 | 4.0724 | 4.563 | 2019-04-04 12:14 | 2019-07-09 11:35 | 2019-10-22 12:15 | 2020-01-15 16:47 | 0 | 0 | 0 | 0 | 1.923% | 4.563 | 2020-01-15 16:47 | 0
Lyndhurst | Macalpine Road | 14 | FALSE | -('014~TR1~MW~AI'+'014~TR2~MW~AI') | 5.9632 | 5.1617 | 5.9952 | 6.8448 | 2019-04-16 16:59 | 2019-06-05 12:04 | 2019-10-28 17:25 | 2020-01-13 16:59 | 0 | 0 | 0 | 0 | 1.648% | 6.8448 | 2020-01-13 16:59 | 0
Lyndhurst | West Kirkton | 15 | FALSE | ('015~T2_T3~AMPS~AI')*1.732*0.011 | 6.0662 | 5.2373 | 6.6272 | 7.3954 | 2019-04-16 16:51 | 2019-06-24 17:28 | 2019-10-30 17:05 | 2019-12-18 17:01 | 0 | 0 | 0 | 0 | 2.747% | 7.3954 | 2019-12-18 17:01 | 0
Macduff | Macduff New | 406 | TRUE |  | No Data | No Data | No Data | Unreliable Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 92.86%
Milton of Craigie | Ashludie | 55 | FALSE | ('055~T1_T2_11~AMPS~AI')*1.732*0.011 | 7.0845 | 5.867 | Unreliable Data | Unreliable Data | 2019-04-03 17:52 | 2019-06-24 17:21 | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 2.473% | 7.0845 | 2019-04-03 17:52 | 0
Milton of Craigie | Baldovie | 56 | FALSE | ('056~T1_T2_11~AMPS~AI')*1.732*0.011 | 11.6447 | 10.3071 | 11.6468 | 11.9461 | 2019-04-02 11:38 | 2019-07-09 13:26 | 2019-10-28 17:15 | 2019-11-19 16:55 | 0 | 0 | 0 | 0 | 1.923% | 11.9461 | 2019-11-19 16:55 | 0
Milton of Craigie | Broughty Ferry | 57 | FALSE | -('057~TR1~MW~AI'+'057~TR2~MW~AI') | 5.8904 | 5.1621 | 6.23 | 7.0873 | 2019-04-06 12:00 | 2019-06-13 16:54 | 2019-10-30 18:21 | 2019-12-05 17:24 | 0 | 0 | 0 | 0 | 2.747% | 7.0873 | 2019-12-05 17:24 | 0
Milton of Craigie | Edzell Street | 58 | FALSE | ('058~T1_T2~AMPS~AI')*1.732*0.011 | 2.2271 | 1.9753 | 2.4985 | 2.8251 | 2019-04-15 18:01 | 2019-06-13 17:44 | 2019-10-28 17:35 | 2019-12-01 17:25 | 0 | 0 | 0 | 0 | 2.747% | 2.8251 | 2019-12-01 17:25 | 0
Milton of Craigie | Longhaugh | 54 | TRUE | ('054~T1_T2_T3~AMPS~AI')*1.732*0.011 | 7.0592 | 5.9527 | 7.3542 | 8.3914 | 2019-04-16 17:29 | 2019-06-24 17:18 | 2019-10-29 17:29 | 2019-12-16 17:23 | 0.33988 | 0.21934 | 0.09488 | 0.4957 | 1.923% | 8.3914 | 2019-12-16 17:23 | 0.4957
Milton of Craigie | Milton Of Craigie | 52 | FALSE | -('052~TR1~MW~AI'+'052~TR2~MW~AI') | 1.273 | 1.5853 | 1.237 | 3.4468 | 2019-04-01 12:32 | 2019-06-26 03:41 | 2019-09-05 17:03 | 2020-01-28 23:39 | 0 | 0 | 0 | 0 | 37.91% | 3.4468 | 2020-01-28 23:39 | 0
Milton of Craigie | Old Craigie Road | 53 | FALSE | ('053~T2~AMPS~AI'+'053~T3~AMPS~AI')*1.732*0.011 | 5.4434 | 4.9577 | 5.8398 | 6.359 | 2019-04-11 09:14 | 2019-06-01 23:55 | 2019-10-30 18:44 | 2019-12-18 18:31 | 0 | 0 | 0 | 0 | 2.198% | 6.359 | 2019-12-18 18:31 | 0
Dounreay | Bettyhill | 591 | FALSE | ('591~11KV~AMPS~AI')*1.732*0.011 | 0.72998 | 0.66089 | 0.64763 | 0.7223 | 2019-04-03 20:27 | 2019-06-13 20:14 | 2019-10-02 18:59 | 2020-02-13 20:44 | 0 | 0 | 0 | 0 | 3.571% | 0.72998 | 2019-04-03 20:27 | 0
Dounreay | Coldbackie | 581 | FALSE | ('581~11KV~AMPS~AI')*1.732*0.011 | 0.78302 | 0.5904 | 0.72788 | 0.87653 | 2019-04-03 07:27 | 2019-06-06 12:26 | 2019-10-31 06:12 | 2020-02-16 11:35 | 0 | 0 | 0 | 0 | 2.473% | 0.87653 | 2020-02-16 11:35 | 0
Mybster | Latheron | 584 | FALSE | ('584~TR1~AMPS~AI')*1.732*0.011 | 1.6172 | 1.3922 | 1.7641 | 1.9452 | 2019-04-10 20:21 | 2019-06-06 11:42 | 2019-10-29 17:34 | 2019-12-24 20:04 | 0 | 0 | 0 | 0 | 1.923% | 1.9452 | 2019-12-24 20:04 | 0
Dounreay | Melvich | 590 | FALSE | ('590~11KV~AMPS~AI')*1.732*0.011 | 0.70067 | Unreliable Data | No Data | Unreliable Data | 2019-04-03 20:02 | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 57.97% | 0.70067 | 2019-04-03 20:02 | 0
Mybster | Wick | 594 | FALSE | -('594~TR1~MW~AI'+'594~TR2~MW~AI') | 7.5191 | 6.2232 | 7.743 | 8.8309 | 2019-04-04 12:08 | 2019-06-13 17:23 | 2019-10-28 17:35 | 2019-12-16 16:56 | 0 | 0 | 0 | 0 | 1.923% | 8.8309 | 2019-12-16 16:56 | 0
Nairn | Ardersier | 779 | FALSE | ('779~T1_T2~AMPS~AI')*1.732*0.011 | 1.881 | 1.3452 | 1.8699 | 2.6848 | 2019-04-03 11:41 | 2019-06-05 16:38 | 2019-10-31 20:09 | 2020-02-13 07:20 | 0 | 0 | 0 | 0 | 1.923% | 2.6848 | 2020-02-13 07:20 | 0
Nairn | Dalcross | 752 | TRUE | ('752~11KV~AMPS~AI')*1.732*0.011 | 1.9275 | 2.1276 | 2.5174 | 3.2756 | 2019-04-04 11:06 | 2019-08-03 11:08 | 2019-10-31 17:00 | 2020-03-06 08:46 | 0 | 0.46804 | 0.42245 | 0.54062 | 6.593% | 3.2756 | 2020-03-06 08:46 | 0.54062
Nairn | Forres | 452 | FALSE | -('452~TR1~MW~AI'+'452~TR2~MW~AI') | 7.3932 | 6.5448 | 7.9386 | 10.1202 | 2019-04-04 10:54 | 2019-06-13 17:54 | 2019-10-31 17:55 | 2019-12-16 17:55 | 0 | 0 | 0 | 0 | 2.747% | 10.1202 | 2019-12-16 17:55 | 0
Nairn | Lethen | 703 | FALSE | ('703~T1~AMPS~AI')*1.732*0.011 | 1.2541 | 1.0568 | 1.3564 | 1.429 | 2019-04-03 11:14 | 2019-06-05 17:01 | 2019-10-30 17:02 | 2019-11-10 11:24 | 0 | 0 | 0 | 0 | 9.89% | 1.429 | 2019-11-10 11:24 | 0
Nairn | Nairn Central | 723 | FALSE | ('723~11KV~AMPS~AI')*1.732*0.011 | 8.4536 | 7.5764 | 8.4974 | 10.0215 | 2019-04-04 11:09 | 2019-06-13 16:55 | 2019-10-31 16:50 | 2020-02-12 11:06 | 0 | 0 | 0 | 0 | 2.198% | 10.0215 | 2020-02-12 11:06 | 0
Persley | Bridge Of Don | 814 | FALSE | ('814~TR2~AMPS~AI'+'814~TR1~AMPS~AI')*1.732*0.011 | 13.2969 | 11.4938 | 12.9396 | 13.8439 | 2019-04-02 11:57 | 2019-06-13 09:09 | 2019-10-28 13:59 | 2020-02-28 09:29 | 0 | 0 | 0 | 0 | 1.648% | 13.8439 | 2020-02-28 09:29 | 0
Persley | Haudagain | 865 | FALSE | ('865~common~AMPS~AI')*1.732*0.011 | 5.2752 | 4.4994 | 5.5152 | 6.0733 | 2019-04-02 20:08 | 2019-06-13 18:37 | 2019-10-28 18:11 | 2020-02-25 18:49 | 0 | 0 | 0 | 0 | 2.198% | 6.0733 | 2020-02-25 18:49 | 0
Persley | Mugiemoss Mills | 912 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Persley | Northfield | 917 | FALSE | ('917~TR1~AMPS~AI'+'917~TR2~AMPS~AI')*1.732*0.011 | 3.856 | 3.8188 | No Data | Unreliable Data | 2019-04-16 17:16 | 2019-06-24 17:43 | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 1.923% | 3.856 | 2019-04-16 17:16 | 0
Persley | Persley Supergrid | 924 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Persley | St Machar | 956 | FALSE | ('956~TR1~AMPS~AI'+'956~TR2~AMPS~AI')*1.732*0.011 | 6.6478 | 6.4078 | 7.6246 | 7.8143 | 2019-04-06 13:36 | 2019-07-11 09:02 | 2019-10-28 18:11 | 2019-11-01 09:48 | 0 | 0 | 0 | 0 | 4.121% | 7.8143 | 2019-11-01 09:48 | 0
Persley | Stoneyhill | 475 | FALSE | ('475~T1~MW~AI') | 3.6408 | 3.9417 | 3.8414 | 3.7829 | 2019-05-10 13:19 | 2019-07-04 12:17 | 2019-09-02 09:17 | 2020-03-02 11:38 | 0 | 0 | 0 | 0 | 4.67% | 3.9417 | 2019-07-04 12:17 | 0
Persley | Stoneyhill Biomass | 476 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Persley | Stoneywood T1&T2 | 947 | FALSE | ('947~TR1~AMPS~AI'+'947~TR2~AMPS~AI')*1.732*0.011 | 9.4006 | 8.3628 | 6.6536 | 7.7982 | 2019-04-03 09:13 | 2019-06-13 08:58 | 2019-10-30 09:34 | 2020-01-31 09:46 | 0 | 0 | 0 | 0 | 1.648% | 9.4006 | 2019-04-03 09:13 | 0
Persley | Whitestripes | 982 | FALSE | ('982~common~AMPS~AI')*1.732*0.011 | 5.8223 | 5.253 | 6.107 | 7.0454 | 2019-04-15 17:19 | 2019-06-13 17:31 | 2019-10-29 17:16 | 2020-02-04 11:11 | 0 | 0 | 0 | 0 | 1.923% | 7.0454 | 2020-02-04 11:11 | 0
Peterhead Grange | Peterhead Grange 11Kv | 928 | FALSE | -('927~T1~MW~AI'+'927~T2~MW~AI') | 10.9758 | 10.2982 | 11.6938 | 13.0542 | 2019-04-15 17:17 | 2019-06-24 17:00 | 2019-10-30 17:05 | 2019-12-16 17:03 | 0.81465 | 0.5326 | 0 | 0.15311 | 3.571% | 13.0542 | 2019-12-16 17:03 | 0.15311
Peterhead Grange | Phead North St | 929 | FALSE | ('929~common~AMPS~AI')*1.732*0.011 | 7.312 | 9.4386 | 9.8181 | 12.0117 | 2019-04-19 10:01 | 2019-08-21 14:18 | 2019-10-18 13:08 | 2020-02-17 16:48 | 0 | 0 | 0 | 0 | 8.791% | 12.0117 | 2020-02-17 16:48 | 0
Port Ann | Airigh-Na-Brodaig | 319 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Bowmore | 313 | FALSE | -('313~TR1~MW~AI') | 2.784 | 2.128 | 2.48 | 3.536 | 2019-04-16 09:08 | 2019-06-05 09:17 | 2019-10-22 18:38 | 2019-11-18 10:05 | 0 | 0 | 0 | 0 | 22.25% | 3.536 | 2019-11-18 10:05 | 0
Port Ann | Crinan | 305 | FALSE | ('305~COMMON~AMPS~AI')*1.732*0.011 | 0.8984 | 0.74859 | 0.78395 | 0.73463 | 2019-04-17 03:36 | 2019-08-19 00:59 | 2019-09-02 00:10 | 2019-11-30 13:46 | 0 | 0 | 0 | 0 | 6.319% | 0.8984 | 2019-04-17 03:36 | 0
Port Ann | Furnace Quarry | 332 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Inverneil | 309 | FALSE | ('309~T1~AMPS~AI')*1.732*0.011 | 0.31466 | 0.5714 | 0.56791 | 0.75071 | 2019-04-10 06:09 | 2019-08-16 15:58 | 2019-09-03 09:34 | 2020-03-30 03:35 | 0 | 0 | 0 | 0 | 10.44% | 0.75071 | 2020-03-30 03:35 | 0
Port Ann | Lochgilphead | 308 | FALSE | -('308~T1~MW~AI'+'308~T2~MW~AI') | 17.9556 | 13.8892 | 16.6509 | 17.6485 | 2019-04-05 03:37 | 2019-08-29 21:19 | 2019-10-31 03:35 | 2019-11-19 13:19 | 9.648 | 9.84 | 9.744 | 9.84 | 2.747% | 17.9556 | 2019-04-05 03:37 | 9.648
Port Ann | Lussagiven | 339 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Port Askaig | 334 | FALSE | ('334~common~AMPS~AI')*1.732*0.011 | 1.1743 | 0.95935 | 0.96028 | 1.2953 | 2019-04-02 09:58 | 2019-08-15 17:23 | 2019-10-25 13:51 | 2020-02-24 13:24 | 0 | 0 | 0 | 0 | 2.198% | 1.2953 | 2020-02-24 13:24 | 0
Port Ann | Port Ellen | 331 | FALSE | ('331~common~AMPS~AI')*1.732*0.011 | 3.052 | 2.7468 | 2.8976 | 3.467 | 2019-04-10 08:22 | 2019-06-19 08:54 | 2019-10-29 18:34 | 2020-02-27 18:48 | 0 | 0 | 0 | 0 | 2.473% | 3.467 | 2020-02-27 18:48 | 0
Port Ann | Stonefield | 397 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Tarbert Jura | 341 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Tarbert Loch Fyne | 310 | FALSE | -('310~TR1~MW~AI'+'310~TR2~MW~AI') | 2.1565 | 1.2109 | 1.7483 | 2.3566 | 2019-04-15 13:21 | 2019-07-05 21:25 | 2019-10-31 18:32 | 2019-12-08 14:00 | 0.0065135 | 0.13585 | 0.023262 | 0.95655 | 7.692% | 2.3566 | 2019-12-08 14:00 | 0.95655
Port Ann | Tayvallich | 391 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Rannoch | Blackmount | 343 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Rannoch | Bridge Of Gaur | 274 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Rannoch | Glenetive | 345 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Rannoch | Tyndrum | 218 | FALSE | -('218~TR1~MW~AI') | 1.1259 | 0.66081 | 0.69288 | 0.41381 | 2019-05-25 19:04 | 2019-07-09 07:11 | 2019-10-01 19:02 | 2019-11-01 07:29 | 0 | 0 | 0 | 0 | 35.99% | 1.1259 | 2019-05-25 19:04 | 0
Redmoss | Bp Netherley | 813 | FALSE | ('813~1C0_T1~AMPS~AI'+'813~2C0_GT2~AMPS~AI')*1.732*0.033 | 0.073486 | 0.073486 | 0.059878 | 0.059878 | 2019-04-01 13:54 | 2019-06-02 09:28 | 2019-09-01 | 2019-11-19 07:30 | 0 | 0 | 0 | 0 | 18.68% | 0.073486 | 2019-06-02 09:28 | 0
Redmoss | Kincorth | 882 | FALSE | ('934~7L5~MW~AI'+'934~8L5~MW~AI') | 6.2452 | 5.9329 | 6.6055 | 7.0859 | 2019-04-04 11:17 | 2019-06-12 13:09 | 2019-10-30 17:00 | 2020-01-14 17:10 | 0 | 0 | 0 | 0 | 2.473% | 7.0859 | 2020-01-14 17:10 | 0
Redmoss | Newtonhill | 915 | TRUE | ('915~common~AMPS~AI')*1.732*0.011 | 8.6362 | 8.8396 | 9.5892 | 10.7146 | 2019-05-08 17:46 | 2019-06-13 08:15 | 2019-10-29 17:45 | 2019-12-11 17:47 | 1.3584 | 2.3065 | 0.15258 | 2.1837 | 2.198% | 10.7146 | 2019-12-11 17:47 | 2.1837
Redmoss | Redmoss | 935 | FALSE | -('935~TR1~MW~AI'+'935~TR2~MW~AI') | 16.1161 | 14.5065 | 16.2972 | 17.9068 | 2019-04-03 08:26 | 2019-06-13 09:23 | 2019-10-30 08:24 | 2020-01-14 08:08 | 0 | 0 | 0 | 0 | 1.648% | 17.9068 | 2020-01-14 08:08 | 0
Shetland | Brae | 699 | FALSE | ('699~TR1~AMPS~AI')*1.732*0.011 | 2.6327 | 1.9257 | 2.4559 | 2.9583 | 2019-04-01 06:37 | 2019-06-01 06:03 | 2019-10-29 05:34 | 2019-12-18 06:04 | 0 | 0 | 0 | 0 | 2.198% | 2.9583 | 2019-12-18 06:04 | 0
Shetland | Firth | 692 | FALSE | ('692~T2_11KV~AMPS~AI')*1.732*0.011 | 1.2562 | 0.88072 | 1.0315 | 1.2199 | 2019-04-11 06:32 | 2019-06-14 08:01 | 2019-10-07 18:07 | 2020-02-13 06:25 | 0 | 0 | 0 | 0 | 4.121% | 1.2562 | 2019-04-11 06:32 | 0
Shetland | Gremista (Lerwick) | 686 | TRUE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | No Data
Shetland | Gutcher | 695 | FALSE | ('695~011~AMPS~AI')*1.732*0.011 | 0.71811 | 0.59878 | 0.6253 | 0.72788 | 2019-04-16 05:03 | 2019-06-13 07:49 | 2019-10-31 05:06 | 2019-11-12 05:02 | 0 | 0 | 0 | 0 | 5.495% | 0.72788 | 2019-11-12 05:02 | 0
Shetland | Mid Yell | 698 | FALSE | ('698~011~AMPS~AI')*1.732*0.011 | 0.86327 | 0.7216 | 0.76417 | 0.93096 | 2019-04-23 07:11 | 2019-06-06 16:35 | 2019-10-30 13:11 | 2020-02-25 07:23 | 0 | 0 | 0 | 0 | 3.022% | 0.93096 | 2020-02-25 07:23 | 0
Shetland | Sandwick | 693 | FALSE | ('693~T1~MW~AI') | 1.1708 | 0.92981 | 1.0714 | 1.4009 | 2019-04-04 06:42 | 2019-06-13 18:12 | 2019-10-30 07:20 | 2019-12-18 07:23 | 0 | 0 | 0 | 0 | 2.198% | 1.4009 | 2019-12-18 07:23 | 0
Shetland | Scalloway | 700 | FALSE | ('700~11~AMPS~AI')*1.732*0.011 | 3.8634 | 2.9743 | 3.4363 | 4.1998 | 2019-04-17 07:30 | 2019-06-13 07:44 | 2019-10-29 07:28 | 2020-03-11 19:08 | 0 | 0 | 0 | 0 | 1.923% | 4.1998 | 2020-03-11 19:08 | 0
Shetland | Sumburgh | 697 | FALSE | ('697~011~AMPS~AI')*1.732*0.011 | 1.6191 | 1.2848 | 1.5549 | 1.9561 | 2019-04-03 07:07 | 2019-06-11 07:06 | 2019-10-29 07:14 | 2020-02-27 07:10 | 0 | 0 | 0 | 0 | 3.297% | 1.9561 | 2020-02-27 07:10 | 0
Shetland | Tumblin | 790 | FALSE | ('790~T2~AMPS~AI')*1.732*0.011 | 1.9661 | 1.4247 | 1.8475 | 2.3205 | 2019-05-07 07:44 | 2019-06-13 07:32 | 2019-10-31 05:34 | 2019-12-18 05:32 | 0 | 0 | 0 | 0 | 2.198% | 2.3205 | 2019-12-18 05:32 | 0
Shetland | UNST | 791 | FALSE | ('791~common~AMPS~AI')*1.732*0.011 | 1.4334 | 1.1138 | 1.386 | 1.6205 | 2019-04-02 05:33 | 2019-06-14 05:34 | 2019-10-29 05:32 | 2019-12-18 05:32 | 0 | 0 | 0 | 0 | 1.648% | 1.6205 | 2019-12-18 05:32 | 0
Shetland | VOE | 687 | FALSE | ('687~common~AMPS~AI')*1.732*0.011 | 3.0818 | 2.3858 | 2.9664 | 3.5694 | 2019-04-04 07:18 | 2019-06-13 07:38 | 2019-10-31 05:34 | 2020-02-28 05:32 | 0 | 0 | 0 | 0 | 2.747% | 3.5694 | 2020-02-28 05:32 | 0
Shin | Gledfield | 523 | FALSE | ('523~T1~AMPS~AI')*1.732*0.011 | 1.1911 | 0.89955 | 1.0916 | 1.5328 | 2019-04-02 06:42 | 2019-06-12 17:50 | 2019-10-29 20:07 | 2019-12-25 11:36 | 0 | 0 | 0 | 0 | 3.846% | 1.5328 | 2019-12-25 11:36 | 0
Shin | Shin | 536 | FALSE | ('545~T3~MW~AI') | 0.33626 | 0.25934 | 0.32381 | 0.41538 | 2019-04-03 20:10 | 2019-06-07 20:24 | 2019-10-31 20:05 | 2019-12-25 11:35 | 0 | 0 | 0 | 0 | 3.571% | 0.41538 | 2019-12-25 11:35 | 0
Sloy | Arrochar | 377 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Sloy | Sloy Power Station | 139 | TRUE | [9 empty] | 2.9563 | 2.9563 | 2.9563 | 2.9563
St Fergus Gas | St Fergus Gas Term | 955 | FALSE | -('SFEG~GT1~MW~AI'+'SFEG~GT2~MW~AI') | 8.4186 | 9.5147 | 6.8218 | 7.2967 | 2019-05-29 08:08 | 2019-07-22 12:21 | 2019-10-29 23:18 | 2019-12-03 11:00 | 0.01952 | 0.26956 | 0.03191 | 0.11029 | 23.35% | 9.5147 | 2019-07-22 12:21 | 0.26956
St Fillans | Dalchonzie | 212 | FALSE | -('212~TR2~MW~AI') | 1.376 | 1.12 | 1.536 | 1.728 | 2019-04-17 08:23 | 2019-08-09 17:03 | 2019-10-28 17:27 | 2019-12-18 17:00 | 0 | 0 | 0 | 0 | 3.846% | 1.728 | 2019-12-18 17:00 | 0
Strathleven | Aberfoyle | 206 | FALSE | -('206~T1~MW~AI') | 1.886 | 1.2696 | 1.91 | 2.1914 | 2019-04-16 19:35 | 2019-06-15 20:08 | 2019-10-29 19:35 | 2019-12-31 19:40 | 0.026054 | 0.98261 | 0.13585 | 0.16191 | 3.571% | 2.1914 | 2019-12-31 19:40 | 0.16191
Strathleven | Auchencarroch | 285 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Strathleven | Blairlinnans | 220 | FALSE | ('220~011~AMPS~AI')*1.732*0.011 | 0.41596 | 0.37127 | 0.42321 | 0.49157 | 2019-05-08 18:18 | 2019-07-03 22:33 | 2019-10-30 04:39 | 2020-03-02 18:30 | 0 | 0 | 0 | 0 | 2.747% | 0.49157 | 2020-03-02 18:30 | 0
Strathleven | Drymen | 203 | TRUE | ('203~T1~AMPS~AI')*1.732*0.011 | 2.0993 | 1.7848 | 2.1122 | 2.5335 | 2019-04-14 18:12 | 2019-07-31 18:29 | 2019-10-26 18:26 | 2019-11-30 17:32 | 0 | 0.45454 | 0.05862 | 0.0008 | 3.571% | 2.5335 | 2019-11-30 17:32 | 0.0008
Strathleven | Kepculloch | 205 | TRUE | ('205~SUMM~AMPS~AI')*1.732*0.011 | 2.8609 | 2.4869 | 2.8586 | 3.3386 | 2019-05-08 19:01 | 2019-08-06 18:49 | 2019-10-29 17:36 | 2019-12-31 17:13 | 0.90598 | 0.758 | 0.54505 | 0.077656 | 3.297% | 3.3386 | 2019-12-31 17:13 | 0.077656
Strathleven | Killearn | 204 | FALSE | ('204~T1~MW~AI') | 1.4853 | 1.2798 | 1.7569 | 2.004 | 2019-04-14 18:04 | 2019-06-12 17:45 | 2019-10-28 19:10 | 2020-02-25 12:36 | 0 | 0 | 0 | 0 | 3.297% | 2.004 | 2020-02-25 12:36 | 0
Strathleven | Ross Priory Pumping Stat. | 239 | FALSE |  | No Data | No Data | No Data | Unreliable Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 93.41%
Peterhead Shell | Boddam | 812 | FALSE | ('812~006~AMPS~AI')*1.732*0.011 | 6.063 | 6.5389 | 6.2472 | 7.0607 | 2019-04-08 12:06 | 2019-06-13 12:09 | 2019-10-30 09:57 | 2020-02-17 10:23 | 0 | 0 | 0 | 0 | 1.648% | 7.0607 | 2020-02-17 10:23 | 0
Strichen | Hatton | 863 | FALSE | -('863~T1~MW~AI'+'863~T2~MW~AI') | 2.414 | 2.1413 | 2.7428 | 3.0877 | 2019-04-03 20:06 | 2019-06-24 17:32 | 2019-10-28 18:15 | 2020-01-13 18:52 | 0 | 0 | 0 | 0 | 2.473% | 3.0877 | 2020-01-13 18:52 | 0
Strichen | Maud | 901 | TRUE | ('901~common~AMPS~AI')*1.732*0.011 | 2.2869 | 2.2942 | 2.3347 | 2.6456 | 2019-04-03 20:04 | 2019-08-30 02:26 | 2019-10-29 20:09 | 2019-11-19 20:22 | 0.03942 | 0.85045 | 0 | 0.27156 | 6.319% | 2.6456 | 2019-11-19 20:22 | 0.27156
Strichen | Mintlaw | 909 | FALSE | -('909~T1~MW~AI'+'909~T2~MW~AI') | 5.1412 | 4.5622 | 5.5837 | 5.9938 | 2019-04-02 16:58 | 2019-06-05 17:01 | 2019-10-30 16:56 | 2019-11-19 17:04 | 1.7868 | 0.46667 | 0 | 0.26227 | 1.648% | 5.9938 | 2019-11-19 17:04 | 0.26227
Strichen | New Pitsligo | 913 | TRUE | ('913~common~AMPS~AI')*1.732*0.011 | 0.83255 | 0.96741 | 1.2321 | 1.3805 | 2019-05-27 21:15 | 2019-08-27 18:42 | 2019-10-28 20:23 | 2019-12-24 11:51 | 0 | 0 | 0 | 0 | 20.88% | 1.3805 | 2019-12-24 11:51 | 0
Strichen | Strichen | 950 | FALSE | -('949~T1~MW~AI'+'949~T2~MW~AI') | 2.8633 | 2.2897 | 2.8708 | 3.4496 | 2019-04-22 17:14 | 2019-08-25 18:53 | 2019-10-27 17:12 | 2020-02-29 18:07 | 5.748 | 2.8672 | 4.9278 | 4.6541 | 6.319% | 3.4496 | 2020-02-29 18:07 | 4.6541
Tarland | Aboyne | 801 | FALSE | ('801~T1~MW~AI'+'801~T2~MW~AI') | 4.8836 | 4.2816 | 5.313 | 6.2839 | 2019-04-16 12:35 | 2019-06-13 16:50 | 2019-10-31 11:35 | 2020-02-28 11:54 | 0 | 0 | 0 | 0 | 2.747% | 6.2839 | 2020-02-28 11:54 | 0
Tarland | Ballater | 806 | TRUE | ('806~common~AMPS~AI')*1.732*0.011 | 4.3924 | 3.4358 | 4.405 | 5.2499 | 2019-04-03 12:01 | 2019-06-13 14:07 | 2019-10-30 20:03 | 2019-12-31 16:52 | 0 | 0 | 0 | 0 | 2.198% | 5.2499 | 2019-12-31 16:52 | 0
Tarland | Mossat | 911 | TRUE | ('911~common~AMPS~AI')*1.732*0.011 | 1.3507 | 1.0869 | 1.438 | 1.7372 | 2019-04-16 20:18 | 2019-06-13 17:08 | 2019-10-31 17:27 | 2019-12-18 11:01 | 0.053038 | 0 | 0.054899 | 0.0027915 | 3.846% | 1.7372 | 2019-12-18 11:01 | 0.0027915
Tarland | Strathdon | 951 | FALSE | ('951~TR1~AMPS~AI')*1.732*0.011 | 0.85056 | 0.59578 | 0.67618 | 0.99781 | 2019-04-06 12:01 | 2019-08-24 10:46 | 2019-10-28 18:15 | 2019-12-07 15:10 | 0 | 0 | 0 | 0 | 3.297% | 0.99781 | 2019-12-07 15:10 | 0
Tarland | Whitehouse | 981 | FALSE | ('981~T1_T2~AMPS~AI')*1.732*0.011 | 3.719 | 2.6591 | 3.5731 | 4.2564 | 2019-04-15 20:16 | 2019-06-13 20:19 | 2019-10-28 17:31 | 2019-12-17 20:05 | 0 | 0 | 0 | 0 | 1.923% | 4.2564 | 2019-12-17 20:05 | 0
Taynuilt | Ardtun Regulator | 344 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Barcaldine | 327 | FALSE | -('327~TR1~MW~AI') | 2.5929 | 2.2311 | 2.9547 | 3.7205 | 2019-04-17 07:29 | 2019-08-11 12:12 | 2019-10-22 19:31 | 2019-11-15 08:43 | 0 | 0 | 0 | 0 | 7.143% | 3.7205 | 2019-11-15 08:43 | 0
Taynuilt | Beochlich | 394 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Blarghour | 351 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Bonawe | 328 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Connel | 306 | FALSE | ('306~T1~AMPS~AI')*1.732*0.011 | 1.2841 | 0.90445 | 1.526 | 1.7047 | 2019-04-04 03:36 | 2019-06-03 18:31 | 2019-10-29 18:32 | 2019-11-18 18:34 | 0 | 0 | 0 | 0 | 3.022% | 1.7047 | 2019-11-18 18:34 | 0
Taynuilt | Craigagoul | 381 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Dalmally | 348 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Dervaig | 346 | TRUE | ('346~SS~AMPS~AI')*1.732*0.011 | 3.3378 | 2.9432 | 2.816 | 5.2816 | 2019-04-08 03:34 | 2019-06-03 18:33 | 2019-10-21 03:33 | 2020-02-05 03:33 | 0.36066 | 0.13637 | 0.17501 | 2 | 4.945% | 5.2816 | 2020-02-05 03:33 | 2
Taynuilt | Eredine | 324 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Kenmore | 329 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Kerrera | 335 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Kilchrenan | 323 | FALSE | ('323~SS~AMPS~AI')*1.732*0.011 | 0.6911 | 0.45731 | 0.58663 | 0.83498 | 2019-04-15 18:55 | 2019-07-04 19:45 | 2019-10-29 18:56 | 2019-12-01 18:37 | 0 | 0 | 0 | 0 | 10.71% | 0.83498 | 2019-12-01 18:37 | 0
Taynuilt | Kilmelford Ps | 304 | FALSE | ('304~1T0~AMPS~AI')*1.732*0.011 | 1.3331 | 2.1853 | 2.2644 | 2.0076 | 2019-04-01 12:12 | 2019-07-22 23:05 | 2019-10-10 11:04 | 2019-12-08 23:11 | 0 | 0 | 0 | 0 | 6.593% | 2.2644 | 2019-10-10 11:04 | 0
Taynuilt | Kilninver | 322 | FALSE | ('322~11KV_SS~AMPS~AI')*1.732*0.011 | 1.7049 | 1.081 | 1.76 | 2.1208 | 2019-04-10 03:33 | 2019-06-07 18:37 | 2019-10-29 18:44 | 2019-11-30 18:47 | 0 | 0 | 0 | 0 | 3.571% | 2.1208 | 2019-11-30 18:47 | 0
Taynuilt | Kinloch | 333 | FALSE | ('333~T1~MW~AI') | 1.4703 | 1.1092 | 1.3502 | 1.463 | 2019-04-03 13:21 | 2019-06-05 19:00 | 2019-10-30 18:43 | 2020-03-16 13:22 | 0 | 0 | 0 | 0 | 2.473% | 1.4703 | 2019-04-03 13:21 | 0
Taynuilt | Lochdonhead | 317 | FALSE | ('317~T1~MW~AI') | 0.91673 | 0.66227 | 0.80342 | 0.89621 | 2019-04-03 13:34 | 2019-06-06 08:26 | 2019-10-28 18:48 | 2020-02-11 13:41 | 0 | 0 | 0 | 0 | 3.022% | 0.91673 | 2019-04-03 13:34 | 0
Taynuilt | Oban | 307 | FALSE | -('307~TR1~MW~AI'+'307~TR2~MW~AI') | 13.056 | 9.984 | 12.736 | 14.88 | 2019-04-03 13:21 | 2019-06-05 16:21 | 2019-10-29 18:34 | 2020-02-11 14:08 | 0 | 0 | 0 | 0 | 1.648% | 14.88 | 2020-02-11 14:08 | 0
Taynuilt | Salen | 315 | FALSE | ('315~TR1~AMPS~AI')*1.732*0.011 | 0.61264 | 0.46903 | 0.57903 | 0.69209 | 2019-04-06 13:27 | 2019-06-05 18:33 | 2019-10-31 17:28 | 2019-12-13 18:34 | 0 | 0 | 0 | 0 | 5.769% | 0.69209 | 2019-12-13 18:34 | 0
Taynuilt | Scammadale | 340 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Strand Regulator | 316 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Taynuilt | 347 | FALSE | ('347~TAYNUILT~AMPS~AI')*1.732*0.011 | 1.1703 | 0.7348 | 1.0649 | 1.4694 | 2019-04-04 03:31 | 2019-06-05 17:22 | 2019-10-25 18:50 | 2019-12-14 13:47 | 0 | 0 | 0 | 0 | 2.198% | 1.4694 | 2019-12-14 13:47 | 0
Taynuilt | Tiree | 314 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Tiroran Bridge | 342 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Thurso | Burgarhill | 701 | FALSE | ('701~011_012~AMPS~AI')*1.732*0.011 | 1.4289 | No Data | No Data | Unreliable Data | 2019-04-11 07:07 | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 89.01% | 1.4289 | 2019-04-11 07:07 | 0
Thurso | Eday | 675 | FALSE | ('675~11KV~AMPS~AI')*1.732*0.011 | 0.19326 | 0.16535 | 0.18489 | 0.23861 | 2019-04-11 19:17 | 2019-06-23 03:17 | 2019-10-30 17:10 | 2019-12-25 11:47 | 0 | 0 | 0 | 0 | 7.967% | 0.23861 | 2019-12-25 11:47 | 0
Thurso | Eday Tidal Stream | 492 | FALSE | ('492~TR1~MW~AI') | 0.928 | 1.088 | 1.088 | 0.864 | 2019-04-03 03:28 | 2019-08-29 12:43 | 2019-09-04 12:48 | 2019-11-02 10:08 | 0 | 0 | 0 | 0 | 10.16% | 1.088 | 2019-08-29 12:43 | 0
Thurso | Flotta | 680 | FALSE | ('680~TR1~amps~AI')*1.732*0.011 | 0.39887 | 0.33883 | 0.37975 | 0.45355 | 2019-04-18 19:41 | 2019-06-04 02:17 | 2019-09-14 07:19 | 2020-03-03 18:15 | 0.82007 | 0.92791 | 1.5764 | 0.87652 | 33.79% | 0.45355 | 2020-03-03 18:15 | 0.87652
Dounreay | Forss | 583 | TRUE | ('583~TR1~AMPS~AI')*1.732*0.011 | 4.8765 | 4.9863 | 5.1059 | 5.294 | 2019-04-01 13:43 | 2019-08-22 16:19 | 2019-09-21 15:51 | 2020-01-29 07:57 | 2.4837 | 2.5851 | 2.5832 | 2.8055 | 14.56% | 5.294 | 2020-01-29 07:57 | 2.8055
Thurso | Halkirk | 597 | FALSE | -('597~TR1~MW~AI') | 1.9311 | 1.9632 | 2.468 | 2.6042 | 2019-04-03 12:04 | 2019-08-29 08:03 | 2019-10-31 07:49 | 2019-12-17 11:17 | 0 | 0 | 0 | 0 | 2.473% | 2.6042 | 2019-12-17 11:17 | 0
Thurso | Hastigrow | 582 | FALSE | ('582~TR1~AMPS~AI')*1.732*0.011 | 2.1703 | 1.7026 | 0.012559 | 2.9492 | 2019-04-05 07:56 | 2019-06-13 13:10 | 2019-09-01 | 2020-02-27 09:13 | 0 | 0 | 0 | 0 | 4.67% | 2.9492 | 2020-02-27 09:13 | 0
Thurso | Kirkwall | 677 | FALSE | -('677~T1~MW~AI'+'677~T2~MW~AI') | 13.0364 | 12.0225 | 13.2288 | 16.2012 | 2019-04-11 04:36 | 2019-06-13 12:05 | 2019-10-31 12:04 | 2019-12-17 12:04 | 0.50012 | 0.50012 | 0.50012 | 0.50012 | 2.198% | 16.2012 | 2019-12-17 12:04 | 0.50012
Thurso | Larel | 571 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Thurso | Lyness | 682 | TRUE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | No Data
Thurso | Mount Pleasant | 585 | FALSE | ('585~T1~AMPS~AI')*1.732*0.011 | 4.2265 | 3.5992 | 4.5073 | 5.7353 | 2019-04-05 07:19 | 2019-07-18 16:46 | 2019-10-31 11:04 | 2019-11-13 20:04 | 0 | 0 | 0 | 0 | 3.846% | 5.7353 | 2019-11-13 20:04 | 0
Thurso | North Hoy | 681 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Thurso | Ormlie | 587 | FALSE | ('587~T1~AMPS~AI')*1.732*0.011 | 4.0304 | 3.5109 | 3.7115 | 5.3554 | 2019-04-04 12:20 | 2019-06-17 16:50 | 2019-10-22 20:08 | 2019-12-17 11:04 | 0 | 0 | 0 | 0 | 3.571% | 5.3554 | 2019-12-17 11:04 | 0
Thurso | Rackwick Primary | 489 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Thurso | Rousay | 498 | FALSE | -('498~011~MW~AI') | 0.32394 | 0.30553 | 0.33417 | 0.43765 | 2019-05-05 12:59 | 2019-07-03 19:41 | 2019-10-21 20:48 | 2019-12-31 14:59 | 0.517 | 0.65 | 0.71 | 0.788 | 17.31% | 0.43765 | 2019-12-31 14:59 | 0.788
Thurso | Sanday | 685 | FALSE | ('685~011~AMPS~AI')*1.732*0.011 | 0.63297 | 0.54225 | 0.67764 | 0.79488 | 2019-04-12 06:38 | 2019-06-06 18:16 | 2019-10-31 11:06 | 2019-12-17 11:09 | 0 | 0 | 0 | 0 | 8.242% | 0.79488 | 2019-12-17 11:09 | 0
Thurso | Scorradale | 673 | TRUE | [9 empty] | 1.152 | 1.152 | 1.152 | 1.152
Thurso | Shapinsay | 683 | FALSE | ('683~011~AMPS~AI')*1.732*0.011 | No Data | No Data | No Data | 0.43745 | Missing Data | Missing Data | Missing Data | 2019-12-31 18:08 | 0 | 0 | 0 | 0 | 70.6% | 0.43745 | 2019-12-31 18:08 | 0
Thurso | St Marys | 679 | FALSE | ('679~TR1~AMPS~AI')*1.732*0.011 | 1.8447 | 1.987 | 1.8684 | 2.2075 | 2019-04-10 07:12 | 2019-08-15 13:59 | 2019-09-12 14:38 | 2020-03-19 18:59 | 0 | 0 | 0 | 0 | 12.09% | 2.2075 | 2020-03-19 18:59 | 0
Thurso | Stromness | 678 | FALSE | -('678~TR1~MW~AI'+'678~TR2~MW~AI') | 5.0208 | 5.8206 | 6.5995 | 7.971 | 2019-05-31 00:31 | 2019-08-16 18:10 | 2019-10-29 20:20 | 2020-02-25 19:05 | 2.2929 | 2.5919 | 2.2831 | 3.108 | 3.022% | 7.971 | 2020-02-25 19:05 | 3.108
Thurso | Stronsay | 684 | FALSE | ('684~011~AMPS~AI')*1.732*0.011 | 0.33707 | 0.24356 | 0.31195 | 0.44734 | 2019-04-20 21:48 | 2019-06-10 19:27 | 2019-10-16 17:21 | 2020-03-05 20:02 | 0 | 0 | 0 | 0 | 14.29% | 0.44734 | 2020-03-05 20:02 | 0
Thurso | Westray | 674 | FALSE | -('674~TR1~MW~AI') | 1.1058 | 1.1419 | 1.0562 | 1.1973 | 2019-05-29 17:06 | 2019-08-30 12:08 | 2019-09-16 19:01 | 2020-03-13 09:10 | 0.505 | 0.54919 | 1.0562 | 0.50842 | 14.29% | 1.1973 | 2020-03-13 09:10 | 0.50842
Tummel Bridge | Aberfeldy | 267 | TRUE |  | No Data | No Data | No Data | Unreliable Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 89.29%
Tummel Bridge | Bonskeid | 266 | FALSE | ('266~common~AMPS~AI')*1.732*0.011 | 3.1349 | 2.5417 | 3.3875 | 3.608 | 2019-04-15 11:34 | 2019-08-01 12:51 | 2019-10-12 18:55 | 2019-12-02 12:02 | 0 | 0 | 0 | 0 | 1.923% | 3.608 | 2019-12-02 12:02 | 0
Tummel Bridge | Calvine | 265 | FALSE | ('265~common~AMPS~AI')*1.732*0.011 | 1.2576 | 0.94353 | 1.2324 | 1.2031 | 2019-04-06 10:13 | 2019-06-02 11:32 | 2019-10-13 13:57 | 2019-11-10 15:33 | 0 | 0 | 0 | 0 | 3.022% | 1.2576 | 2019-04-06 10:13 | 0
Tummel Bridge | Coshieville | 268 | FALSE | ('268~001~AMPS~AI'+'268~002~AMPS~AI')*1.732*0.011 | 1.3503 | 1.1244 | 1.284 | 1.2672 | 2019-04-14 20:07 | 2019-08-07 05:36 | 2019-10-09 23:55 | 2019-11-20 14:03 | 0 | 0 | 0 | 0 | 14.29% | 1.3503 | 2019-04-14 20:07 | 0
Tummel Bridge | Fincastle | 276 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Tummel Bridge | Kinloch Rannoch | 262 | TRUE | ('262~011~AMPS~AI')*1.732*0.011 | 1.3485 | 1.9003 | 2.2677 | 2.7687 | 2019-04-08 00:02 | 2019-08-23 00:32 | 2019-09-24 23:58 | 2020-01-04 02:13 | 0.87348 | 1.0112 | 1.1932 | 1.6098 | 41.48% | 2.7687 | 2020-01-04 02:13 | 1.6098
Tummel Bridge | Pitlochry | 263 | FALSE | -('263~TR1~MW~AI'+'263~TR2~MW~AI') | 2.9736 | 2.1343 | 2.7458 | 3.0695 | 2019-04-16 12:03 | 2019-07-03 17:27 | 2019-10-28 19:54 | 2019-11-19 17:08 | 0 | 0 | 0 | 0 | 4.945% | 3.0695 | 2019-11-19 17:08 | 0
Willowdale | Denburn | 841 | FALSE | ('841~T1~Amps~ai'+'841~T2~Amps~ai')*1.732*0.011 | 12.3923 | 11.41 | 12.37 | 13.9625 | 2019-04-03 12:17 | 2019-06-13 12:58 | 2019-10-30 11:36 | 2019-11-19 11:38 | 0 | 0 | 0 | 0 | 1.923% | 13.9625 | 2019-11-19 11:38 | 0
Willowdale | Greyfriars | 861 | FALSE | -('861~TR1~MW~AI'+'861~TR2~MW~AI') | 5.6081 | 4.8489 | 6.8926 | 7.5457 | 2019-04-01 16:28 | 2019-06-26 19:37 | 2019-10-28 18:28 | 2019-11-19 18:02 | 0 | 0 | 0 | 0 | 5.769% | 7.5457 | 2019-11-19 18:02 | 0
Willowdale | Hayton | 867 | FALSE | -('867~T1~MW~AI'+'867~T2~MW~AI') | 4.3474 | 3.6147 | 5.0412 | 5.4114 | 2019-04-11 11:19 | 2019-06-24 17:42 | 2019-10-28 17:54 | 2020-02-04 09:16 | 0.55551 | 0.52015 | 0.78627 | 0.51177 | 3.297% | 5.4114 | 2020-02-04 09:16 | 0.51177
Willowdale | St Nicholas | 958 | FALSE | -('958~TR1~MW~AI'+'958~TR2~MW~AI') | 5.5945 | 4.9052 | 5.6746 | 6.4761 | 2019-04-04 15:07 | 2019-06-13 15:06 | 2019-10-31 15:03 | 2019-11-19 15:01 | 0 | 0 | 0 | 0 | 1.648% | 6.4761 | 2019-11-19 15:01 | 0
Woodhill | Queens Lane North | 932 | FALSE | ('932~TR1~Amps~AI'+'932~TR3~Amps~AI')*1.732*0.011 | 9.6697 | 7.4718 | 8.965 | 10.1153 | 2019-04-15 17:45 | 2019-06-13 12:21 | 2019-10-30 18:20 | 2020-02-14 14:46 | 0 | 0 | 0 | 0 | 1.648% | 10.1153 | 2020-02-14 14:46 | 0
Woodhill | Springhill | 943 | FALSE | ('WOHI~1L5~AMPS~AI')*2*1.732*0.033 | 11.6091 | 10.5933 | 14.6899 | 17.0787 | 2019-04-15 17:59 | 2019-06-12 17:43 | 2019-10-29 17:39 | 2019-11-19 17:19 | 0 | 0 | 0 | 0 | 2.198% | 17.0787 | 2019-11-19 17:19 | 0
Woodhill | Woodhill | 986 | FALSE | -('986~TR1~MW~AI'+'986~TR3~MW~AI') | 12.0609 | 18.1926 | 16.4333 | 15.5813 | 2019-05-24 12:01 | 2019-08-01 14:07 | 2019-10-04 11:10 | 2019-11-13 16:56 | 3.2817 | 6.6256 | 4.7697 | 3.2733 | 25.27% | 18.1926 | 2019-08-01 14:07 | 6.6256
Tummel Bridge | Tummel Bridge | 260 | FALSE | ('260~T2_11~AMPS~AI')*1.732*0.011 | 0.75743 | 0.5676 | 0.81698 | 0.83745 | 2019-04-15 21:01 | 2019-06-12 09:28 | 2019-10-28 20:02 | 2020-03-03 12:16 | 0 | 0 | 0 | 0 | 5.22% | 0.83745 | 2020-03-03 12:16 | 0
Port Ann | Cromalt | 326 | FALSE | -('326~TR1~MW~AI') | 0.792 | 0.544 | 0.736 | 0.88 | 2019-04-03 13:20 | 2019-08-31 21:18 | 2019-10-28 18:54 | 2019-11-18 18:47 | 0 | 0 | 0 | 0 | 2.747% | 0.88 | 2019-11-18 18:47 | 0
Dunvegan | Dunvegan | 638 | FALSE | ('638~T1~AMPS~AI')*1.732*0.011 | 2.1457 | 1.7661 | 1.9187 | 2.2425 | 2019-04-03 20:05 | 2019-06-06 18:42 | 2019-10-29 18:50 | 2020-03-15 11:40 | 0 | 0 | 0 | 0 | 2.747% | 2.2425 | 2020-03-15 11:40 | 0
Dyce | Harvest Avenue | 991 | FALSE | -('991~TR1~MW~AI'+'991~TR2~MW~AI') | 0.536 | 2.432 | 3.08 | 3.456 | 2019-04-04 10:53 | 2019-08-21 14:21 | 2019-10-30 09:15 | 2020-01-23 09:02 | 0 | 0 | 0 | 0 | 4.67% | 3.456 | 2020-01-23 09:02 | 0
Fort Augustus | Ardochy | 894 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Kinlochleven | Kinlochleven | 729 | FALSE | ('729~T1~MW~AI'+'729~T2~MW~AI') | 1.103 | 0.88907 | 1.1038 | 1.2239 | 2019-04-02 03:41 | 2019-06-18 16:26 | 2019-10-29 03:36 | 2020-02-13 03:06 | 0 | 0 | 0.27915 | 0.29962 | 2.747% | 1.2239 | 2020-02-13 03:06 | 0.29962
Peterhead Shell | Peterhead Shell | 926 | TRUE | [9 empty] | 0 | 0 | 0 | 0
Dounreay | DSRL |  | FALSE | ('598~T1~MW~AI'+'598~T2~MW~AI') | 4.7187 | 4.4426 | 5.0269 | 5.5276 | 2019-04-03 09:03 | 2019-06-13 10:10 | 2019-10-31 09:41 | 2019-11-19 10:36 | 0 | 0 | 0 | 0 | 1.923% | 5.5276 | 2019-11-19 10:36 | 0
Bridge of Dun | Glaxo (33kV Customer) |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
|  |  | TRUE | [9 empty] | 0 | 0 | 0 | 0
Formulas:
Time of Maximum Demand Overall = IF([Maximum Demand Overall]="","",IF([Maximum Demand Overall]=[Maximum Spring],[Time of Maximum for Filtered Data],IF([Maximum Demand Overall]=[Maximum Summer],[Maximum Summer],IF([Maximum Demand Overall]=[Maximum Autumn],[Maximum Autumn],IF([Maximum Demand Overall]=[Maximum Winter],[Maximum Winter])))))
Note on B249: Mills, David: Due to measurement point for generation it is not possible to distinguish between load and generation at this site

## SubstationLoad_Max_GSPs
GSP | Load - Filtered Data (Maximum Net of Generation) |  |  |  | Time of Maximum for Filtered Data |  |  |  | Generation at time of Maximum |  |  |  | Maximum Demand Overall | Time of Maximum Demand Overall | Generation at time of Maximum Demnad Overall
| Maximum Spring | Maximum Summer | Maximum Autumn | Maximum Winter | Maximum Spring | Maximum Summer | Maximum Autumn | Maximum Winter | Maximum Spring | Maximum Summer | Maximum Autumn | Maximum Winter
Abernethy | 28.5824 | 24.6779 | 32.8785 | 36.463 | 2019-04-10 08:24 | 2019-08-31 10:55 | 2019-10-30 17:26 | 2019-11-19 17:10 | 3.9393 | 2.3163 | 0.50269 | 0.76481 | 36.463 | 2019-11-19 17:10 | 0.76481
Alness | 90.6123 | 105.324 | 103.6759 | 137.5609 | 2019-04-06 23:59 | 2019-08-30 02:55 | 2019-09-02 13:41 | 2020-01-10 13:35 | 51.9119 | 57.647 | 58.8629 | 80.1327 | 137.5609 | 2020-01-10 13:35 | 80.1327
AN SUIDHE | 14.727 | 15.2761 | 17.6043 | 19.6268 | 2019-04-27 15:57 | 2019-08-31 03:46 | 2019-09-10 21:42 | 2019-12-08 12:00 | 0 | 0 | 0 | 0 | 19.6268 | 2019-12-08 12:00 | 0
Arbroath | 28.2283 | 23.5863 | 30.2298 | 31.5358 | 2019-04-01 17:19 | 2019-06-24 17:01 | 2019-10-15 18:36 | 2019-12-23 12:11 | 0.37528 | 0.47234 | 0.037235 | 1.4918 | 31.5358 | 2019-12-23 12:11 | 1.4918
Ardkinglas | 0.1716 | 0.1584 | 0.2772 | 1.6104 | 2019-04-12 01:08 | 2019-07-08 12:08 | 2019-09-25 10:32 | 2020-01-08 11:54 | 0 | 0 | 0 | 0 | 1.6104 | 2020-01-08 11:54 | 0
Ardmore | 28.9541 | 25.2914 | 28.9588 | 32.2136 | 2019-04-01 08:52 | 2019-07-16 16:20 | 2019-09-02 11:02 | 2019-12-11 13:22 | 31.0989 | 26.0073 | 30.4032 | 37.594 | 32.2136 | 2019-12-11 13:22 | 37.594
Beauly | 18.6608 | 17.7031 | 21.5755 | 24.9014 | 2019-05-10 07:55 | 2019-06-24 17:41 | 2019-10-30 17:46 | 2019-11-20 07:23 | 0.054899 | 0.16842 | 0.20099 | 0.18145 | 24.9014 | 2019-11-20 07:23 | 0.18145
Berryburn | 0.071783 | 0.071783 | 0.10769 | 1.3426 | 2019-04-11 11:53 | 2019-06-06 21:26 | 2019-10-29 17:34 | 2020-02-14 17:14 | 0.071783 | 0.071783 | 0.10769 | 0.02392 | 1.3426 | 2020-02-14 17:14 | 0.02392
Boat of Garten | 20.9838 | 16.0418 | 22.955 | 27.9453 | 2019-04-15 10:50 | 2019-07-05 17:41 | 2019-10-31 10:35 | 2019-11-19 11:07 | 0 | 0 | 0 | 0 | 27.9453 | 2019-11-19 11:07 | 0
Braco West | 58.6147 | 63.9124 | 73.606 | 90.5813 | 2019-04-17 00:14 | 2019-08-13 15:16 | 2019-09-03 16:41 | 2020-02-01 05:33 | 25.9305 | 26.4119 | 31.4284 | 36.1541 | 90.5813 | 2020-02-01 05:33 | 36.1541
Bridge of Dun | 20.1629 | 19.212 | 21.1713 | 25.1996 | 2019-04-11 11:38 | 2019-08-20 17:35 | 2019-09-30 17:33 | 2019-11-30 16:54 | 0.13233 | 0.14601 | 0.6559 | 0.35371 | 25.1996 | 2019-11-30 16:54 | 0.35371
Broadford | 10.2573 | 10.1773 | 11.492 | 13.4588 | 2019-04-16 20:13 | 2019-08-14 18:40 | 2019-10-21 20:04 | 2019-12-01 13:37 | 0 | 0 | 0 | 0 | 13.4588 | 2019-12-01 13:37 | 0
Brora | 7.9859 | 5.7204 | 7.159 | 8.4503 | 2019-04-03 07:17 | 2019-06-13 12:05 | 2019-10-31 07:16 | 2019-12-18 07:15 | 0 | 0 | 0 | 0 | 8.4503 | 2019-12-18 07:15 | 0
Burghmuir | 38.3749 | 31.7439 | 39.0764 | 45.2098 | 2019-04-03 11:33 | 2019-06-05 12:34 | 2019-10-29 17:27 | 2019-11-19 16:58 | 0 | 0 | 0 | 0 | 45.2098 | 2019-11-19 16:58 | 0
Cairnford | 0.62548 | 0.7075 | 0.74368 | 0.75656 | 2019-04-20 19:43 | 2019-07-08 06:46 | 2019-10-13 06:21 | 2020-03-06 06:40 | 0.3618 | 0.5427 | 0.57888 | 0.7236 | 0.75656 | 2020-03-06 06:40 | 0.7236
Carradale | 9.0498 | 7.398 | 4.5931 | 16.4678 | 2019-05-11 03:04 | 2019-06-06 04:06 | 2019-09-14 00:08 | 2020-02-13 18:45 | 0.032227 | 0.0058594 | 1.7209 | 0.3252 | 16.4678 | 2020-02-13 18:45 | 0.3252
Cassley | 1.7757 | 2.1476 | 2.1722 | 2.3593 | 2019-05-11 | 2019-06-23 11:57 | 2019-10-12 12:10 | 2019-12-06 11:19 | 0.7305 | 0.7605 | 13.2784 | 11.805 | 2.3593 | 2019-12-06 11:19 | 11.805
Ceannacroc | 1.6265 | 0.7485 | -0.9735 | 0.7338 | 2019-05-16 15:10 | 2019-06-01 23:51 | 2019-10-03 14:38 | 2019-11-06 10:06 | 1.014 | 1.824 | 0.864 | 1.5162 | 1.6265 | 2019-05-16 15:10 | 1.014
Charleston | 18.5148 | 20.9195 | 20.0786 | 21.6145 | 2019-04-24 17:09 | 2019-07-25 10:56 | 2019-09-12 11:39 | 2019-12-02 11:49 | 0 | 0 | 0 | 0 | 21.6145 | 2019-12-02 11:49 | 0
Clachan | 44.3391 | 49.4335 | 49.0133 | 53.2295 | 2019-04-06 06:03 | 2019-08-19 02:52 | 2019-09-26 07:04 | 2020-02-08 19:18 | 0.192 | 3.1157 | 2.993 | 8.5274 | 53.2295 | 2020-02-08 19:18 | 8.5274
Clayhills | 29.8375 | 25.0855 | 27.5055 | 31.7735 | 2019-04-03 11:33 | 2019-07-24 15:02 | 2019-10-30 12:04 | 2019-12-17 14:17 | 0 | 0 | 0 | 0 | 31.7735 | 2019-12-17 14:17 | 0
Coupar Angus | 27.7951 | 22.8971 | 29.6135 | 43.8551 | 2019-04-14 11:30 | 2019-06-19 16:41 | 2019-10-12 01:24 | 2020-01-19 22:46 | 30.4048 | 21.5517 | 30.5469 | 43.5647 | 43.8551 | 2020-01-19 22:46 | 43.5647
Craigiebuckler | 19.5586 | 17.1185 | 21.6915 | 23.3276 | 2019-04-16 20:26 | 2019-06-10 17:46 | 2019-10-29 17:51 | 2019-12-11 19:09 | 1.1582 | 0.94705 | 0.9424 | 1.1622 | 23.3276 | 2019-12-11 19:09 | 1.1622
Dallas | 1.2973 | 2.6524 | 1.2604 | 2.5829 | 2019-05-07 14:56 | 2019-06-29 17:04 | 2019-09-08 14:18 | 2019-12-08 02:49 | 0.77964 | 1.2415 | 0.79855 | 0.78131 | 2.6524 | 2019-06-29 17:04 | 1.2415
Dounreay | 6.2477 | 5.9162 | 7.107 | 8.3247 | 2019-05-10 11:14 | 2019-06-19 15:00 | 2019-10-30 19:01 | 2020-02-11 11:03 | 2.4969 | 0.36302 | 1.087 | 20.0735 | 8.3247 | 2020-02-11 11:03 | 20.0735
Dudhope | 39.6104 | 33.4652 | 37.6328 | 44.2394 | 2019-04-16 11:40 | 2019-06-17 14:34 | 2019-10-30 16:58 | 2019-11-19 12:20 | 0 | 0 | 0 | 0 | 44.2394 | 2019-11-19 12:20 | 0
Dunbeath Dube | 0.25154 | 0.23316 | 0.1642 | 0.73396 | 2019-05-10 09:43 | 2019-06-09 11:44 | 2019-09-20 08:25 | 2020-03-25 14:06 | 0 | 0 | 0 | 0 | 0.73396 | 2020-03-25 14:06 | 0
Dunvegan | 30.3723 | 51.4697 | 54.2932 | 53.3626 | 2019-04-06 23:55 | 2019-08-30 00:27 | 2019-09-14 02:19 | 2019-12-09 01:25 | 16.512 | 26.34 | 27.696 | 27.78 | 54.2932 | 2019-09-14 02:19 | 27.696
Dunoon | 15.1525 | 11.5452 | 14.7011 | 19.0127 | 2019-04-11 21:19 | 2019-07-08 17:05 | 2019-10-29 20:15 | 2019-11-17 18:57 | 0 | 0 | 0 | 0 | 19.0127 | 2019-11-17 18:57 | 0
Dyce | 31.1354 | 26.8828 | 32.2744 | 38.3709 | 2019-04-03 10:43 | 2019-06-25 10:43 | 2019-10-30 17:00 | 2020-02-13 09:03 | 2.6064 | 11.2474 | 2.2994 | 0.72225 | 38.3709 | 2020-02-13 09:03 | 0.72225
Edinbane | 0.12078 | 0.38648 | 0.19324 | 0.36233 | 2019-05-26 15:05 | 2019-06-12 13:02 | 2019-09-21 16:51 | 2020-01-30 04:47 | 0 | 0 | 0 | 0 | 0.38648 | 2019-06-12 13:02 | 0
Elgin | 39.1977 | 35.5437 | 41.1908 | 47.1701 | 2019-04-04 11:09 | 2019-06-13 12:04 | 2019-10-30 17:01 | 2019-11-19 16:48 | 0 | 0 | 0 | 0 | 47.1701 | 2019-11-19 16:48 | 0
Fasnakyle | 93.9851 | 83.7172 | 90.7396 | 98.7678 | 2019-04-06 18:13 | 2019-08-17 22:51 | 2019-10-12 11:47 | 2020-02-09 14:24 | 13.8426 | 15.7648 | 11.6129 | 15.8317 | 98.7678 | 2020-02-09 14:24 | 15.8317
Fort Augustus | 5.1629 | 7.0625 | 7.2399 | 9.9761 | 2019-04-06 23:19 | 2019-08-11 23:45 | 2019-10-27 02:53 | 2020-01-21 02:40 | 3.5803 | 2.6582 | 2.604 | 6.4697 | 9.9761 | 2020-01-21 02:40 | 6.4697
Fetteresso | 1.2073 | 1.4026 | 1.2403 | 1.305 | 2019-05-24 16:06 | 2019-06-26 13:01 | 2019-09-24 12:21 | 2020-02-20 01:19 | 0.647 | 0.7764 | 0.647 | 0.7117 | 1.4026 | 2019-06-26 13:01 | 0.7764
Fiddes | 60.6121 | 80.0896 | 95.4908 | 110.0853 | 2019-05-02 18:18 | 2019-08-28 13:17 | 2019-10-10 01:19 | 2020-01-16 21:45 | 1.5142 | 3.2598 | 4.7471 | 5.0503 | 110.0853 | 2020-01-16 21:45 | 5.0503
Fraserburgh | 15.0493 | 13.9166 | 16.5562 | 17.9867 | 2019-04-04 09:48 | 2019-06-06 11:32 | 2019-10-29 16:57 | 2019-12-17 11:44 | 0.0029304 | 0 | 0 | 0 | 17.9867 | 2019-12-17 11:44 | 0
Fort William | 44.7426 | 61.2745 | 56.5362 | 29.0353 | 2019-04-17 13:48 | 2019-08-16 22:32 | 2019-09-01 13:32 | 2019-11-15 08:07 | 1.2253 | 30.3448 | 31.0504 | 3.6404 | 61.2745 | 2019-08-16 22:32 | 30.3448
Glenagnes | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0
Grudie Bridge | 7.54 | 12.82 | 0.24922 | 6.1146 | 2019-05-08 20:12 | 2019-06-15 20:08 | 2019-10-05 20:23 | 2019-11-09 08:45 | 0.52201 | 0.07444 | 0.58715 | 0.52945 | 12.82 | 2019-06-15 20:08 | 0.07444
Inverness | 54.7846 | 44.0603 | 59.5442 | 63.2434 | 2019-04-03 12:08 | 2019-07-26 11:35 | 2019-10-31 17:27 | 2019-11-19 16:52 | 44.2939 | 29.8522 | 20.1287 | 25.5466 | 63.2434 | 2019-11-19 16:52 | 25.5466
Keith | 35.6893 | 25.291 | 15.52 | 38.9798 | 2019-04-04 09:03 | 2019-07-02 02:50 | 2019-10-29 17:32 | 2020-01-09 17:04 | 11.6505 | 6.0549 | 12.4446 | 13.0068 | 38.9798 | 2020-01-09 17:04 | 13.0068
Macduff | 17.8286 | 22.8024 | 23.4327 | 24.7291 | 2019-05-30 16:50 | 2019-08-13 17:52 | 2019-09-04 12:09 | 2019-11-27 17:33 | 3.3089 | 9.3651 | 9.634 | 8.571 | 24.7291 | 2019-11-27 17:33 | 8.571
Killin | 17.385 | 26.9261 | 27.7736 | 31.5833 | 2019-04-08 07:09 | 2019-08-22 23:26 | 2019-09-02 22:12 | 2020-02-22 16:10 | 1.649 | 5.6125 | 5.788 | 6.3497 | 31.5833 | 2020-02-22 16:10 | 6.3497
Kinlochleven | 31.2645 | 33.0953 | 33.0585 | 33.6174 | 2019-04-07 00:32 | 2019-08-23 00:14 | 2019-09-04 05:55 | 2020-02-29 02:14 | 4.788 | 6.2321 | 6.5317 | 6.7873 | 33.6174 | 2020-02-29 02:14 | 6.7873
Kintore | 49.6728 | 45.8177 | 61.2419 | 65.1126 | 2019-04-10 08:14 | 2019-06-10 17:31 | 2019-10-29 17:38 | 2019-11-13 17:20 | 3.7458 | 3.5052 | 3.026 | 3.1477 | 65.1126 | 2019-11-13 17:20 | 3.1477
Lairg | 1.2092 | 5.2609 | 4.6819 | 1.2697 | 2019-05-07 07:54 | 2019-08-14 09:06 | 2019-09-26 18:31 | 2020-02-11 13:18 | 0 | 0 | 0.11722 | 0 | 5.2609 | 2019-08-14 09:06 | 0
Lunanhead | 26.4107 | 22.7161 | 28.602 | 31.4618 | 2019-04-15 17:25 | 2019-06-24 16:52 | 2019-10-30 17:14 | 2019-11-19 16:41 | 2.4491 | 0.4134 | 0.11433 | 0.045434 | 31.4618 | 2019-11-19 16:41 | 0.045434
Lyndhurst | 17.8374 | 16.3021 | 19.6758 | 22.7396 | 2019-04-01 17:25 | 2019-08-27 17:13 | 2019-10-28 16:58 | 2019-11-19 16:28 | 0 | 0 | 0 | 0 | 22.7396 | 2019-11-19 16:28 | 0
Milton of Craigie | 36.4165 | 35.787 | 43.178 | 45.5121 | 2019-04-01 17:46 | 2019-08-09 17:06 | 2019-10-21 17:35 | 2019-11-21 17:17 | 0 | 0.04588 | 0.07626 | 0.13996 | 45.5121 | 2019-11-21 17:17 | 0.13996
Mybster | 9.2123 | 8.1541 | 10.5757 | 11.946 | 2019-04-11 11:04 | 2019-06-17 17:22 | 2019-10-29 17:35 | 2019-12-16 17:02 | 0.31232 | 0.30124 | 0.47323 | 0.32348 | 11.946 | 2019-12-16 17:02 | 0.32348
Nairn | 23.1111 | 22.6244 | 26.492 | 28.8495 | 2019-04-05 08:56 | 2019-06-05 16:11 | 2019-10-28 16:49 | 2019-12-16 17:50 | 0 | 2.7878 | 0.16005 | 0.18982 | 28.8495 | 2019-12-16 17:50 | 0.18982
Orrin | 23.7122 | 20.4745 | 21.2927 | 23.67 | 2019-05-18 18:49 | 2019-08-15 07:30 | 2019-09-14 06:18 | 2020-01-15 11:06 | 0 | 19.7655 | 26.315 | 18.2417 | 23.7122 | 2019-05-18 18:49 | 0
Glenfarclas | 3.0532 | 3.1011 | 1.1389 | 2.3 | 2019-05-26 16:43 | 2019-06-03 05:30 | 2019-09-23 08:44 | 2019-12-20 06:52 | 1.9162 | 1.9641 | 0.67066 | 1.3413 | 3.1011 | 2019-06-03 05:30 | 1.9641
Peterhead Grange | 5.5971 | 7.2002 | 2.6662 | 11.4765 | 2019-05-16 23:55 | 2019-07-21 | 2019-09-17 23:32 | 2020-03-27 08:26 | 0 | 1.6334 | 3.3689 | 0.22826 | 11.4765 | 2020-03-27 08:26 | 0.22826
Peterhead Shell | 5.8218 | -0.93333 | -1.719 | -1.6762 | 2019-04-01 07:14 | 2019-06-12 06:03 | 2019-10-31 15:39 | 2020-03-11 10:26 | 0 | 0 | 0 | 0 | 5.8218 | 2019-04-01 07:14 | 0
Persley | 35.6483 | 30.6666 | 35.3553 | 38.3589 | 2019-04-03 10:35 | 2019-06-13 12:10 | 2019-10-30 17:03 | 2019-11-19 16:57 | 0 | 0 | 0 | 0 | 38.3589 | 2019-11-19 16:57 | 0
Port Ann | 9.7517 | 8.5258 | 12.8411 | 11.4307 | 2019-04-26 17:42 | 2019-07-14 21:19 | 2019-10-29 03:34 | 2019-11-29 13:23 | 1.0108 | 0.047455 | 1.4667 | 0.22685 | 12.8411 | 2019-10-29 03:34 | 1.4667
Rannoch | 57.4638 | 54.8369 | 57.5529 | 66.0342 | 2019-04-05 19:28 | 2019-08-07 18:56 | 2019-10-27 15:08 | 2020-03-17 22:06 | 3.3153 | 4.6505 | 2.7441 | 4.622 | 66.0342 | 2020-03-17 22:06 | 4.622
Redmoss | 40.995 | 40.1714 | 41.315 | 43.1586 | 2019-05-07 14:09 | 2019-06-05 10:59 | 2019-10-30 08:24 | 2019-11-19 08:37 | 0.21645 | 0.1981 | 0.097285 | 0.51071 | 43.1586 | 2019-11-19 08:37 | 0.51071
St Fergus Gas | 8.4186 | 9.5147 | 6.8218 | 7.2967 | 2019-05-29 08:08 | 2019-07-22 12:21 | 2019-10-29 23:18 | 2019-12-03 11:00 | 0.01952 | 0.26956 | 0.03191 | 0.11029 | 9.5147 | 2019-07-22 12:21 | 0.26956
St Fillans | 1.1552 | 3.971 | 3.61 | 5.899 | 2019-04-11 22:01 | 2019-08-17 17:10 | 2019-09-01 23:01 | 2020-03-17 11:50 | 0 | 0 | 0 | 15.4 | 5.899 | 2020-03-17 11:50 | 15.4
Shetland | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0
Shin | 2.2321 | 19.0553 | -0.72923 | 18.102 | 2019-05-06 06:56 | 2019-08-02 03:14 | 2019-10-24 21:21 | 2020-01-26 12:26 | 0 | 0 | 0.71429 | 0 | 19.0553 | 2019-08-02 03:14 | 0
Sloy | 59.3125 | 138.2599 | 133.205 | 151.0956 | 2019-05-07 17:51 | 2019-08-31 17:35 | 2019-09-02 10:03 | 2020-03-30 04:09 | 0.80846 | 14.4615 | 10.2763 | 1.5072 | 151.0956 | 2020-03-30 04:09 | 1.5072
Strathleven | 28.076 | 40.4305 | 44.5032 | 53.5303 | 2019-04-02 19:38 | 2019-08-02 13:04 | 2019-10-17 17:12 | 2019-12-31 17:38 | 0 | 0 | 0 | 0 | 53.5303 | 2019-12-31 17:38 | 0
Strichen | 4.1063 | 4.9707 | 6.9427 | 6.0834 | 2019-05-31 | 2019-08-09 22:14 | 2019-10-24 12:35 | 2019-11-25 06:26 | 0 | 0 | 0 | 0 | 6.9427 | 2019-10-24 12:35 | 0
Tarland | 9.4873 | 9.3264 | 12.7056 | 13.633 | 2019-04-18 07:17 | 2019-08-20 20:02 | 2019-10-21 20:06 | 2019-11-27 11:34 | 0 | 0 | 0 | 0 | 13.633 | 2019-11-27 11:34 | 0
Taynuilt | -2.3542 | 25.0828 | 27.6372 | 24.0918 | 2019-05-27 00:11 | 2019-08-24 00:24 | 2019-09-15 00:27 | 2020-02-02 23:15 | 0 | 0 | 0 | 0 | 27.6372 | 2019-09-15 00:27 | 0
Thurso | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0
Tummel Bridge | 4.3847 | 6.6551 | 57.1458 | 11.6496 | 2019-04-01 16:39 | 2019-07-17 21:31 | 2019-10-12 17:28 | 2019-11-18 09:07 | 0 | 0 | 0 | 0 | 57.1458 | 2019-10-12 17:28 | 0
Willowdale | 29.2819 | 26.3956 | 27.7836 | 31.2109 | 2019-04-03 12:05 | 2019-06-13 16:51 | 2019-10-31 16:59 | 2019-11-19 17:43 | 0 | 0 | 0 | 0 | 31.2109 | 2019-11-19 17:43 | 0
Woodhill | 31.1204 | 35.1272 | 39.4785 | 45.0432 | 2019-04-25 15:16 | 2019-08-30 11:09 | 2019-10-07 12:14 | 2019-12-12 17:32 | 0 | 0 | 0 | 0 | 45.0432 | 2019-12-12 17:32 | 0
Formulas:
Time of Maximum Demand Overall = IF([Maximum Demand Overall]="","",IF([Maximum Demand Overall]=[Maximum Spring],[Time of Maximum for Filtered Data],IF([Maximum Demand Overall]=[Maximum Summer],[Maximum Summer],IF([Maximum Demand Overall]=[Maximum Autumn],[Maximum Autumn],IF([Maximum Demand Overall]=[Maximum Winter],[Maximum Winter])))))

## SubstationLoad_Min_Primaries
GSP | PRIMARY | NRN | If PI is in Amp and there is DG | PI Expression | Load - Filtered Data (Minimum Net of Generation) |  |  |  | Time of Minimum for Filtered Data |  |  |  | Generation at time of Minimum |  |  |  | Percentage of Overall Filtered Data | Minimum Demand Overall | Time of Minimum Demand Overall | Generation at time of Minimum Demnad Overall
[5 empty] | Minimum Spring | Minimum Summer | Minimum Autumn | Minimum Winter | Minimum Spring | Minimum Summer | Minimum Autumn | Minimum Winter | Minimum Spring | Minimum Summer | Minimum Autumn | Minimum Winter
Abernethy | Abernethy | 242 | TRUE | ('241~T1~AMPS~AI')*1.732*0.011 | 0.038697 | 0.030293 | 0.047122 | 0.26608 | 2019-05-06 00:12 | 2019-08-02 22:07 | 2019-09-06 22:05 | 2019-11-03 02:24 | 0.014885 | 0.014885 | 0.0093031 | 0.013955 | 23.08%
Abernethy | Balbeggie | 255 | FALSE | -('255~T1~MW~AI') | 1.0424 | 0.80923 | 0.9301 | 1.4889 | 2019-05-26 23:54 | 2019-06-05 04:17 | 2019-09-11 04:09 | 2019-11-04 03:50 | 0 | 0 | 0.22518 | 0.034428 | 3.571%
Abernethy | Binn Hill Landfill | 284 | FALSE | ('284~CS1~MW~AI') | 1.0157 | 0.72732 | 0.45562 | 1.1077 | 2019-04-17 07:14 | 2019-08-03 15:26 | 2019-09-16 17:00 | 2019-11-01 08:56 | 0 | 0 | 0 | 0 | 29.95%
Abernethy | Bridge Of Earn | 279 | FALSE | ('279~003~AMPS~AI'+'279~004~AMPS~AI')*1.732*0.011 | 0.80018 | 0.58109 | 0.6954 | 1.1384 | 2019-05-25 02:14 | 2019-08-06 14:32 | 2019-09-04 04:30 | 2019-11-02 05:46 | 0 | 0 | 0 | 0 | 1.648%
Abernethy | Errol | 254 | TRUE | ('254~SUMM~AMPS~AI')*1.732*0.011 | 0.96901 | 0.79603 | 0.74726 | 1.0525 | 2019-05-31 23:00 | 2019-07-23 02:31 | 2019-09-17 00:32 | 2020-01-20 01:06 | 0 | 0 | 0 | 0 | 17.58%
Abernethy | Glendevon | 273 | TRUE | ('273~11KV~AMPS~AI')*1.732*0.011 | Unreliable Data | Unreliable Data | 0.241 | 0.29683 | Missing Data | Missing Data | 2019-10-02 04:19 | 2020-02-26 10:58 | 0 | 0 | 0.241 | 0.29683 | 16.21%
Abernethy | Harbour | 247 | FALSE | ('247~T1_T2~AMPS~AI')*1.732*0.011 | 2.7656 | 2.4586 | 2.7042 | 3.2205 | 2019-05-28 05:09 | 2019-07-24 05:17 | 2019-09-03 04:09 | 2020-03-31 00:26 | 0 | 0 | 0 | 0 | 1.648%
Abernethy | Milnathort | 251 | TRUE | ('251~011~AMPS~AI'+'251~4L5~AMPS~AI')*1.732*0.011 | 3.3777 | 2.6919 | 3.1972 | 4.1202 | 2019-05-25 05:25 | 2019-07-01 04:41 | 2019-09-01 04:08 | 2020-03-25 01:32 | 0 | 0.28008 | 0.3387 | 0.39639 | 1.648%
Abernethy | Rumbling Bridge | 252 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Abernethy | Scone | 271 | FALSE | ('271~common~AMPS~AI')*1.732*0.011 | 1.094 | 0.83166 | 1.0493 | 1.4149 | 2019-05-16 05:20 | 2019-08-14 11:07 | 2019-09-23 02:24 | 2020-03-26 02:18 | 0 | 0 | 0 | 0 | 1.648%
Alness | Balaldie | 552 | FALSE | ('552~097~AMPS~AI'+'552~098~AMPS~AI'+'552~099~AMPS~AI')*1.732*0.011 | 0.52376 | 0.43911 | 0.55632 | 0.80751 | 2019-04-07 02:05 | 2019-08-07 02:16 | 2019-09-04 02:10 | 2020-03-06 01:47 | 0 | 0 | 0 | 0 | 2.473%
Alness | Contullich | 541 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Alness | Crosshills | 551 | FALSE | ('551~T1_T2~AMPS~AI')*1.732*0.011 | 2.2131 | 1.7917 | 2.0847 | 2.4168 | 2019-05-26 05:30 | 2019-06-30 04:57 | 2019-09-12 02:30 | 2020-03-28 01:50 | 0 | 0 | 0 | 0 | 1.648%
Alness | Glastullich | 522 | TRUE | ('522~11KV~AMPS~AI')*1.732*0.011 | 0.13675 | 0.061396 | 0.069768 | 0.15628 | 2019-04-17 15:14 | 2019-08-30 03:22 | 2019-09-14 04:59 | 2020-02-10 02:15 | 0 | 0 | 0 | 0 | 34.34%
Alness | Invergordon | 559 | TRUE | ('559~T1_T2~AMPS~AI')*1.732*0.011 | 4.2629 | 4.5143 | 4.3001 | 3.7119 | 2019-04-03 02:21 | 2019-08-06 18:10 | 2019-10-28 10:32 | 2019-11-06 05:02 | 0 | 3.465 | 3.1 | 0 | 23.35%
Alness | Lealty | 576 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Alness | Nigg | 554 | FALSE | ('554~TR1~AMPS~AI')*1.732*0.011 | 0.32373 | 0.18977 | 0.26512 | 0.42698 | 2019-05-16 05:28 | 2019-08-25 15:47 | 2019-09-01 16:09 | 2020-01-03 10:18 | 0 | 0 | 0 | 0 | 11.26%
Alness | Peddieston | 553 | FALSE | ('553~T1~AMPS~AI'+'553~T2~AMPS~AI')*1.732*0.011 | 0.43573 | 0.32183 | 0.40364 | 0.53568 | 2019-05-15 02:11 | 2019-08-11 02:27 | 2019-09-11 02:27 | 2019-11-07 09:20 | 0 | 0 | 0 | 0 | 2.198%
Alness | Tain | 546 | FALSE | ('546~T1_T2~AMPS~AI')*1.732*0.011 | 1.7196 | 1.3846 | 1.6582 | 1.9764 | 2019-04-22 23:26 | 2019-08-26 02:56 | 2019-09-24 03:49 | 2020-03-24 23:22 | 0 | 0 | 0 | 0 | 1.648%
Arbroath | Carnoustie | 64 | FALSE | -('064~TR1~MW~AI'+'064~TR2~MW~AI') | 2.0874 | 1.7875 | 1.9434 | 2.6512 | 2019-05-30 02:27 | 2019-07-21 04:54 | 2019-09-18 02:54 | 2020-03-31 01:54 | 0 | 0 | 0 | 0 | 1.648%
Arbroath | Charles Avenue | 62 | FALSE | ('062~T1_T2_11~AMPS~AI')*1.732*0.011 | 2.9024 | 2.4 | 2.7405 | 3.3496 | 2019-05-25 05:18 | 2019-06-20 03:40 | 2019-09-02 04:00 | 2020-03-31 02:23 | 0 | 0 | 0 | 0 | 1.648%
Arbroath | Elliot Depot | 68 | FALSE | ('068~T1_11~AMPS~AI')*1.732*0.011 | 1.8196 | 1.5182 | 1.6354 | 1.5294 | 2019-05-04 23:59 | 2019-08-25 05:53 | 2019-09-16 01:18 | 2020-01-02 23:42 | 0 | 0 | 0 | 0 | 6.044%
Arbroath | Hume Street | 67 | FALSE | ('067~T1_T2_11~AMPS~AI')*1.732*0.011 | 2.6457 | 2.1657 | 2.4224 | 3.2932 | 2019-05-25 02:23 | 2019-07-21 03:56 | 2019-09-22 03:54 | 2019-11-04 01:24 | 0 | 0 | 0 | 0 | 1.648%
Arbroath | Redford | 66 | FALSE | -('066~T1~MW~AI') | 0.40667 | No Data | 0.22581 | 0.60431 | 2019-05-11 15:13 | Missing Data | 2019-09-08 13:03 | 2020-03-13 11:30 | 0.042117 | 0 | 0.0011045 | 0.087036 | 35.71%
Ardmore | Aird | 671 | FALSE | ('671~T1_T2~AMPS~AI')*1.732*0.011 | 0.45222 | 0.24565 | 0.18005 | 0.45501 | 2019-04-26 01:34 | 2019-06-27 23:55 | 2019-10-09 04:57 | 2019-12-29 01:15 | 0 | 0 | 0 | 0 | 20.88%
Ardmore | Arnish | 669 | FALSE | ('669~TR1~MW~AI') | 0.12835 | 0.38505 | 0.77009 | Unreliable Data | 2019-04-25 11:35 | 2019-06-21 00:22 | 2019-10-03 22:48 | Missing Data | 0 | 0 | 0 | 0 | 20.6%
Ardmore | Barra G S | 659 | FALSE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 85.16%
Stornoway | Barvas | 651 | FALSE | ('651~T1_T2~AMPS~AI')*1.732*0.011 | 0.53318 | 0.33219 | 0.43547 | 0.60227 | 2019-05-13 04:54 | 2019-08-10 05:54 | 2019-09-06 05:55 | 2019-11-04 01:16 | 0 | 0 | 0 | 0 | 4.67%
Stornoway | Battery Point | 652 | FALSE | ('652~T1~MW~AI'+'652~T1~MW~AI'+'652~T1~MW~AI') | 3.8571 | 2.9341 | 3.5604 | 4.6154 | 2019-04-23 05:00 | 2019-08-04 05:27 | 2019-09-29 04:45 | 2019-11-03 05:50 | 0 | 0 | 0 | 0 | 7.143%
Stornoway | Callanish | 670 | FALSE | ('670~011~AMPS~AI')*1.732*0.011 | 0.4599 | 0.51782 | 0.48572 | 0.57435 | 2019-05-24 01:04 | 2019-08-05 01:00 | 2019-09-27 05:49 | 2019-11-11 23:32 | 0 | 0 | 0 | 0 | 4.67%
Ardmore | Clachan | 653 | FALSE | ('653~TR2~AMPS~AI')*1.732*0.011 | 0.68883 | 0.48597 | 0.20819 | 0.23697 | 2019-05-16 03:51 | 2019-08-30 03:50 | 2019-09-22 02:25 | 2019-11-02 01:10 | 0 | 0 | 0 | 0 | 12.09%
Stornoway | Coll | 672 | TRUE | ('672~TR1~AMPS~AI')*1.732*0.011 | 0.36247 | 0.19096 | 0.26824 | 0.47211 | 2019-05-16 13:56 | 2019-08-21 00:36 | 2019-10-17 04:21 | 2019-12-25 23:51 | 0.010745 | 0.19096 | 0.11331 | 0 | 34.07%
Ardmore | Drimore | 644 | FALSE | ('644~T1~AMPS~AI')*1.732*0.011 | 0.11777 | 0.051724 | 0.055073 | 0.12857 | 2019-04-18 04:51 | 2019-07-01 18:42 | 2019-09-05 23:58 | 2019-11-01 01:44 | 0 | 0 | 0 | 0 | 32.14%
Ardmore | Eoligarry Pmr | 666 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Ardmore | Frobost Regulator | 663 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Stornoway | Gisla | 648 | TRUE | ('648~1H0~AMPS~AI')*1.732*0.033 | 0.31121 | No Data | No Data | No Data | 2019-04-26 05:50 | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 69.78%
Ardmore | Harris Grid | 647 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Stornoway | Laxay | 657 | FALSE | ('657~T1~AMPS~AI')*1.732*0.011 | 0.39196 | 0.25305 | 0.2904 | 0.39545 | 2019-04-26 04:35 | 2019-08-26 04:42 | 2019-09-26 04:35 | 2019-11-04 01:03 | 0 | 0 | 0 | 0 | 4.121%
Ardmore | Loch Carnan | 665 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Stornoway | Maaruig | 650 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Ardmore | Northbay Pmr | 667 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Ardmore | Pollachar | 660 | FALSE | -('660~Tr1~mw~AI'+'660~Tr2~mw~AI') | 0.63405 | 0.46496 | 0.53431 | 0.79121 | 2019-05-27 11:59 | 2019-07-04 03:46 | 2019-09-23 23:55 | 2020-02-07 01:15 | 0 | 0.46496 | 0.53431 | 0.79121 | 11.81%
Ardmore | Rodil Pmr | 664 | FALSE | [5 empty] | 2018-05-08 19:37 | 2018-06-21 10:31 | 2018-10-08 19:35 | 2018-03-02 03:37 | 0 | 0 | 0 | 0
Harris | Stockinish | 658 | FALSE | ('658~MW~MW~AI') | 0.16117 | 0.07326 | 0.092796 | 0.1685 | 2019-04-30 05:49 | 2019-08-28 23:58 | 2019-09-02 01:09 | 2020-02-08 05:42 | 0 | 0 | 0 | 0 | 32.42%
Stornoway | Stornoway Grid | 645 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Harris | Tarbert | 662 | FALSE | ('662~T1_T2~AMPS~AI')*1.732*0.011 | 0.24635 | 0.18424 | 0.24635 | 0.27566 | 2019-05-16 05:19 | 2019-08-16 02:30 | 2019-09-25 04:55 | 2019-11-04 05:14 | 0 | 0 | 0 | 0 | 2.473%
Beauly | Aigas | 501 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Beauly | Blackstand | 509 | FALSE | ('509~TR1~AMPS~AI')*1.732*0.011 | 0.70837 | 0.59342 | 0.66965 | 0.92432 | 2019-05-01 00:26 | 2019-08-06 03:27 | 2019-09-25 02:19 | 2020-03-27 02:31 | 0 | 0 | 0 | 0 | 2.473%
Beauly | Conon Bridge | 513 | FALSE | -('513~TR1~MW~AI'+'513~TR2~MW~AI') | No Data | 0.832 | 0.784 | 1.12 | Missing Data | 2019-08-21 02:39 | 2019-09-12 13:33 | 2019-11-04 01:50 | 0 | 0 | 0 | 0 | 26.1%
Beauly | Dingwall | 515 | TRUE | ('515~T1~AMPS~AI'+'515~T2~AMPS~AI')*1.732*0.011 | 1.3127 | 0.84289 | 1.1703 | 1.6522 | 2019-05-30 23:56 | 2019-06-12 01:21 | 2019-09-18 23:23 | 2020-02-01 01:10 | 0.44757 | 0.26798 | 0.19354 | 0.044664 | 25%
Beauly | Kiltarlity | 520 | FALSE | ('520~001~AMPS~AI'+'520~002~AMPS~AI')*1.732*0.011 | 0.30874 | 0.20978 | 0.25874 | 0.41538 | 2019-04-25 13:18 | 2019-07-29 14:18 | 2019-09-12 12:34 | 2020-03-26 10:27 | 0 | 0 | 0 | 0 | 10.71%
Beauly | Marybank | 538 | FALSE | ('538~TR1~AMPS~AI')*1.732*0.011 | 0.29308 | 0.21981 | 0.26866 | 0.51289 | 2019-05-28 13:09 | 2019-07-29 00:10 | 2019-09-11 00:10 | 2019-11-08 01:10 | 0 | 0 | 0 | 0 | 3.846%
Beauly | Muir Of Ord | 547 | FALSE | ('547~T1_T2~AMPS~AI')*1.732*0.011 | 5.2858 | 4.2923 | 5.6877 | 5.4589 | 2019-05-02 01:27 | 2019-07-16 03:40 | 2019-09-29 02:24 | 2020-01-05 02:30 | 0 | 0 | 0 | 0 | 5.769%
Beauly | Muirend | 542 | FALSE | ('542~TR1~AMPS~AI')*1.732*0.011 | 0.52836 | 0.44079 | 0.51475 | 0.83466 | 2019-05-15 14:26 | 2019-07-25 13:07 | 2019-09-04 02:06 | 2019-11-04 02:37 | 0 | 0 | 0 | 0 | 3.297%
Beauly | North Kessock | 558 | FALSE | ('558~TR1~AMPS~AI')*1.732*0.011 | 0.25606 | 0.18595 | 0.24082 | 0.39018 | 2019-05-29 14:03 | 2019-08-02 14:11 | 2019-09-19 14:28 | 2020-01-23 02:29 | 0 | 0 | 0 | 0 | 2.747%
Boat of Garten | Aviemore | 704 | FALSE | ('704~TR1~AMPSA~AI'+'704~TR2~AMPSA~AI')*1.741*0.011 | 2.6991 | 2.0786 | 2.575 | 3.6299 | 2019-05-15 23:54 | 2019-07-27 02:21 | 2019-09-21 02:48 | 2019-11-04 02:42 | 0 | 0 | 0 | 0 | 3.846%
Boat of Garten | Ballindalloch | 706 | FALSE | -('706~TR1~MW~AI'+'706~TR2~MW~AI') | 1.808 | 0.96 | 1.152 | 1.968 | 2019-05-26 01:09 | 2019-08-25 03:09 | 2019-09-01 02:09 | 2020-03-28 23:09 | 0 | 0 | 0 | 0 | 3.022%
Boat of Garten | Boat Of Garten 11 Kv | 708 | FALSE | -('707~T1~MW~AI'+'707~T2~MW~AI') | 0.86906 | 0.62008 | 0.72015 | 0.95209 | 2019-05-15 23:05 | 2019-07-27 02:41 | 2019-09-25 02:40 | 2020-03-31 23:00 | 0 | 0 | 0 | 0 | 1.923%
Boat of Garten | Dalwhinnie | 777 | FALSE | ('777~011~AMPS~AI')*1.732*0.011 | 0.26054 | 0.22983 | 0.26147 | 0.3173 | 2019-05-16 02:04 | 2019-07-27 03:37 | 2019-09-20 23:28 | 2020-03-27 15:37 | 0 | 0 | 0 | 0 | 1.923%
Boat of Garten | Grantown | 722 | FALSE | ('722~T1_T2~AMPS~AI')*1.732*0.011 | 1.6335 | 1.1721 | 1.5666 | 2.3554 | 2019-04-23 | 2019-07-15 02:56 | 2019-09-22 02:56 | 2020-03-31 23:12 | 0 | 0 | 0 | 0 | 1.923%
Boat of Garten | Kingussie | 727 | FALSE | -('727~1H0~MW~AI'+'727~2H0~MW~AI') | 0.992 | 0.576 | 0.756 | 0.964 | 2019-04-09 00:35 | 2019-08-20 02:54 | 2019-09-06 02:54 | 2019-11-03 23:21 | 0 | 0 | 0 | 0 | 12.09%
Boat of Garten | Tomatin | 738 | FALSE | ('738~1H0~AMPS~AI')*1.732*0.033 | 0.27987 | 0.16792 | 0.22389 | 0.27987 | 2019-04-01 02:36 | 2019-06-16 02:28 | 2019-09-02 | 2019-11-02 02:23 | 0 | 0 | 0 | 0 | 7.692%
Braco West | Callander | 210 | TRUE | ('210~002~AMPS~AI'+'210~003~AMPS~AI'+'210~004~AMPS~AI'+'210~005~AMPS~AI'+'210~006~AMPS~AI'+'210~007~AMPS~AI')*1.732*0.011 | 1.1749 | 0.85054 | 0.85959 | 1.2654 | 2019-04-27 14:34 | 2019-08-11 00:13 | 2019-09-02 04:29 | 2019-11-25 02:25 | 0.0009305 | 0.20843 | 0.12562 | 0 | 4.121%
Braco West | Crieff | 208 | FALSE | ('208~T1_T2_SU~AMPS~AI')*1.732*0.011 | 1.5838 | 1.2442 | 1.1303 | 2.1675 | 2019-04-29 02:21 | 2019-06-29 04:25 | 2019-09-27 02:25 | 2020-03-31 00:18 | 0 | 0 | 0 | 0 | 10.71%
Braco West | Dunblane | 209 | FALSE | ('209~SUMM~AMPS~AI')*1.732*0.011 | 2.7222 | 2.2385 | 2.459 | 3.1835 | 2019-04-23 03:31 | 2019-08-11 03:30 | 2019-09-02 03:41 | 2019-11-04 03:56 | 0 | 0 | 0 | 0 | 1.648%
Braco West | Forteviot | 253 | FALSE | -('253~TR1~MW~AI') | 0.48551 | 0.45367 | 0.53327 | 0.66061 | 2019-04-07 06:35 | 2019-06-30 06:16 | 2019-09-03 01:55 | 2019-11-04 02:28 | 0 | 0 | 0 | 0 | 1.648%
Braco West | Gleneagles | 207 | FALSE | ('207~T1_11~AMPS~AI'+'207~T2_11~AMPS~AI')*1.732*0.011 | 4.1118 | 3.6281 | 3.7397 | 4.5025 | 2019-05-16 02:01 | 2019-07-15 03:09 | 2019-09-23 02:24 | 2019-11-04 01:08 | 0 | 0 | 0 | 0 | 1.923%
Braco West | Kippen | 211 | FALSE | ('211~11KV~AMPS~AI')*1.732*0.011 | 0.86652 | 0.67685 | 0.94461 | 1.9301 | 2019-05-28 14:13 | 2019-07-20 16:18 | 2019-09-21 14:46 | 2020-03-28 10:16 | 0 | 0 | 0 | 0 | 5.22%
Bridge of Dun | Brechin | 73 | FALSE | -('073~TR1~MW~AI'+'073~TR2~MW~AI') | 1.707 | 1.2672 | 1.3597 | 1.8531 | 2019-05-04 01:57 | 2019-08-30 02:59 | 2019-09-24 02:25 | 2019-11-03 02:15 | 0.29584 | 0.21118 | 0.32933 | 0.31072 | 4.67%
Bridge of Dun | Bridge Of Dun 11Kv | 72 | FALSE | ('072~T1_11~AMPS~AI')*1.732*0.011 | 0.062331 | 0.052097 | 0.074425 | 0.097682 | 2019-05-16 09:39 | 2019-06-28 11:20 | 2019-09-26 10:09 | 2020-03-15 03:36 | 0 | 0 | 0 | 0 | 13.46%
Bridge of Dun | Inchbare | 76 | FALSE | ('076~TR1~AMPS~AI')*1.732*0.011 | 0.35056 | 0.27435 | 0.28959 | 0.39628 | 2019-05-29 00:53 | 2019-06-03 04:10 | 2019-09-01 03:09 | 2019-11-28 04:10 | 0 | 0 | 0 | 0 | 7.967%
Bridge of Dun | Logie Pert | 77 | FALSE | -('077~TR1~MW~AI') | 0.088844 | 0.13591 | 0.35398 | 0.22421 | 2019-05-15 13:55 | 2019-07-19 13:57 | 2019-10-26 13:11 | 2020-02-23 13:57 | 0.05676 | 0.031637 | 0.025123 | 0.043733 | 25.27%
Bridge of Dun | Mill Rd Montrose | 75 | FALSE | -('075~TR1~MW~AI'+'075~TR2~MW~AI') | 2.1336 | 1.5962 | 1.9732 | 2.5186 | 2019-05-26 02:16 | 2019-07-23 05:09 | 2019-09-02 02:09 | 2020-03-27 01:30 | 0 | 0 | 0 | 0 | 1.648%
Bridge of Dun | Montrose North | 74 | FALSE | ('074~T1_T2_11~AMPS~AI')*1.732*0.011 | 2.7015 | 2.7462 | 2.7908 | 3.5164 | 2019-05-27 01:10 | 2019-06-02 03:47 | 2019-09-22 04:33 | 2019-11-04 01:04 | 0 | 0 | 0 | 0 | 1.648%
Bridge of Dun | St Cyrus | 952 | TRUE | ('952~common~AMPS~AI')*1.732*0.011 | 0.27976 | 0.12864 | 0.1642 | 0.31458 | 2019-05-05 23:54 | 2019-08-06 04:04 | 2019-09-03 02:32 | 2020-02-06 23:27 | 0.22989 | 0.12864 | 0.1642 | 0.31458 | 19.78%
Broadford | Achintee | 624 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Broadford | Broadford | 637 | FALSE | -('627~T1~MW~AI') | 0.52065 | 0.4017 | 0.4836 | 0.6786 | 2019-05-15 14:25 | 2019-08-06 03:55 | 2019-09-23 02:56 | 2020-03-31 23:46 | 0 | 0 | 0 | 0 | 2.198%
Broadford | Kishornhill | 633 | FALSE | ('633~1H0~AMPS~AI')*1.732*0.033 | 0.3358 | 0.22387 | 0.22387 | 0.3358 | 2019-04-01 00:26 | 2019-06-01 | 2019-09-01 00:47 | 2019-12-19 00:51 | 0 | 0 | 0 | 0 | 13.74%
Broadford | Kyle | 634 | FALSE | ('634~T1_T2~AMPS~AI')*1.732*0.011 | 0.81908 | 0.6614 | 0.83304 | 1.0382 | 2019-05-16 00:10 | 2019-06-29 05:27 | 2019-09-22 00:23 | 2020-03-26 16:08 | 0 | 0 | 0 | 0 | 3.022%
Broadford | Lower Ollach | 623 | FALSE | ('623~11KV~AMPS~AI')*1.732*0.011 | 0.27768 | 0.26233 | 0.29512 | 0.35373 | 2019-04-22 23:54 | 2019-07-27 05:56 | 2019-09-23 04:04 | 2019-12-30 07:43 | 0 | 0 | 0 | 0 | 2.198%
Broadford | Nostie Bridge | 636 | FALSE | ('636~T1~AMPS~AI')*1.732*0.011 | 0.1349 | 0.063671 | 0.06338 | 0.10147 | 2019-04-03 23:17 | 2019-07-26 15:23 | 2019-09-01 13:14 | 2020-03-16 10:42 | 0 | 0 | 0 | 0 | 16.76%
Broadford | Shieldaig | 641 | FALSE | ('641~11KV~AMPS~AI')*1.732*0.011 | 0.11026 | 0.082349 | 0.10398 | 0.15004 | 2019-04-22 12:58 | 2019-07-21 09:30 | 2019-09-13 19:47 | 2019-11-03 22:10 | 0 | 0 | 0 | 0 | 35.71%
Broadford | Skulamus | 639 | FALSE | ('639~T1~AMPS~AI')*1.732*0.011 | 0.7382 | 0.52303 | 0.71255 | 0.99649 | 2019-04-24 02:00 | 2019-07-26 04:30 | 2019-09-23 01:53 | 2019-11-18 10:25 | 0 | 0 | 0 | 0 | 3.022%
Brora | Benbraggie Mast | 524 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Brora | Brora | 550 | FALSE | -('550~T1_T2~MW~AI') | 0.465 | 0.31434 | 0.31992 | 0.51708 | 2019-05-27 23:57 | 2019-08-19 02:10 | 2019-09-01 00:07 | 2020-03-08 23:16 | 0 | 0 | 0 | 0 | 5.495%
Brora | Dornoch | 557 | FALSE | ('557~T1~AMPS~AI')*1.732*0.011 | 1.228 | 0.95746 | 1.0935 | 1.3428 | 2019-05-16 02:32 | 2019-07-24 02:51 | 2019-09-25 03:57 | 2020-03-27 10:30 | 0 | 0 | 0 | 0 | 2.198%
Brora | Golspie | 525 | FALSE | -('525~T1~MW~AI') | 0.55606 | 0.43886 | 0.52969 | 0.71721 | 2019-05-15 23:28 | 2019-07-25 02:50 | 2019-09-01 23:55 | 2020-03-31 00:01 | 0 | 0 | 0 | 0 | 1.923%
Brora | Helmsdale | 560 | FALSE | -('560~TR1~MW~AI') | 0.25641 | 0.21635 | 0.22436 | 0.33654 | 2019-04-23 01:09 | 2019-08-26 01:10 | 2019-09-24 03:09 | 2019-11-01 01:09 | 0 | 0 | 0 | 0 | 1.648%
Burghmuir | Burghmuir | 246 | FALSE | ('246~T1_T2_11~AMPS~AI')*1.732*0.011 | 1.7866 | 1.4627 | 1.7977 | 2.088 | 2019-05-25 04:23 | 2019-07-07 05:27 | 2019-09-02 02:22 | 2020-03-27 04:00 | 0 | 0 | 0 | 0 | 3.571%
Burghmuir | Goodlyburn | 249 | FALSE | -('249~T1~MW~AI'+'249~T2~MW~AI') | 2.592 | 2.336 | 2.624 | 3.456 | 2019-05-26 05:54 | 2019-07-07 04:54 | 2019-09-01 02:55 | 2019-11-03 01:55 | 0 | 0 | 0 | 0 | 1.648%
Burghmuir | Inveralmond | 240 | FALSE | -('240~TR1~MW~AI'+'240~TR2~MW~AI') | No Data | No Data | No Data | 1.952 | Missing Data | Missing Data | Missing Data | 2019-12-15 03:59 | 0 | 0 | 0 | 0 | 62.91%
Burghmuir | Redgorton | 270 | FALSE | ('270~common~AMPS~AI')*1.732*0.011 | 0.90649 | 0.57876 | 0.74844 | 1.4039 | 2019-05-16 02:17 | 2019-08-01 02:51 | 2019-09-02 01:51 | 2020-03-31 23:51 | 0 | 0 | 0 | 0 | 1.648%
Burghmuir | Thimblerow | 248 | FALSE | ('248~002~AMPS~AI'+'248~003~AMPS~AI'+'248~005~AMPS~AI'+'248~006~AMPS~AI'+'248~007~AMPS~AI'+'248~008~AMPS~AI'+'248~009~AMPS~AI'+'248~010~AMPS~AI'+'248~011~AMPS~AI')*1.732*0.011 | 3.7558 | 3.5128 | 3.5854 | 4.2849 | 2019-05-27 04:27 | 2019-06-23 05:18 | 2019-09-02 02:38 | 2020-03-26 04:26 | 0 | 0 | 0 | 0 | 1.648%
Carradale | Balliekine | 372 | FALSE | ('372~SS_LOAD~AMPS~AI')*1.732*0.011 | 0.10235 | 0.028845 | 0.01954 | 0.025123 | 2019-05-15 14:05 | 2019-08-03 11:42 | 2019-09-07 09:17 | 2019-11-10 21:04 | 0 | 0 | 0 | 0 | 37.36%
Carradale | Ballure | 318 | TRUE | ('318~common~AMPS~AI')*1.732*0.011 | 0.28312 | 0.22691 | 0.22464 | 0.28377 | 2019-05-16 13:14 | 2019-08-28 01:57 | 2019-09-13 01:06 | 2019-11-25 02:09 | 0.010254 | 0.076172 | 0.013184 | 0.11279 | 9.89%
Carradale | Brodick | 370 | FALSE | ('370~T1~MW~AI'+'370~T2~MW~AI') | 1.3957 | 0.73701 | 0.84139 | 1.5404 | 2019-05-28 23:57 | 2019-08-22 23:52 | 2019-09-02 23:56 | 2019-11-01 23:15 | 0 | 0 | 0 | 0 | 6.593%
Carradale | Campbeltown | 312 | FALSE | -('312~TR1~MW~AI'+'312~TR2~MW~AI') | 1.8256 | 1.1247 | 0.9454 | 1.0269 | 2019-04-13 02:33 | 2019-08-01 01:40 | 2019-10-09 02:26 | 2019-11-01 02:56 | 0 | 0 | 0 | 0 | 30.77%
Carradale | Claonaig | 338 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Carradale | Dippen | 336 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Carradale | Machrie | 373 | FALSE | ('373~011~AMPS~AI')*1.732*0.011 | 0.36359 | 0.29311 | 0.33079 | 0.50596 | 2019-05-16 13:35 | 2019-07-01 03:54 | 2019-09-23 03:49 | 2019-11-02 01:26 | 0 | 0 | 0 | 0 | 2.198%
Carradale | Westpark Fergus | 349 | FALSE | ('349~11KV_LOAD~AMPS~AI')*1.732*0.011 | 0.13344 | 0.10501 | 0.087216 | 0.065935 | 2019-05-12 11:19 | 2019-06-29 17:05 | 2019-10-20 03:02 | 2020-02-27 12:44 | 0 | 0 | 0 | 0 | 24.18%
Carradale | Whiting Bay | 371 | FALSE | ('371~T1_11KV~AMPS~AI')*1.732*0.011 | 0.47316 | 0.29311 | 0.35871 | 0.62111 | 2019-05-24 13:07 | 2019-07-28 03:56 | 2019-09-26 04:23 | 2019-12-07 01:26 | 0 | 0 | 0 | 0 | 2.747%
Cassley | Cannich | 511 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Cassley | Overscaig | 563 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Cassley | Rhiconich | 544 | FALSE | ('544~T1_T2~AMPS~AI')*1.732*0.011 | 0.5262 | 0.38244 | 0.51364 | 0.66856 | 2019-05-01 02:41 | 2019-07-29 06:48 | 2019-09-24 03:15 | 2020-02-19 15:25 | 0 | 0 | 0 | 0 | 3.571%
Charleston | Buttars Loan | 005 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Charleston | Charleston | 002 | FALSE | ('002~T1_T2_11~AMPS~AI')*1.732*0.011 | 1.8018 | 1.7237 | 1.8465 | 1.8799 | 2019-05-25 06:21 | 2019-07-07 06:07 | 2019-09-28 02:28 | 2019-11-03 02:30 | 0 | 0 | 0 | 0 | 3.297%
Charleston | Gourdie | 004 | FALSE | ('004~TR1~MW~AI') | 0.6027 | 0.5166 | 0.7134 | 0.8241 | 2019-05-14 12:49 | 2019-07-16 14:47 | 2019-09-01 04:24 | 2019-11-28 08:00 | 0 | 0 | 0 | 0 | 4.945%
Charleston | Menzieshill | 003 | FALSE | -('003~TR1~MW~AI'+'003~TR2~MW~AI') | 2.4899 | 2.0363 | 2.2984 | 3.2863 | 2019-05-25 04:44 | 2019-07-07 05:22 | 2019-09-01 05:36 | 2019-11-03 05:30 | 0 | 0 | 0 | 0 | 2.198%
Charleston | Ninewells | 006 | FALSE | ('006~11~AMPS~AI')*1.732*0.011 | 1.4959 | 1.3284 | 1.2949 | 1.6298 | 2019-05-30 01:23 | 2019-08-29 01:46 | 2019-09-02 01:35 | 2020-03-31 23:58 | 0 | 0 | 0 | 0 | 2.198%
Clachan | Butterbridge | 387 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Clachan | Douglas Pier | 388 | FALSE | ('388~TRANS~AMPS~AI')*1.732*0.011 | 0.25661 | Unreliable Data | 0.073217 | 0.20501 | 2019-05-01 01:42 | Missing Data | 2019-09-08 02:29 | 2020-02-03 01:35 | 0 | 0 | 0 | 0 | 25.27%
Clachan | Inveraray | 321 | FALSE | -('321~TR1~MW~AI') | 0.2 | 0.16 | 0.184 | 0.256 | 2019-04-24 00:36 | 2019-08-08 04:22 | 2019-09-01 01:39 | 2019-11-03 23:22 | 0 | 0 | 0 | 0 | 3.022%
Clachan | Lochgoilhead | 369 | TRUE | ('369~T1~AMPS~AI')*1.732*0.033 | 0.11523 | 0.1037 | 0.14979 | 0.20165 | 2019-04-19 23:34 | 2019-08-28 00:09 | 2019-10-01 23:30 | 2019-11-09 22:28 | 0 | 0 | 0 | 0 | 22.25%
Clachan | Strachur | 382 | FALSE | ('382~11KV~AMPS~AI')*1.732*0.011 | 0.078162 | 0.028613 | 0.047455 | 0.16679 | 2019-05-04 13:05 | 2019-08-08 05:15 | 2019-09-06 01:41 | 2019-11-04 23:24 | 0 | 0 | 0 | 0 | 11.26%
Clayhills | Balnagask | 808 | FALSE | -('808~TR1~MW~AI') | No Data | No Data | No Data | 0.83408 | Missing Data | Missing Data | Missing Data | 2020-03-23 05:20 | 0 | 0 | 0 | 0 | 60.44%
Clayhills | Clayhills | 826 | FALSE | ('826~COMMON~AMPS~AI')*1.732*0.011 | 4.4877 | 4.1137 | 4.3816 | 4.9956 | 2019-05-25 04:31 | 2019-06-22 04:38 | 2019-09-23 03:39 | 2020-03-27 01:57 | 0 | 0 | 0 | 0 | 1.648%
Clayhills | Commerce Street | 827 | FALSE | -('827~TR1~MW~AI'+'827~TR2~MW~AI') | 4.3232 | 3.899 | 4.101 | 4.1818 | 2019-05-26 05:30 | 2019-06-30 04:39 | 2019-09-01 04:30 | 2020-03-31 23:18 | 0 | 0 | 0 | 0 | 1.648%
Clayhills | Craiginches | 832 | FALSE | -('832~TR1~MW~AI'+'832~TR2~MW~AI') | 3.408 | 2.94 | 2.796 | 3.168 | 2019-04-21 03:57 | 2019-08-19 02:49 | 2019-09-01 02:12 | 2019-12-30 02:22 | 0 | 0 | 0 | 0 | 6.319%
Coupar Angus | Alyth | 258 | FALSE | ('258~011~AMPS~AI')*1.732*0.011 | 0.81064 | 0.64991 | 0.71106 | 0.88227 | 2019-05-04 02:06 | 2019-07-06 04:51 | 2019-09-11 03:54 | 2020-03-30 00:59 | 0 | 0 | 0 | 0 | 1.923%
Coupar Angus | Blairgowrie | 257 | FALSE | -('257~TR1~MW~AI'+'257~TR2~MW~AI') | No Data | No Data | No Data | 2.6107 | Missing Data | Missing Data | Missing Data | 2020-03-25 01:39 | 0 | 0 | 0 | 0 | 70.33%
Coupar Angus | Caputh | 256 | FALSE | ('256~T1~MW~AI'+'256~T2~MW~AI') | 1.264 | 0.744 | 0.888 | 1.432 | 2019-05-10 23:51 | 2019-08-31 23:55 | 2019-09-11 01:36 | 2020-03-07 23:30 | 0 | 0 | 0 | 0 | 12.91%
Coupar Angus | Coupar Angus | 244 | FALSE | ('243~1H0~MW~AI'+'243~2H0~MW~AI') | 2.0761 | 1.6471 | 1.9305 | 2.532 | 2019-05-30 04:40 | 2019-08-11 02:34 | 2019-09-29 03:41 | 2020-03-28 01:22 | 0.012096 | 0.039081 | 0.046525 | 0 | 2.473%
Coupar Angus | Dalrulzion | 259 | FALSE | ('259~T1~AMPS~AI'+'259~T2~AMPS~AI')*1.732*0.011 | 0.40438 | 0.25554 | 0.30263 | 0.52532 | 2019-05-28 04:28 | 2019-08-07 02:10 | 2019-09-04 02:05 | 2019-11-02 06:48 | 0 | 0 | 0 | 0 | 4.67%
Coupar Angus | Leoch | 90 | FALSE | -('090~TR1~MW~AI') | 0.17975 | 0.03868 | 0.0085716 | 0.33284 | 2019-04-26 13:38 | 2019-06-21 11:14 | 2019-10-05 23:59 | 2020-01-26 06:05 | 0.23175 | 0.2772 | 0.52457 | 0.34484 | 39.56%
Craigiebuckler | Craigiebuckler | 830 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Craigiebuckler | Craigton | 834 | FALSE | [9 empty] | 0.93775 | 0.93775 | 0.93775 | 0.93775
Craigiebuckler | Culter | 836 | FALSE | -('836~TR1~MW~AI'+'836~TR2~MW~AI') | 1.2478 | 0.99864 | 1.0224 | 1.5501 | 2019-05-25 04:27 | 2019-07-06 04:09 | 2019-09-24 03:43 | 2020-03-25 04:17 | 0.00472 | 0.11644 | 0.0841 | 0.02628 | 2.473%
Craigiebuckler | Ruthrieston | 939 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Dudhope | Constable Street | 32 | FALSE | -('032~TR1~MW~AI'+'032~TR2~MW~AI') | 4.2191 | 3.7512 | 4.0311 | 4.7189 | 2019-05-25 04:26 | 2019-07-14 05:22 | 2019-09-02 03:53 | 2020-03-31 02:26 | 0 | 0 | 0 | 0 | 1.648%
Dunbeath Dube | Dunbeath Grid | 595 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Dudhope | Rosebank Street | 33 | FALSE | -('033~TR1~MW~AI'+'033~TR2~MW~AI') | 3.6675 | 2.7384 | 3.5045 | 3.8794 | 2019-05-26 05:54 | 2019-07-28 06:39 | 2019-09-22 03:56 | 2020-03-29 06:39 | 0 | 0 | 0 | 0 | 6.044%
Dunvegan | Drynoch | 629 | FALSE | ('629~T1~AMPS~AI')*1.732*0.011 | 0.23688 | 0.1316 | 0.13991 | 0.18978 | 2019-04-07 04:08 | 2019-08-11 03:57 | 2019-09-21 04:42 | 2020-01-02 23:16 | 0 | 0 | 0 | 0 | 29.95%
Dunvegan | Portree | 632 | FALSE | ('632~T1~AMPS~AI'+'632~T2~AMPS~AI')*1.732*0.011 | 1.295 | 1.0066 | 1.1759 | 1.6132 | 2019-04-26 02:25 | 2019-07-29 03:16 | 2019-09-25 02:29 | 2019-11-04 01:25 | 0 | 0 | 0 | 0 | 1.648%
Dunvegan | Uig | 640 | FALSE | ('640~11KV~AMPS~AI')*1.732*0.011 | 0.37057 | 0.30427 | 0.33777 | 0.45013 | 2019-04-23 01:05 | 2019-06-30 03:50 | 2019-09-26 02:20 | 2019-12-06 01:17 | 0 | 0 | 0 | 0 | 2.198%
Dunoon | Ardyne Point | 376 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Dunoon | Bruchag | 365 | FALSE | -('365~TR1~MW~AI'+'365~TR2~MW~AI') | 0.70422 | 0.48015 | 0.54417 | 0.9603 | 2019-05-14 00:19 | 2019-08-12 00:03 | 2019-09-23 00:37 | 2020-03-31 00:01 | 0 | 0 | 0 | 0 | 1.923%
Dunoon | Colintraive | 385 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Dunoon | Dunoon | 363 | FALSE | ('363~SUMM~AMPS~AI')*1.732*0.011 | 1.8626 | 1.524 | 1.8043 | 2.0458 | 2019-05-16 02:52 | 2019-07-11 08:12 | 2019-09-21 02:55 | 2020-01-23 02:56 | 0 | 0 | 0 | 0 | 1.648%
Dunoon | Glendaruel | 383 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Dunoon | Innellan | 379 | FALSE | ('379~SUMM~AMPS~AI')*1.732*0.011 | 0.23582 | 0.22465 | Unreliable Data | Unreliable Data | 2019-05-15 12:26 | 2019-06-28 15:34 | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 2.747%
Dunoon | Kames | 366 | FALSE | ('366~11KV_SS~AMPS~AI')*1.732*0.011 | 0.11864 | 0.0656 | 0.064204 | 0.1298 | 2019-04-22 11:40 | 2019-08-22 02:10 | 2019-09-01 23:51 | 2019-11-02 02:43 | 0 | 0 | 0 | 0 | 8.791%
Dunoon | Newton | 384 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Dunoon | Otter Ferry | 375 | FALSE | ('375~11KV_SS~AMPS~AI')*1.732*0.011 | 0.40198 | 0.22332 | 0.22192 | 0.31963 | 2019-05-14 13:11 | 2019-08-20 02:57 | 2019-10-12 01:23 | 2019-12-09 00:38 | 0 | 0 | 0 | 0 | 18.13%
Dunoon | Rothesay | 362 | FALSE | ('362~T1_T2~AMPS~AI')*1.732*0.011 | 1.2391 | 1.0912 | 1.2921 | 1.6884 | 2019-05-16 05:06 | 2019-07-02 05:10 | 2019-09-22 03:24 | 2019-11-01 03:08 | 0 | 0 | 0 | 0 | 1.648%
Dunoon | Sandbank | 364 | FALSE | -('364~T1~MW~AI'+'364~T2~MW~AI') | 0.92087 | 0.55104 | 0.57054 | 1.0202 | 2019-05-28 02:25 | 2019-08-17 02:55 | 2019-09-11 01:25 | 2019-11-02 02:57 | 0.17214 | 0.47455 | 0.4699 | 0.48479 | 5.22%
Dyce | Balmedie | 807 | TRUE | ('807~common~AMPS~AI')*1.732*0.011 | 0.81302 | 0.64419 | 0.7749 | 1.1042 | 2019-05-30 04:07 | 2019-07-26 04:13 | 2019-09-06 03:57 | 2020-03-02 00:17 | 0.19532 | 0.10092 | 0.082781 | 0.08092 | 2.747%
Dyce | Dyce North | 844 | FALSE | ('843~1L5~MW~AI'+'843~2L5~MW~AI') | 5.1649 | 4.4104 | 4.7902 | 5.5866 | 2019-04-21 04:34 | 2019-06-30 05:20 | 2019-09-23 01:40 | 2020-03-28 03:18 | 0.013957 | 0.005583 | 0.048386 | 0.098633 | 1.648%
Dyce | Ellon 11 kV | 849 | FALSE | ('849A~TR1~AMPS~AI'+'849A~TR2~AMPS~AI')*1.732*0.011 | 3.1707 | 2.6809 | 3.034 | 3.8618 | 2019-05-25 04:27 | 2019-08-08 03:36 | 2019-09-28 01:39 | 2020-01-23 00:55 | 0 | 0 | 0 | 0 | 1.648%
Dyce | Kingseat | 884 | FALSE | ('884~common~AMPS~AI')*1.732*0.011 | 0.32001 | 0.32746 | 0.25489 | 0.35724 | 2019-04-19 23:40 | 2019-07-26 11:49 | 2019-10-01 15:36 | 2020-01-30 23:39 | 0 | 0 | 0 | 0 | 37.91%
Dyce | Stoneywood T3 | 947 | FALSE | -('947~TR3~MW~AI') | 0.52719 | 0.2439 | 0.01018 | 0.79788 | 2019-05-13 21:56 | 2019-07-29 02:58 | 2019-10-28 23:33 | 2020-03-14 04:45 | 0.09519 | 0 | 0.09018 | 0.94188 | 48.63%
Elgin | Ashgrove | 458 | FALSE | ('458~T1_T2~AMPS~AI')*1.732*0.011 | 1.4438 | 1.4177 | 1.5331 | 1.8828 | 2019-05-02 05:02 | 2019-07-14 05:47 | 2019-09-22 03:37 | 2019-12-30 04:26 | 0 | 0 | 0 | 0 | 3.846%
Elgin | Bilbohall | 499 | FALSE | ('499~T1_T2~AMPS~AI')*1.732*0.011 | 1.2001 | 1.1052 | 1.3787 | 1.267 | 2019-05-08 13:11 | 2019-07-22 18:56 | 2019-09-04 01:47 | 2020-01-18 23:28 | 0 | 0 | 0 | 0 | 34.34%
Elgin | Burghead | 454 | FALSE | ('454~T1_T2~AMPS~AI')*1.732*0.011 | 2.3001 | 2.4899 | 2.7652 | 3.1615 | 2019-04-03 01:06 | 2019-06-29 21:34 | 2019-10-28 05:15 | 2019-12-06 16:13 | 0 | 0 | 0 | 0 | 2.473%
Elgin | Cumming Street | 457 | FALSE | ('457~T1_T2~AMPS~AI')*1.732*0.011 | 3.2596 | 2.9173 | Unreliable Data | Unreliable Data | 2019-04-27 02:30 | 2019-07-21 04:58 | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 68.13%
Elgin | Elgin | 482 | FALSE | ('482~T1_T2~AMPS~AI')*1.732*0.011 | 1.0024 | 0.80518 | 0.90659 | 1.4169 | 2019-05-25 04:54 | 2019-06-30 03:56 | 2019-09-10 02:06 | 2020-03-28 04:52 | 0 | 0 | 0 | 0 | 1.648%
Elgin | Fochabers | 487 | FALSE | ('487~11KV~AMPS~AI')*1.732*0.011 | 1.6691 | 1.2542 | 1.684 | 1.9817 | 2019-05-11 12:53 | 2019-08-03 14:22 | 2019-09-08 14:30 | 2019-12-30 02:12 | 0 | 0 | 0 | 0 | 6.044%
Elgin | Kinloss | 453 | FALSE | ('453~T1_T2~AMPS~AI')*1.732*0.011 | 0.011163 | 0.0074421 | 0.22326 | 0.21954 | 2019-04-19 12:53 | 2019-06-04 00:11 | 2019-09-04 23:29 | 2019-12-27 23:13 | 0 | 0 | 0 | 0 | 41.48%
Elgin | Lhanbryde | 488 | FALSE | ('488~T1_T2~AMPS~AI')*1.732*0.011 | 0.10605 | 0.011163 | 0.014884 | 0.15256 | 2019-04-30 14:01 | 2019-06-12 02:20 | 2019-09-13 04:38 | 2019-11-04 02:01 | 0 | 0 | 0 | 0 | 16.48%
Elgin | Lossiemouth | 455 | FALSE | ('455~T1_T2~AMPS~AI')*1.732*0.011 | 1.9015 | 1.8866 | 2.2294 | 2.6201 | 2019-05-24 02:38 | 2019-08-11 03:59 | 2019-09-22 03:13 | 2019-11-02 04:53 | 0 | 0 | 0 | 0 | 1.648%
Fasnakyle | Fasnakyle Primary | 519 | FALSE | ('FASN~T5~AMPS~AI')*1.732*0.011 | 0.11442 | 0.063489 | 0.076745 | 0.10465 | 2019-05-26 23:15 | 2019-08-24 01:51 | 2019-09-08 23:58 | 2020-02-09 23:19 | 0 | 0 | 0 | 0 | 12.36%
Fiddes | Edzell | 847 | TRUE | ('847~common~AMPS~AI')*1.732*0.011 | 0.16139 | 0.1178 | 0.19252 | 0.13496 | 2019-04-08 00:44 | 2019-06-22 15:11 | 2019-09-03 01:38 | 2019-12-29 23:23 | 0 | 0 | 0 | 0 | 42.03%
Fiddes | Inverbervie | 873 | FALSE | -('873~TR1~MW~AI'+'873~TR2~MW~AI') | 0.47335 | 0.28713 | 0.16935 | 0.31026 | 2019-04-27 00:14 | 2019-07-19 12:17 | 2019-10-04 01:49 | 2019-12-04 00:31 | 2.1135 | 1.5012 | 2.3562 | 1.7333 | 42.03%
Fiddes | Laurencekirk | 890 | FALSE | -('890~TR1~MW~AI'+'890~TR2~MW~AI') | 0.98986 | 0.8181 | 0.89944 | 1.1947 | 2019-05-06 01:24 | 2019-06-26 00:41 | 2019-09-05 03:04 | 2019-11-05 01:15 | 0 | 0 | 0.06744 | 0.20268 | 18.13%
Fiddes | Stonehaven | 945 | TRUE | ('945~T1~AMPS~AI'+'945~T2~AMPS~AI')*1.732*0.011 | 3.5855 | 3.9221 | 4.0611 | 4.3811 | 2019-04-11 01:21 | 2019-08-30 04:01 | 2019-09-15 03:18 | 2020-01-08 01:50 | 0.040011 | 2.3034 | 2.4154 | 2.9578 | 6.044%
Fort Augustus | Aberchalder | 710 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort Augustus | Bunoich | 745 | FALSE | ('745~011~AMPS~AI')*1.732*0.011 | 0.05346 | 0.037654 | 0.045557 | 0.064384 | 2019-04-24 23:24 | 2019-07-28 05:24 | 2019-09-04 04:24 | 2019-11-04 04:24 | 0 | 0 | 0 | 0 | 2.198%
Fort Augustus | Drumnadrochit | 517 | TRUE | ('517~TR1~AMPS~AI')*1.732*0.011 | 0.58121 | 0.46034 | 0.49529 | 0.91697 | 2019-05-01 02:37 | 2019-08-26 02:48 | 2019-09-23 03:02 | 2019-11-25 02:27 | 0 | 0.07537 | 0.098633 | 0.19168 | 5.22%
Fort Augustus | Farr Grid | 709 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort Augustus | Glen Laogh | 396 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort Augustus | Glendoe Primary | 781 | FALSE | ('781~002~AMPS~AI'+'781~003~AMPS~AI')*1.732*0.011 | 0.28713 | 0.27269 | 0.31118 | 0.30637 | 2019-04-05 16:09 | 2019-07-25 05:59 | 2019-09-23 01:01 | 2020-03-27 15:41 | 0 | 0 | 0 | 0 | 1.923%
Fort Augustus | Invergarry | 766 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort Augustus | Markethill | 742 | FALSE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | No Data
Quoich | Quoich Primary | 748 | TRUE | [9 empty] | 0.792 | 0.792 | 0.792 | 0.792
Fort William | Annat | 702 | FALSE | -('702~TR1~MW~AI') | 0.68839 | 0.49628 | 0.51229 | 0.78444 | 2019-05-27 02:49 | 2019-08-03 05:54 | 2019-09-01 05:42 | 2019-11-04 02:54 | 0 | 0 | 0 | 0 | 4.67%
Fort William | Arisaig | 740 | FALSE | ('740~T1~AMPS~AI')*1.732*0.011 | 0.14446 | 0.1326 | 0.14097 | 0.16051 | 2019-04-30 00:41 | 2019-06-28 11:47 | 2019-10-11 00:34 | 2019-11-05 01:25 | 0 | 0 | 0 | 0 | 4.121%
Fort William | Carnoch Regulator | 782 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Corran | 744 | FALSE | ('744~11KV~AMPS~AI')*1.732*0.011 | 0.41183 | 0.20548 | 0.26294 | 0.34218 | 2019-04-02 00:09 | 2019-08-20 15:37 | 2019-10-24 00:14 | 2020-01-22 02:14 | 0 | 0 | 0 | 0 | 21.15%
Fort William | Dailbeg | 720 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Fishnish | 395 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Glensanda | 714 | FALSE | ('714~common~AMPS~AI')*1.732*0.011 | 0.5583 | 0.70346 | 0.56947 | 0.53597 | 2019-04-27 13:09 | 2019-06-04 12:19 | 2019-10-08 12:24 | 2020-03-31 18:09 | 0 | 0 | 0 | 0 | 23.63%
Fort William | Glenuig | 756 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Inverlochy | 724 | FALSE | -('724~TR1~MW~AI'+'724~TR2~MW~AI') | 2.8733 | 1.7034 | 1.8186 | 2.6641 | 2019-04-03 00:01 | 2019-06-11 02:39 | 2019-09-12 23:59 | 2020-03-30 00:27 | 0.17493 | 0.030706 | 0.44571 | 0.028845 | 4.945%
Fort William | Kingairloch | 771 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Kinlochmoidart | 754 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Liddesdale | 721 | FALSE | ('721~016~AMPS~AI')*1.732*0.011 | 0.15628 | 0.11302 | 0.13814 | 0.21907 | 2019-05-15 02:38 | 2019-07-17 03:53 | 2019-09-01 03:42 | 2020-01-02 08:04 | 0 | 0 | 0 | 0 | 1.923%
Fort William | Lochailort Regulator | 730 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Lochaline | 747 | FALSE | ('747~T1_POWER~MVA~AI') | 0.2 | 0.0875 | 0.075 | 0.0625 | 2019-04-07 18:20 | 2019-06-10 17:48 | 2019-10-09 10:43 | 2020-02-25 20:02 | 0 | 0 | 0 | 0 | 7.418%
Fort William | Mallaig | 731 | FALSE | ('731~TR1~AMPS~AI')*1.732*0.011 | 0.44772 | 0.2572 | 0.2191 | 0.29531 | 2019-04-25 05:54 | 2019-08-12 06:16 | 2019-09-10 | 2019-11-03 08:26 | 0 | 0 | 0 | 0 | 25%
Fort William | Pinegrove | 734 | FALSE | ('734~T1_T2~AMPS~AI')*1.732*0.011 | 2.1136 | 1.6373 | 1.9498 | 2.2512 | 2019-04-24 23:48 | 2019-08-04 05:29 | 2019-09-24 23:36 | 2020-03-31 23:09 | 0 | 0 | 0 | 0 | 1.923%
Fort William | Poor House | 753 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Rahoy | 732 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Salen 2 | 749 | FALSE | ('749~T1~AMPS~AI')*1.732*0.011 | 0.54295 | 0.29032 | 0.29032 | 0.44943 | 2019-04-21 23:44 | 2019-07-19 02:11 | 2019-09-23 23:47 | 2019-11-04 23:27 | 0 | 0 | 0 | 0 | 32.69%
Fort William | Shona Beag | 755 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fort William | Strontian | 751 | FALSE | ('751~11KV~AMPS~AI')*1.732*0.011 | 0.1647 | 0.10049 | 0.097702 | 0.17307 | 2019-05-16 01:12 | 2019-08-22 23:46 | 2019-09-12 01:46 | 2019-11-02 02:06 | 0 | 0 | 0 | 0 | 13.46%
Fraserburgh | Cairnbulg | 821 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Fraserburgh | Fraserburgh | 854 | FALSE | -('854~TR1~MW~AI'+'854~TR3~MW~AI') | 3.9515 | 3.6364 | 3.2715 | 4.2752 | 2019-05-25 01:37 | 2019-07-01 05:42 | 2019-10-07 00:40 | 2020-03-28 07:51 | 0 | 0 | 0 | 0 | 9.615%
Glenagnes | Overgate | 24 | FALSE | -('024~TR1~MW~AI'+'024~TR2~MW~AI'+'024~TR3~MW~AI') | 4.8126 | 4.3875 | 4.4597 | 4.596 | 2019-05-28 05:08 | 2019-08-01 04:39 | 2019-09-02 03:42 | 2020-03-31 03:55 | 0 | 0 | 0 | 0 | 1.648%
Glenagnes | Walton | 25 | FALSE | ('025~T2_T3_11~AMPS~AI')*1.732*0.011 | 1.3208 | 1.0278 | 1.1136 | 1.6578 | 2019-05-26 02:29 | 2019-08-10 05:16 | 2019-09-01 06:11 | 2020-01-01 09:04 | 0 | 0 | 0 | 0 | 1.648%
Grudie Bridge | Achiltibuie | 505 | FALSE | ('505~T1~MVA~AI') | 0.003081 | 0.017845 | 0.034718 | 0.040673 | 2019-04-29 23:49 | 2019-08-13 07:39 | 2019-10-02 12:18 | 2019-11-29 07:36 | 0.039081 | 0.046525 | 0.070718 | 0.098633 | 46.15%
Grudie Bridge | Achnasheen | 798 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Aultbea | 504 | FALSE | -('504~T1~MW~AI') | 0.4368 | 0.2961 | 0.2982 | 0.5019 | 2019-05-31 23:51 | 2019-07-26 03:47 | 2019-09-10 00:10 | 2020-03-26 01:05 | 0 | 0 | 0 | 0 | 4.121%
Grudie Bridge | Biden Clan Raonaild | 535 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Comrie | 562 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Conon Falls | 514 | FALSE |  | No Data | No Data | No Data | Unreliable Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 81.32%
Grudie Bridge | Cuileig Power Station | 573 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Drumrunie | 518 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Garbat Forest | 567 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Garve | 569 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Inverbroom | 527 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Kerry Falls | 531 | TRUE | ('531~TR1~TR1_AMPS~AI')*1.732*0.011 | 0.058605 | 0.020931 | 0.072096 | 1.358 | 2019-04-29 00:11 | 2019-07-03 00:39 | 2019-10-07 00:16 | 2020-02-13 16:33 | 0 | 0 | 0.0065135 | 1.0496 | 38.74%
Grudie Bridge | Kinlochewe | 532 | FALSE | [9 empty] | 0.22611 | 0.22611 | 0.22611 | 0.22611
Grudie Bridge | Letterewe | 507 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Loch Dubh P S | 799 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Loch Glascarnoch | 568 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Lochinver | 556 | FALSE | ('556~011~AMPS~AI')*1.732*0.011 | 0.40942 | 0.24193 | 0.25123 | 0.3722 | 2019-04-18 23:26 | 2019-08-28 02:10 | 2019-09-02 02:06 | 2020-03-27 01:10 | 0 | 0 | 0 | 0 | 7.418%
Grudie Bridge | Minor Grudie | 564 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Grudie Bridge | Ullapool | 549 | FALSE | ('549~071~AMPS~AI'+'549~072~AMPS~AI')*1.732*0.011 | 0.6574 | 0.53876 | 0.59319 | 0.77325 | 2019-05-15 23:45 | 2019-07-21 03:53 | 2019-09-22 01:52 | 2020-01-23 02:32 | 0 | 0 | 0 | 0 | 1.923%
Inverness | Culloden | 712 | FALSE | ('712~T1~AMPS~AI'+'712~T2~AMPS~AI')*1.732*0.011 | 2.7879 | 2.347 | 2.5117 | 3.2456 | 2019-05-15 02:31 | 2019-08-07 03:49 | 2019-09-24 03:53 | 2020-03-28 02:37 | 0 | 0 | 0 | 0 | 1.648%
Inverness | Dalneigh | 713 | FALSE | ('713~T1_T2~AMPS~AI')*1.732*0.011 | 2.4104 | 1.8853 | 2.2763 | 2.9466 | 2019-05-16 04:56 | 2019-07-13 06:07 | 2019-09-23 03:56 | 2019-11-04 02:35 | 0 | 0 | 0 | 0 | 2.198%
Inverness | Errogie | 761 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Inverness | Foyers | 718 | FALSE | ('718~T1~AMPS~AI')*1.732*0.011 | 0.076747 | 0.068375 | 0.077445 | 0.089539 | 2019-04-30 00:18 | 2019-07-27 05:42 | 2019-09-09 01:21 | 2020-01-22 22:53 | 0 | 0 | 0 | 0 | 3.846%
Inverness | Hilton | 750 | FALSE | ('750~T1_T2~AMPS~AI')*1.732*0.011 | 2.827 | 2.5731 | 2.7126 | 3.3852 | 2019-05-16 03:33 | 2019-07-28 05:29 | 2019-09-24 03:25 | 2019-11-26 02:30 | 0 | 0 | 0 | 0 | 1.648%
Inverness | Inverarnie | 757 | FALSE | ('757~011~AMPS~AI')*1.732*0.011 | 0.083745 | 0.045362 | 0.085141 | Unreliable Data | 2019-04-21 04:50 | 2019-07-31 05:25 | 2019-09-15 15:02 | Missing Data | 0 | 0 | 0 | 0 | 15.93%
Inverness | Inverness 11 Kv | 726 | FALSE | ('725~T1_T2~AMPS~AI')*1.732*0.011 | 2.2369 | 1.9239 | 2.0541 | 2.542 | 2019-05-26 04:51 | 2019-08-07 03:39 | 2019-09-01 03:12 | 2020-03-27 04:49 | 0 | 0 | 0 | 0 | 3.297%
Inverness | Raigmore | 735 | FALSE | ('735~T1_T2~MW~AI') | 4.715 | 4.7058 | 5.003 | 0.01104 | 2019-05-04 22:33 | 2019-06-08 04:42 | 2019-09-22 02:36 | 2019-11-04 02:32 | 0 | 0 | 0 | 0 | 3.022%
Inverness | Waterloo Place | 741 | FALSE | ('741~T1_T2~AMPS~AI')*1.732*0.011 | 4.2979 | 3.4439 | 3.7397 | 4.4095 | 2019-04-28 06:22 | 2019-08-11 05:45 | 2019-09-16 03:38 | 2020-03-31 04:39 | 0 | 0 | 0 | 0 | 1.923%
Inverness | Wester Drummond | 763 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Keith | Aberlour | 460 | FALSE | ('460~T1_T2~AMPS~AI')*1.732*0.011 | 1.5256 | 1.0679 | 1.2726 | 1.2131 | 2019-05-26 02:11 | 2019-08-14 02:20 | 2019-09-01 01:55 | 2020-01-05 02:43 | 0 | 0 | 0 | 0 | 8.242%
Keith | Buckie | 462 | TRUE | ('462~T1_T2~AMPS~AI')*1.732*0.011 | 5.8706 | 5.799 | 5.6812 | 6.2049 | 2019-04-20 03:25 | 2019-06-24 04:00 | 2019-09-09 13:57 | 2020-01-29 10:14 | 3.3286 | 3.2942 | 0.0018606 | 0.0083728 | 1.923%
Keith | Cullen | 469 | FALSE | -('469~TR1~MW~AI') | 0.2745 | 0.2562 | 0.2257 | 0.4026 | 2019-05-02 05:15 | 2019-06-15 01:47 | 2019-10-16 04:21 | 2020-01-21 02:26 | 0 | 0 | 0 | 0 | 21.43%
Keith | Dufftown | 461 | FALSE | ('461~T1_T2~AMPS~AI')*1.732*0.011 | 1.4367 | 1.0235 | 1.2506 | 1.3101 | 2019-05-16 01:55 | 2019-07-04 05:52 | 2019-09-11 04:28 | 2020-01-03 02:18 | 0 | 0 | 0 | 0 | 5.495%
Keith | Huntly | 869 | TRUE | ('869~common~AMPS~AI')*1.732*0.011 | 1.5724 | 1.2031 | 1.2561 | 1.7324 | 2019-05-27 00:33 | 2019-07-24 05:30 | 2019-09-11 01:48 | 2020-03-25 00:50 | 0.29218 | 0.5034 | 0.26612 | 0.34801 | 2.747%
Keith | Insch | 871 | TRUE | ('871~common~AMPS~AI')*1.732*0.011 | 2.9509 | 2.077 | 2.3518 | 2.9179 | 2019-04-22 15:24 | 2019-07-25 14:42 | 2019-09-01 06:28 | 2019-11-04 02:08 | 2 | 2 | 2 | 2 | 5.495%
Keith | Keith | 464 | FALSE | ('463~T1~AMPS~AI'+'463~T2~AMPS~AI')*1.732*0.011 | 2.0875 | 1.6466 | 1.8475 | 1.9871 | 2019-05-26 06:29 | 2019-07-23 02:52 | 2019-10-27 02:08 | 2020-03-01 03:40 | 0 | 0 | 0 | 0 | 9.066%
Keith | Limehillocks | 465 | TRUE | ('465~11KV~AMPS~AI')*1.732*0.011 | 0.17028 | 0.12748 | 0.15912 | 0.23542 | 2019-04-15 10:57 | 2019-08-21 12:50 | 2019-09-07 02:12 | 2019-11-03 22:44 | 0.11631 | 0.053038 | 0.067926 | 0.174 | 21.98%
Keith | Marnoch | 401 | TRUE | ('401~T1_T2~AMPS~AI')*1.732*0.011 | 0.38056 | 0.27106 | 0.4202 | 0.59319 | 2019-05-12 16:27 | 2019-07-20 02:43 | 2019-10-01 05:02 | 2020-03-16 00:19 | 0.90649 | 0.58732 | 0.92404 | 0.79127 | 17.58%
Keith | Portsoy | 435 | TRUE | ('435~TR2~AMPS~AI')*1.732*0.011 | 0.51924 | 0.39275 | 0.55754 | 0.53806 | 2019-05-11 14:22 | 2019-07-14 00:30 | 2019-09-01 23:54 | 2020-01-03 06:07 | 0.15725 | 0.14507 | 0.11935 | 0.19513 | 11.81%
Keith | Rothes | 459 | FALSE | ('459~T1_T2~AMPS~AI')*1.732*0.011 | 2.1904 | 1.5725 | 1.954 | 1.915 | 2019-05-16 01:51 | 2019-07-20 01:48 | 2019-09-01 02:57 | 2019-12-29 02:31 | 0 | 0 | 0 | 0 | 1.923%
Keith | Turriff | 964 | FALSE | -('964~T1~MW~AI'+'964~T2~MW~AI') | 1.0496 | 2.3711 | 3.473 | 3.4118 | 2019-05-15 19:00 | 2019-06-09 01:32 | 2019-09-11 00:51 | 2020-02-22 00:07 | 2.1129 | 0.34464 | 5.6991 | 6.7199 | 20.88%
Killin | Cashlie | 269 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Killin | Chaorach | 140 | FALSE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 61.26%
Killin | Killin Town | 219 | FALSE | ('219~011~AMPS~AI')*1.732*0.011 | 0.25682 | 0.12352 | 0.18773 | 0.31684 | 2019-05-27 00:01 | 2019-08-23 00:05 | 2019-09-12 | 2020-03-17 10:15 | 0 | 0 | 0 | 0 | 13.46%
Killin | Lochearnhead | 217 | TRUE | ('217~common~AMPS~AI')*1.732*0.011 | 0.3273 | 0.23867 | 0.3906 | 0.35489 | 2019-05-24 12:54 | 2019-07-09 23:58 | 2019-09-23 23:52 | 2019-11-05 04:36 | 0 | 0.072579 | 0.3906 | 0.35489 | 18.96%
Killin | Lubnaig | 221 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Kinlochleven | Glencoe | 330 | FALSE | ('330~001~MW~AI') | 0.56061 | 0.40909 | 0.5 | 0.65151 | 2019-05-30 02:30 | 2019-08-08 04:18 | 2019-09-23 02:34 | 2019-11-04 02:39 | 0 | 0 | 0 | 0 | 4.945%
Kintore | Banchory | 810 | FALSE | -('810~T1~MW~AI'+'810~T2~MW~AI') | 2.7627 | 2.3668 | 2.8628 | 3.6037 | 2019-05-16 01:42 | 2019-06-30 05:20 | 2019-09-23 01:31 | 2020-03-31 01:29 | 0 | 0 | 0 | 0 | 1.648%
Kintore | Fyvie | 856 | FALSE | -('856~T1~MW~AI'+'856~T2~MW~AI') | -1.1879 | -1.3388 | -1.7301 | -1.4523 | 2019-04-07 03:08 | 2019-07-27 16:04 | 2019-10-12 13:34 | 2020-02-10 23:01 | 1.0153 | 2.6965 | 2.6126 | 3.1149 | 57.14%
Kintore | Inverurie | 875 | FALSE | -('875~T1~MW~AI'+'875~T2~MW~AI'+'875~TR3~MW~AI') | 3.5604 | 2.7327 | 2.7286 | 3.4046 | 2019-04-16 01:45 | 2019-06-25 04:34 | 2019-09-01 04:27 | 2019-11-04 02:20 | 0.054212 | 0.043468 | 0.042002 | 0.15873 | 3.846%
Kintore | Kemnay | 881 | FALSE | ('881~common~AMPS~AI')*1.732*0.011 | 0.93773 | 0.76656 | 0.84842 | 1.1536 | 2019-05-14 01:21 | 2019-07-11 04:31 | 2019-09-01 04:23 | 2019-11-02 04:10 | 0 | 0 | 0 | 0 | 1.648%
Kintore | Kintore Supergrid | 886 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Kintore | Methlick | 903 | TRUE | ('903~TOTAL~AMPS~AI')*1.732*0.011 | 0.31816 | 0.1871 | 0.27404 | 0.52697 | 2019-05-10 11:08 | 2019-08-06 00:27 | 2019-09-04 04:05 | 2019-11-12 23:57 | 0.078162 | 0.080023 | 0.21681 | 0.44943 | 10.71%
Kintore | Midmar | 907 | FALSE | -('907~T1~MW~AI') | 0.52008 | 0.41248 | 0.44234 | 0.47822 | 2019-05-27 01:56 | 2019-07-18 23:27 | 2019-10-06 23:42 | 2020-01-04 00:53 | 0.25217 | 0.010235 | 0.36941 | 0.25496 | 32.69%
Kintore | Oldmeldrum | 921 | TRUE | ('921~common~AMPS~AI')*1.732*0.011 | 3.2204 | 3.049 | 3.1899 | 3.2499 | 2019-05-25 03:36 | 2019-06-12 01:38 | 2019-10-23 01:38 | 2019-11-04 01:40 | 2.9301 | 2.7588 | 2.8103 | 2.9597 | 1.923%
Kintore | Park | 923 | FALSE | ('923~TR1~AMPS~AI')*1.732*0.011 | 0.57156 | 0.38866 | 0.5487 | 0.77732 | 2019-05-16 02:54 | 2019-08-03 12:44 | 2019-09-04 01:54 | 2019-11-02 00:55 | 0 | 0 | 0 | 0 | 1.648%
Kintore | Skene | 941 | FALSE | -('941~TR1~MW~AI'+'941~TR2~MW~AI') | 3.76 | 3.376 | 3.536 | 3.792 | 2019-05-25 04:15 | 2019-06-30 04:40 | 2019-09-15 03:31 | 2020-03-25 01:17 | 0 | 0 | 0 | 0 | 1.648%
Kintore | Torryburn | 962 | TRUE | ('962~T1~AMPS~AI'+'962~T2~AMPS~AI')*1.732*0.011 | 2.6187 | 2.2522 | 2.4262 | 2.9415 | 2019-05-25 04:23 | 2019-07-07 04:47 | 2019-09-01 04:14 | 2019-12-15 05:45 | 0.034422 | 0.058613 | 0.16561 | 0.0055819 | 1.648%
Lairg | Lairg | 534 | FALSE | ('534~TR1~AMPS~AI')*1.732*0.011 | 0.20238 | 0.15842 | 0.18633 | 0.30218 | 2019-04-29 01:28 | 2019-08-06 02:46 | 2019-09-24 04:26 | 2019-11-02 04:51 | 0 | 0 | 0 | 0 | 1.648%
Lairg | Torboll | 540 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Lairg | Tressady | 548 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Lunanhead | Friockheim | 89 | FALSE | -('089~TR2~MW~AI') | 0.4852 | 0.29819 | 0.51516 | 0.98929 | 2019-04-22 14:07 | 2019-08-29 10:51 | 2019-09-13 12:45 | 2020-03-08 14:16 | 0.4852 | 0.29819 | 0.51516 | 0.63229 | 16.21%
Lunanhead | Inverarity | 87 | FALSE | -('087~TR1~MW~AI') | 0.04 | No Data | No Data | No Data | 2019-04-01 11:26 | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 51.37%
Lunanhead | Lochside | 83 | FALSE | ('083~T1_T2_11~AMPS~AI')*1.732*0.011 | 5.8644 | 5.496 | 6.2572 | 6.3011 | 2019-05-30 01:14 | 2019-06-30 02:16 | 2019-09-14 02:26 | 2020-01-05 02:31 | 0 | 0 | 0 | 0 | 7.143%
Lunanhead | Lunanhead | 82 | TRUE | ('082~T1_T2_11~AMPS~AI')*1.732*0.011 | 1.6603 | 1.1417 | 1.2023 | 1.8331 | 2019-04-21 14:20 | 2019-08-11 06:40 | 2019-09-01 03:20 | 2020-03-25 02:27 | 0.39886 | 0.0030575 | 0.59386 | 1.1689 | 7.143%
Lunanhead | Maryton | 84 | TRUE | ('084~T1_T2_11~AMPS~AI')*1.732*0.011 | 1.4088 | 0.95748 | 0.99936 | 1.6293 | 2019-05-26 05:41 | 2019-08-17 03:48 | 2019-09-01 02:23 | 2020-03-25 02:23 | 0.01861 | 0.013957 | 0.078162 | 0.11631 | 1.648%
Lyndhurst | Lochee | 13 | FALSE | -('013~TR1~MW~AI'+'013~TR2~MW~AI') | 1.516 | 1.3636 | 1.4839 | 1.8448 | 2019-05-16 03:48 | 2019-07-15 05:27 | 2019-09-01 04:09 | 2019-11-04 01:29 | 0 | 0 | 0 | 0 | 1.648%
Lyndhurst | Lyndhurst | 12 | FALSE | ('012~001~AMPS~AI'+'012~002~AMPS~AI'+'012~003~AMPS~AI'+'012~004~AMPS~AI'+'012~005~AMPS~AI'+'012~006~AMPS~AI'+'012~007~AMPS~AI')*1.732*0.011 | 1.2622 | 1.1526 | 1.1479 | 1.5146 | 2019-05-26 05:17 | 2019-06-30 05:51 | 2019-09-01 06:00 | 2020-03-28 06:02 | 0 | 0 | 0 | 0 | 1.648%
Lyndhurst | Macalpine Road | 14 | FALSE | -('014~TR1~MW~AI'+'014~TR2~MW~AI') | 1.6992 | 1.5709 | 1.8114 | 2.132 | 2019-05-16 02:24 | 2019-07-21 05:24 | 2019-09-17 02:24 | 2019-11-04 02:25 | 0 | 0 | 0 | 0 | 1.923%
Lyndhurst | West Kirkton | 15 | FALSE | ('015~T2_T3~AMPS~AI')*1.732*0.011 | 2.1225 | 1.9865 | 2.1519 | 2.4993 | 2019-05-25 02:21 | 2019-07-31 05:24 | 2019-09-24 02:20 | 2020-03-20 02:16 | 0 | 0 | 0 | 0 | 1.648%
Macduff | Macduff New | 406 | TRUE |  | No Data | No Data | No Data | Unreliable Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 94.51%
Milton of Craigie | Ashludie | 55 | FALSE | ('055~T1_T2_11~AMPS~AI')*1.732*0.011 | 2.361 | 2.121 | Unreliable Data | Unreliable Data | 2019-05-24 05:18 | 2019-07-21 05:30 | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 1.648%
Milton of Craigie | Baldovie | 56 | FALSE | ('056~T1_T2_11~AMPS~AI')*1.732*0.011 | 3.4664 | 3.0833 | 2.5684 | 2.3172 | 2019-05-31 23:26 | 2019-07-14 05:31 | 2019-10-09 02:22 | 2020-02-15 23:31 | 0 | 0 | 0 | 0 | 33.24%
Milton of Craigie | Broughty Ferry | 57 | FALSE | -('057~TR1~MW~AI'+'057~TR2~MW~AI') | 1.7153 | 1.5291 | 1.6023 | 1.9015 | 2019-05-16 02:24 | 2019-07-08 04:24 | 2019-09-03 02:24 | 2020-03-26 01:24 | 0 | 0 | 0 | 0 | 1.648%
Milton of Craigie | Edzell Street | 58 | FALSE | ('058~T1_T2~AMPS~AI')*1.732*0.011 | 0.49608 | 0.45352 | 0.54213 | 0.72075 | 2019-05-25 05:16 | 2019-07-07 05:52 | 2019-09-08 04:06 | 2020-03-31 04:53 | 0 | 0 | 0 | 0 | 3.022%
Milton of Craigie | Longhaugh | 54 | TRUE | ('054~T1_T2_T3~AMPS~AI')*1.732*0.011 | 2.4595 | 1.8802 | 2.1388 | 2.7336 | 2019-05-26 05:55 | 2019-06-30 06:19 | 2019-09-12 02:29 | 2019-11-04 01:24 | 0.1821 | 0.3291 | 0.08116 | 0.21542 | 1.648%
Milton of Craigie | Milton Of Craigie | 52 | FALSE | -('052~TR1~MW~AI'+'052~TR2~MW~AI') | No Data | -2.7982 | -2.7262 | -2.1978 | Missing Data | 2019-08-16 23:10 | 2019-10-03 | 2020-02-21 23:57 | 0 | 0 | 0 | 0 | 84.34%
Milton of Craigie | Old Craigie Road | 53 | FALSE | ('053~T2~AMPS~AI'+'053~T3~AMPS~AI')*1.732*0.011 | 1.8256 | 1.5577 | 2.049 | 2.3337 | 2019-04-17 02:09 | 2019-08-11 03:09 | 2019-09-09 02:19 | 2020-03-30 02:25 | 0 | 0 | 0 | 0 | 2.473%
Mybster | Bettyhill | 591 | FALSE | ('591~11KV~AMPS~AI')*1.732*0.011 | 0.21774 | 0.15144 | 0.1954 | 0.22262 | 2019-04-29 13:38 | 2019-08-05 04:43 | 2019-10-22 02:29 | 2020-01-20 02:28 | 0 | 0 | 0 | 0 | 1.923%
Mybster | Coldbackie | 581 | FALSE | ('581~11KV~AMPS~AI')*1.732*0.011 | 0.19052 | 0.14516 | 0.18563 | 0.26589 | 2019-05-01 00:03 | 2019-07-26 04:19 | 2019-09-29 23:13 | 2020-03-27 23:01 | 0 | 0 | 0 | 0 | 5.769%
Mybster | Latheron | 584 | FALSE | ('584~TR1~AMPS~AI')*1.732*0.011 | 0.43673 | 0.3757 | 0.38714 | 0.51683 | 2019-04-26 01:37 | 2019-08-29 23:48 | 2019-09-26 02:39 | 2019-11-01 23:22 | 0 | 0 | 0 | 0 | 9.89%
Mybster | Melvich | 590 | FALSE | ('590~11KV~AMPS~AI')*1.732*0.011 | 0.15353 | Unreliable Data | No Data | Unreliable Data | 2019-05-04 02:41 | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 63.46%
Mybster | Wick | 594 | FALSE | -('594~TR1~MW~AI'+'594~TR2~MW~AI') | 2.8636 | 2.3837 | 2.6557 | 3.0876 | 2019-04-27 00:08 | 2019-08-05 02:53 | 2019-09-22 02:56 | 2020-03-28 04:56 | 0 | 0 | 0 | 0 | 1.648%
Nairn | Ardersier | 779 | FALSE | ('779~T1_T2~AMPS~AI')*1.732*0.011 | 0.47444 | 0.39072 | 0.46328 | 0.68096 | 2019-05-16 02:31 | 2019-08-03 03:39 | 2019-09-25 04:46 | 2019-11-03 02:41 | 0 | 0 | 0 | 0 | 2.473%
Nairn | Dalcross | 752 | TRUE | ('752~11KV~AMPS~AI')*1.732*0.011 | 0.12279 | 0.17489 | 0.4568 | 0.77402 | 2019-05-26 01:01 | 2019-06-02 15:07 | 2019-09-01 00:48 | 2020-03-24 22:45 | 0 | 0 | 0.18145 | 0.1526 | 12.09%
Nairn | Forres | 452 | FALSE | -('452~TR1~MW~AI'+'452~TR2~MW~AI') | 2.6058 | 1.9392 | 1.9392 | 3.03 | 2019-04-20 03:54 | 2019-08-18 01:55 | 2019-09-15 03:55 | 2019-11-03 04:55 | 0 | 0 | 0 | 0 | 1.648%
Nairn | Lethen | 703 | FALSE | ('703~T1~AMPS~AI')*1.732*0.011 | 0.38422 | 0.3284 | 0.36747 | 0.00093031 | 2019-05-30 02:09 | 2019-07-04 02:08 | 2019-09-01 23:56 | 2019-11-25 21:46 | 0 | 0 | 0 | 0 | 4.121%
Nairn | Nairn Central | 723 | FALSE | ('723~11KV~AMPS~AI')*1.732*0.011 | 2.5437 | 2.2696 | 2.4451 | 2.9933 | 2019-05-16 05:14 | 2019-06-30 05:20 | 2019-09-02 02:10 | 2020-03-27 02:27 | 0 | 0 | 0 | 0 | 1.648%
Persley | Bridge Of Don | 814 | FALSE | ('814~TR2~AMPS~AI'+'814~TR1~AMPS~AI')*1.732*0.011 | 3.8741 | 3.4833 | 3.6731 | 4.276 | 2019-05-25 04:28 | 2019-08-11 05:37 | 2019-09-09 01:46 | 2019-11-03 01:34 | 0 | 0 | 0 | 0 | 1.648%
Persley | Haudagain | 865 | FALSE | ('865~common~AMPS~AI')*1.732*0.011 | 1.92 | 1.6689 | 1.8586 | 2.1712 | 2019-05-15 04:41 | 2019-08-04 04:37 | 2019-09-24 04:35 | 2019-11-03 05:20 | 0 | 0 | 0 | 0 | 1.923%
Persley | Mugiemoss Mills | 912 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Persley | Northfield | 917 | FALSE | ('917~TR1~AMPS~AI'+'917~TR2~AMPS~AI')*1.732*0.011 | 1.0645 | 0.96772 | No Data | Unreliable Data | 2019-05-25 04:11 | 2019-07-14 04:54 | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 1.648%
Persley | Persley Supergrid | 924 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Persley | St Machar | 956 | FALSE | ('956~TR1~AMPS~AI'+'956~TR2~AMPS~AI')*1.732*0.011 | 1.3396 | 1.6019 | 1.4122 | 1.1108 | 2019-05-08 04:31 | 2019-07-02 02:09 | 2019-10-14 | 2019-11-06 02:06 | 0 | 0 | 0 | 0 | 9.341%
Persley | Stoneyhill | 475 | FALSE | ('475~T1~MW~AI') | 1.9395 | 1.8517 | 2.0524 | 2.2614 | 2019-04-10 10:11 | 2019-06-11 15:03 | 2019-10-23 16:10 | 2019-12-09 14:45 | 0 | 0 | 0 | 0 | 17.58%
Persley | Stoneyhill Biomass | 476 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Persley | Stoneywood T1&T2 | 947 | FALSE | ('947~TR1~AMPS~AI'+'947~TR2~AMPS~AI')*1.732*0.011 | 3.3726 | 2.1823 | 2.1975 | 2.5027 | 2019-04-21 03:36 | 2019-08-25 02:49 | 2019-09-01 02:25 | 2020-03-28 03:54 | 0 | 0 | 0 | 0 | 1.648%
Persley | Whitestripes | 982 | FALSE | ('982~common~AMPS~AI')*1.732*0.011 | 1.8252 | 1.507 | 1.7136 | 2.1936 | 2019-05-16 04:39 | 2019-07-13 04:38 | 2019-09-22 04:35 | 2019-11-03 04:36 | 0 | 0 | 0 | 0 | 1.648%
Peterhead Grange | Peterhead Grange 11Kv | 928 | FALSE | -('927~T1~MW~AI'+'927~T2~MW~AI') | 4.1443 | 3.5275 | 3.9385 | 4.685 | 2019-05-25 05:10 | 2019-07-06 05:43 | 2019-09-09 02:34 | 2020-03-28 05:57 | 0.041758 | 0.34798 | 0.28278 | 0.17216 | 2.198%
Peterhead Grange | Phead North St | 929 | FALSE | ('929~common~AMPS~AI')*1.732*0.011 | 2.4727 | 2.322 | 2.9527 | 2.3666 | 2019-05-27 04:54 | 2019-06-11 04:32 | 2019-10-02 03:31 | 2020-03-28 05:54 | 0 | 0 | 0 | 0 | 5.769%
Port Ann | Airigh-Na-Brodaig | 319 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Bowmore | 313 | FALSE | -('313~TR1~MW~AI') | 1.04 | 0.784 | 1.024 | -1.024 | 2019-05-15 23:49 | 2019-08-03 03:12 | 2019-09-22 05:09 | 2019-12-11 21:11 | 0 | 0 | 0 | 0 | 38.74%
Port Ann | Crinan | 305 | FALSE | ('305~COMMON~AMPS~AI')*1.732*0.011 | 0.11306 | 0.099098 | 0.13771 | 0.12562 | 2019-05-01 20:09 | 2019-07-07 14:29 | 2019-10-30 08:22 | 2020-03-07 04:03 | 0 | 0 | 0 | 0 | 27.75%
Port Ann | Furnace Quarry | 332 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Inverneil | 309 | FALSE | ('309~T1~AMPS~AI')*1.732*0.011 | 0.040466 | 0.15698 | 0.36698 | 0.29512 | 2019-05-24 05:59 | 2019-08-14 14:08 | 2019-10-26 03:35 | 2019-12-11 03:01 | 0 | 0 | 0 | 0 | 40.38%
Port Ann | Lochgilphead | 308 | FALSE | -('308~T1~MW~AI'+'308~T2~MW~AI') | 2.423 | 1.5128 | 2.0044 | 3.1389 | 2019-04-28 11:33 | 2019-08-01 02:46 | 2019-10-06 07:32 | 2019-12-22 08:48 | 0 | 0.096 | 0 | 0.096 | 20.88%
Port Ann | Lussagiven | 339 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Port Askaig | 334 | FALSE | ('334~common~AMPS~AI')*1.732*0.011 | 0.25217 | 0.25403 | 0.37964 | 0.47549 | 2019-05-25 01:16 | 2019-06-07 23:29 | 2019-09-26 01:08 | 2019-12-29 23:34 | 0 | 0 | 0 | 0 | 5.769%
Port Ann | Port Ellen | 331 | FALSE | ('331~common~AMPS~AI')*1.732*0.011 | 1.0087 | 0.79465 | 0.80581 | 1.1017 | 2019-04-24 23:33 | 2019-08-18 23:47 | 2019-10-16 00:15 | 2020-01-07 23:56 | 0 | 0 | 0 | 0 | 9.89%
Port Ann | Stonefield | 397 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Tarbert Jura | 341 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Port Ann | Tarbert Loch Fyne | 310 | FALSE | -('310~TR1~MW~AI'+'310~TR2~MW~AI') | 0.57872 | 0.11979 | 0.18585 | 0.48683 | 2019-05-16 02:42 | 2019-08-25 02:10 | 2019-09-29 00:47 | 2020-02-01 00:04 | 0.003722 | 0.069787 | 0.13585 | 0.71183 | 14.84%
Port Ann | Tayvallich | 391 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Rannoch | Blackmount | 343 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Rannoch | Bridge Of Gaur | 274 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Rannoch | Glenetive | 345 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Rannoch | Tyndrum | 218 | FALSE | -('218~TR1~MW~AI') | 0.044909 | No Data | No Data | No Data | 2019-04-01 23:29 | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 52.75%
Redmoss | Bp Netherley | 813 | FALSE | ('813~1C0_T1~AMPS~AI'+'813~2C0_GT2~AMPS~AI')*1.732*0.033 | 0.070765 | 0.043547 | 0.024495 | 0.024495 | 2019-05-15 | 2019-06-10 08:22 | 2019-09-19 11:03 | 2019-11-01 00:41 | 0 | 0 | 0 | 0 | 7.143%
Redmoss | Kincorth | 882 | FALSE | ('934~7L5~MW~AI'+'934~8L5~MW~AI') | 2.402 | 2.0897 | 2.426 | 2.7623 | 2019-05-26 05:09 | 2019-07-20 05:10 | 2019-09-01 03:09 | 2020-03-08 02:10 | 0 | 0 | 0 | 0 | 2.198%
Redmoss | Newtonhill | 915 | TRUE | ('915~common~AMPS~AI')*1.732*0.011 | 2.9646 | 2.6962 | 3.0454 | 3.4531 | 2019-05-24 03:43 | 2019-08-18 02:33 | 2019-09-23 03:14 | 2019-12-30 03:43 | 0.67274 | 0.97788 | 0.061408 | 1.6041 | 1.648%
Redmoss | Redmoss | 935 | FALSE | -('935~TR1~MW~AI'+'935~TR2~MW~AI') | 5.0099 | 4.3862 | 5.1708 | 5.7141 | 2019-05-26 05:05 | 2019-08-04 05:42 | 2019-09-01 02:39 | 2019-12-29 02:20 | 0 | 0 | 0 | 0 | 1.648%
Shetland | Brae | 699 | FALSE | ('699~TR1~AMPS~AI')*1.732*0.011 | 0.6977 | 0.43723 | 0.45583 | 0.84655 | 2019-04-22 22:58 | 2019-08-11 02:23 | 2019-09-01 02:53 | 2019-11-02 02:20 | 0 | 0 | 0 | 0 | 3.297%
Shetland | Firth | 692 | FALSE | ('692~T2_11KV~AMPS~AI')*1.732*0.011 | 0.43129 | 0.32102 | 0.45222 | 0.57226 | 2019-05-13 19:15 | 2019-07-28 13:45 | 2019-09-01 00:19 | 2019-12-25 08:22 | 0 | 0 | 0 | 0 | 3.297%
Shetland | Gremista (Lerwick) | 686 | TRUE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | No Data
Shetland | Gutcher | 695 | FALSE | ('695~011~AMPS~AI')*1.732*0.011 | 0.1305 | No Data | Unreliable Data | Unreliable Data | 2019-05-26 10:28 | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 12.91%
Shetland | Mid Yell | 698 | FALSE | ('698~011~AMPS~AI')*1.732*0.011 | 0.21495 | 0.13678 | 0.14795 | 0.25612 | 2019-05-12 09:34 | 2019-07-22 04:30 | 2019-09-11 02:27 | 2019-11-01 23:53 | 0 | 0 | 0 | 0 | 11.81%
Shetland | Sandwick | 693 | FALSE | ('693~T1~MW~AI') | 0.37939 | 0.23376 | 0.30273 | 0.4707 | 2019-05-16 02:55 | 2019-08-11 02:58 | 2019-09-04 02:53 | 2019-11-02 01:47 | 0 | 0 | 0 | 0 | 3.846%
Shetland | Scalloway | 700 | FALSE | ('700~11~AMPS~AI')*1.732*0.011 | 1.2883 | 0.93934 | 1.245 | 1.573 | 2019-05-16 00:27 | 2019-07-28 04:45 | 2019-09-22 02:53 | 2020-03-31 00:17 | 0 | 0 | 0 | 0 | 1.648%
Shetland | Sumburgh | 697 | FALSE | ('697~011~AMPS~AI')*1.732*0.011 | 0.56737 | 0.38174 | 0.49619 | 0.70695 | 2019-05-16 02:59 | 2019-07-29 04:55 | 2019-09-11 22:58 | 2019-11-02 22:49 | 0 | 0 | 0 | 0 | 2.473%
Shetland | Tumblin | 790 | FALSE | ('790~T2~AMPS~AI')*1.732*0.011 | 0.61396 | 0.34884 | 0.38652 | 0.80513 | 2019-05-31 23:23 | 2019-08-30 02:38 | 2019-09-12 02:27 | 2020-03-10 12:25 | 0 | 0 | 0 | 0 | 3.571%
Shetland | UNST | 791 | FALSE | ('791~common~AMPS~AI')*1.732*0.011 | 0.46618 | 0.34615 | 0.4285 | 0.56109 | 2019-04-23 11:21 | 2019-08-27 20:21 | 2019-10-17 11:10 | 2020-03-26 14:52 | 0 | 0 | 0 | 0 | 2.747%
Shetland | VOE | 687 | FALSE | ('687~common~AMPS~AI')*1.732*0.011 | 1.0459 | 0.58808 | 0.85234 | 1.4144 | 2019-05-25 00:24 | 2019-08-11 02:56 | 2019-09-03 02:57 | 2019-11-02 02:27 | 0 | 0 | 0 | 0 | 2.473%
Shin | Gledfield | 523 | FALSE | ('523~T1~AMPS~AI')*1.732*0.011 | 0.33918 | 0.25668 | 0.25179 | 0.42091 | 2019-05-14 14:23 | 2019-06-28 14:17 | 2019-09-20 14:21 | 2019-11-03 22:22 | 0 | 0 | 0 | 0 | 4.67%
Shin | Shin | 536 | FALSE | ('545~T3~MW~AI') | 0.068864 | 0.05348 | 0.060073 | 0.11209 | 2019-04-30 11:58 | 2019-07-29 13:41 | 2019-09-26 14:12 | 2019-11-01 02:31 | 0 | 0 | 0 | 0 | 6.044%
Sloy | Arrochar | 377 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Sloy | Sloy Power Station | 139 | FALSE | [9 empty] | 2.9563 | 2.9563 | 2.9563 | 2.9563
St Fergus Gas | St Fergus Gas Term | 955 | FALSE | -('SFEG~GT1~MW~AI'+'SFEG~GT2~MW~AI') | -7.1688 | -8.4892 | -15.0997 | -16.3314 | 2019-05-26 11:23 | 2019-08-27 16:30 | 2019-10-09 19:24 | 2020-01-19 11:58 | 0.79472 | 0.79844 | 0.62834 | 1.1191 | 65.93%
St Fillans | Dalchonzie | 212 | FALSE | -('212~TR2~MW~AI') | 0.544 | 0.416 | 0.48 | 0.736 | 2019-05-27 23:29 | 2019-07-19 02:25 | 2019-09-06 02:25 | 2019-11-26 23:20 | 0 | 0 | 0 | 0 | 1.648%
Strathleven | Aberfoyle | 206 | FALSE | -('206~T1~MW~AI') | 0.5163 | 0.34684 | 0.45549 | 0.66443 | 2019-05-30 07:27 | 2019-07-24 03:57 | 2019-09-25 00:05 | 2020-03-30 14:45 | 0.41686 | 0.021401 | 1.0431 | 0.094911 | 16.21%
Strathleven | Auchencarroch | 285 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Strathleven | Blairlinnans | 220 | FALSE | ('220~011~AMPS~AI')*1.732*0.011 | 0.061706 | 0.044688 | 0.059782 | 0.13244 | 2019-04-15 15:01 | 2019-08-10 14:37 | 2019-09-05 13:56 | 2020-03-05 14:07 | 0 | 0 | 0 | 0 | 26.65%
Strathleven | Drymen | 203 | TRUE | ('203~T1~AMPS~AI')*1.732*0.011 | 0.62561 | 0.41601 | 0.40145 | 0.58005 | 2019-05-24 15:05 | 2019-08-24 03:58 | 2019-09-13 02:23 | 2020-03-26 01:39 | 0 | 0.18112 | 0.17818 | 0.20562 | 11.26%
Strathleven | Kepculloch | 205 | TRUE | ('205~SUMM~AMPS~AI')*1.732*0.011 | 0.95367 | 0.72184 | 0.73647 | 1.1012 | 2019-05-31 02:04 | 2019-07-12 13:18 | 2019-10-23 14:44 | 2019-12-13 01:44 | 0.17924 | 0.30183 | 0 | 0.074237 | 2.198%
Strathleven | Killearn | 204 | FALSE | ('204~T1~MW~AI') | 0.49639 | 0.32558 | 0.36978 | 0.64744 | 2019-04-22 14:40 | 2019-08-17 03:13 | 2019-09-01 04:41 | 2020-01-08 02:00 | 0 | 0 | 0 | 0 | 6.593%
Strathleven | Ross Priory Pumping Stat. | 239 | FALSE |  | No Data | No Data | No Data | Unreliable Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 91.21%
Strichen | Boddam | 812 | FALSE | ('812~006~AMPS~AI')*1.732*0.011 | 1.9033 | 1.7345 | 1.8419 | 1.7191 | 2019-05-12 04:47 | 2019-07-14 01:02 | 2019-10-18 03:26 | 2020-01-02 03:57 | 0 | 0 | 0 | 0 | 3.022%
Strichen | Hatton | 863 | FALSE | -('863~T1~MW~AI'+'863~T2~MW~AI') | 0.67368 | 0.51328 | 0.54937 | 0.70977 | 2019-04-24 11:20 | 2019-08-29 23:21 | 2019-10-19 03:22 | 2020-03-22 02:24 | 0 | 0 | 0 | 0 | 16.76%
Strichen | Maud | 901 | TRUE | ('901~common~AMPS~AI')*1.732*0.011 | 0.146 | 0.085035 | 0.11059 | 0.26319 | 2019-05-06 00:29 | 2019-07-25 02:55 | 2019-09-04 03:58 | 2020-03-09 14:11 | 0.146 | 0.06643 | 0.09198 | 0.16644 | 27.75%
Strichen | Mintlaw | 909 | FALSE | -('909~T1~MW~AI'+'909~T2~MW~AI') | 1.4456 | 1.2225 | 1.4164 | 1.4543 | 2019-05-29 15:23 | 2019-08-30 04:39 | 2019-09-29 23:17 | 2020-01-08 01:19 | 0.83077 | 1.3817 | 0.45568 | 1.5311 | 21.7%
Strichen | New Pitsligo | 913 | TRUE | ('913~common~AMPS~AI')*1.732*0.011 | -0.73616 | -0.66894 | -0.71907 | -0.77559 | 2019-05-07 01:23 | 2019-07-08 03:45 | 2019-09-03 22:33 | 2019-11-13 00:30 | 0 | 0 | 0 | 0 | 82.42%
Strichen | Strichen | 950 | FALSE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 53.3%
Tarland | Aboyne | 801 | FALSE | ('801~T1~MW~AI'+'801~T2~MW~AI') | 1.5638 | 1.0991 | 1.4182 | 1.9895 | 2019-05-15 00:30 | 2019-07-27 14:49 | 2019-09-21 01:55 | 2020-03-31 00:25 | 0 | 0 | 0 | 0 | 1.648%
Tarland | Ballater | 806 | TRUE | ('806~common~AMPS~AI')*1.732*0.011 | 1.381 | 1.0199 | 1.3177 | 1.7229 | 2019-05-16 00:11 | 2019-06-30 04:28 | 2019-09-26 01:39 | 2020-03-31 00:23 | 0 | 0 | 0 | 0 | 2.473%
Tarland | Mossat | 911 | TRUE | ('911~common~AMPS~AI')*1.732*0.011 | 0.33729 | 0.1907 | 0.22787 | 0.43956 | 2019-05-26 23:58 | 2019-06-18 14:10 | 2019-09-06 14:26 | 2019-11-03 04:40 | 0.12376 | 0.010235 | 0.079092 | 0.14888 | 18.13%
Tarland | Strathdon | 951 | FALSE | ('951~TR1~AMPS~AI')*1.732*0.011 | 0.16759 | 0.099781 | 0.12691 | 0.21603 | 2019-05-11 15:02 | 2019-06-25 04:32 | 2019-09-12 04:30 | 2019-11-03 04:28 | 0 | 0 | 0 | 0 | 20.88%
Tarland | Whitehouse | 981 | FALSE | ('981~T1_T2~AMPS~AI')*1.732*0.011 | 0.99346 | 0.70355 | 1.1079 | 1.3517 | 2019-05-15 13:39 | 2019-07-25 13:45 | 2019-09-04 00:09 | 2020-03-17 10:52 | 0 | 0 | 0 | 0 | 1.923%
Taynuilt | Ardtun Regulator | 344 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Barcaldine | 327 | FALSE | -('327~TR1~MW~AI') | 0.51255 | 0.42813 | 0.47637 | 0.48843 | 2019-04-04 | 2019-07-12 00:52 | 2019-10-27 02:52 | 2020-01-04 23:34 | 0 | 0 | 0 | 0 | 29.4%
Taynuilt | Beochlich | 394 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Blarghour | 351 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Bonawe | 328 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Connel | 306 | FALSE | ('306~T1~AMPS~AI')*1.732*0.011 | 0.32009 | 0.16749 | 0.22704 | 0.4057 | 2019-05-31 02:42 | 2019-07-25 13:32 | 2019-09-07 12:56 | 2019-11-02 13:05 | 0 | 0 | 0 | 0 | 7.143%
Taynuilt | Craigagoul | 381 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Dalmally | 348 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Dervaig | 346 | TRUE | ('346~SS~AMPS~AI')*1.732*0.011 | 0.98735 | 0.60591 | 0.6218 | 0.90842 | 2019-05-13 13:11 | 2019-08-29 00:52 | 2019-09-06 00:51 | 2020-01-13 20:16 | 0 | 0.511 | 0.48781 | 0.18123 | 7.967%
Taynuilt | Eredine | 324 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Kenmore | 329 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Kerrera | 335 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Kilchrenan | 323 | FALSE | ('323~SS~AMPS~AI')*1.732*0.011 | 0.14473 | 0.035112 | 0.034255 | 0.033399 | 2019-04-02 13:11 | 2019-07-15 02:47 | 2019-10-01 01:51 | 2020-01-27 12:15 | 0 | 0 | 0 | 0 | 30.49%
Taynuilt | Kilmelford Ps | 304 | FALSE | ('304~1T0~AMPS~AI')*1.732*0.011 | 0.36282 | 0.20188 | 0.82891 | 0.6354 | 2019-05-15 13:12 | 2019-07-06 12:51 | 2019-10-30 07:10 | 2019-12-30 18:36 | 0 | 0 | 0 | 0 | 31.59%
Taynuilt | Kilninver | 322 | FALSE | ('322~11KV_SS~AMPS~AI')*1.732*0.011 | 0.14027 | 0.071881 | 0.087234 | 0.19889 | 2019-05-28 11:00 | 2019-06-08 23:24 | 2019-09-01 00:16 | 2019-12-14 11:04 | 0 | 0 | 0 | 0 | 22.53%
Taynuilt | Kinloch | 333 | FALSE | ('333~T1~MW~AI') | 0.61172 | 0.263 | 0.29084 | 0.43809 | 2019-04-02 02:43 | 2019-06-27 02:31 | 2019-09-24 02:55 | 2019-11-04 01:53 | 0 | 0 | 0 | 0 | 8.242%
Taynuilt | Lochdonhead | 317 | FALSE | ('317~T1~MW~AI') | 0.30476 | 0.23736 | 0.28669 | 0.33797 | 2019-04-25 00:28 | 2019-08-03 01:18 | 2019-09-04 00:32 | 2020-01-31 23:13 | 0 | 0 | 0 | 0 | 1.648%
Taynuilt | Oban | 307 | FALSE | -('307~TR1~MW~AI'+'307~TR2~MW~AI') | 4.544 | 4.096 | 4.448 | 5.888 | 2019-04-22 23:51 | 2019-08-27 00:01 | 2019-09-25 00:01 | 2020-03-30 00:01 | 0 | 0 | 0 | 0 | 1.648%
Taynuilt | Salen | 315 | FALSE | ('315~TR1~AMPS~AI')*1.732*0.011 | 0.15736 | 0.11535 | 0.14285 | 0.22688 | 2019-04-25 00:29 | 2019-06-26 04:27 | 2019-09-24 23:25 | 2019-11-03 22:28 | 0 | 0 | 0 | 0 | 1.923%
Taynuilt | Scammadale | 340 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Strand Regulator | 316 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Taynuilt | 347 | FALSE | ('347~TAYNUILT~AMPS~AI')*1.732*0.011 | 0.23723 | 0.21141 | 0.23095 | 0.40333 | 2019-04-24 11:39 | 2019-06-14 12:49 | 2019-09-21 12:52 | 2020-03-31 00:30 | 0 | 0 | 0 | 0 | 3.297%
Taynuilt | Tiree | 314 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Taynuilt | Tiroran Bridge | 342 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Thurso | Burgarhill | 701 | FALSE | ('701~011_012~AMPS~AI')*1.732*0.011 | 0.13303 | No Data | No Data | Unreliable Data | 2019-04-07 14:54 | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 88.74%
Thurso | Eday | 675 | FALSE | ('675~11KV~AMPS~AI')*1.732*0.011 | 0.013954 | 0.013954 | 0.011163 | 0.015349 | 2019-04-29 15:44 | 2019-06-04 01:28 | 2019-09-19 16:06 | 2020-01-01 08:55 | 0 | 0 | 0 | 0 | 29.12%
Thurso | Eday Tidal Stream | 492 | FALSE |  | No Data | No Data | Unreliable Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 29.12%
Thurso | Flotta | 680 | FALSE | ('680~TR1~amps~AI')*1.732*0.011 | No Data | No Data | -0.99016 | No Data | Missing Data | Missing Data | 2019-10-17 21:39 | Missing Data | 0 | 0 | 0 | 0 | 61.26%
Thurso | Forss | 583 | TRUE | ('583~TR1~AMPS~AI')*1.732*0.011 | 0.14117 | 0.093491 | 0.14175 | 0.25709 | 2019-05-10 14:38 | 2019-07-28 06:54 | 2019-10-18 05:13 | 2020-03-24 05:37 | 0 | 0.010464 | 0.033603 | 0.15732 | 24.45%
Thurso | Halkirk | 597 | FALSE | -('597~TR1~MW~AI') | 0.64904 | 0.4968 | 0.6811 | 0.7452 | 2019-05-30 13:05 | 2019-08-05 03:53 | 2019-09-05 02:14 | 2019-12-29 00:49 | 0 | 0 | 0 | 0 | 3.571%
Thurso | Hastigrow | 582 | FALSE | ('582~TR1~AMPS~AI')*1.732*0.011 | 0.44271 | 0.012559 | 0.012559 | 0.57156 | 2019-04-29 23:58 | 2019-06-17 07:59 | 2019-09-01 | 2020-03-25 02:11 | 0 | 0 | 0 | 0 | 18.13%
Thurso | Kirkwall | 677 | FALSE | -('677~T1~MW~AI'+'677~T2~MW~AI') | 4.5942 | 3.2487 | 3.1739 | 4.6849 | 2019-05-02 23:55 | 2019-08-20 01:27 | 2019-09-16 23:50 | 2019-11-03 23:35 | 0.50012 | 0.50012 | 0.50012 | 0.50012 | 9.341%
Thurso | Larel | 571 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Thurso | Lyness | 682 | TRUE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | No Data
Thurso | Mount Pleasant | 585 | FALSE | ('585~T1~AMPS~AI')*1.732*0.011 | 1.5284 | 1.46 | 1.7384 | 1.6459 | 2019-04-26 23:16 | 2019-06-27 00:12 | 2019-09-22 03:52 | 2020-03-29 23:10 | 0 | 0 | 0 | 0 | 1.648%
Thurso | North Hoy | 681 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Thurso | Ormlie | 587 | FALSE | ('587~T1~AMPS~AI')*1.732*0.011 | 1.4984 | 1.3438 | 1.49 | 1.7509 | 2019-04-25 23:43 | 2019-07-26 03:10 | 2019-09-05 00:23 | 2019-12-04 04:50 | 0 | 0 | 0 | 0 | 2.198%
Thurso | Rackwick Primary | 489 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Thurso | Rousay | 498 | FALSE |  | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 67.03%
Thurso | Sanday | 685 | FALSE | ('685~011~AMPS~AI')*1.732*0.011 | 0.089328 | 0.052341 | 0.024426 | 0.068392 | 2019-04-08 | 2019-06-20 21:05 | 2019-10-08 11:28 | 2019-12-04 03:27 | 0 | 0 | 0 | 0 | 34.62%
Thurso | Scorradale | 673 | FALSE | [9 empty] | 1.152 | 1.152 | 1.152 | 1.152
Thurso | Shapinsay | 683 | FALSE | ('683~011~AMPS~AI')*1.732*0.011 | No Data | No Data | No Data | 0.10116 | Missing Data | Missing Data | Missing Data | 2020-01-02 23:48 | 0 | 0 | 0 | 0 | 72.8%
Thurso | St Marys | 679 | FALSE | ('679~TR1~AMPS~AI')*1.732*0.011 | 0.26372 | 0.069768 | 0.055815 | 0.068373 | 2019-05-31 23:51 | 2019-08-22 12:13 | 2019-09-05 13:37 | 2019-11-23 07:56 | 0 | 0 | 0 | 0 | 32.42%
Thurso | Stromness | 678 | FALSE | -('678~TR1~MW~AI'+'678~TR2~MW~AI') | 0.79121 | 1.2735 | 1.386 | 1.9015 | 2019-04-16 23:57 | 2019-08-29 13:11 | 2019-09-14 02:25 | 2020-03-21 23:55 | 0 | 0.70485 | 0.70485 | 0.777 | 24.18%
Thurso | Stronsay | 684 | FALSE |  | Unreliable Data | Unreliable Data | Unreliable Data | Unreliable Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0 | 9.066%
Thurso | Westray | 674 | FALSE | -('674~TR1~MW~AI') | -0.72652 | -0.63071 | -0.96774 | -0.68953 | 2019-04-29 11:08 | 2019-06-22 00:19 | 2019-09-15 00:59 | 2020-03-29 11:34 | 0.69926 | 0.27442 | 0.6663 | 1.0086 | 65.93%
Tummel Bridge | Aberfeldy | 267 | TRUE | -('267~TR1~MW~AI'+'267~TR2~MW~AI') | 0.93251 | 0.72393 | 0.76546 | 0.7655 | 2019-04-03 23:40 | 2019-07-28 03:25 | 2019-09-08 04:13 | 2020-03-08 19:26 | 0.61614 | 0 | 0.46584 | 0.76364 | 15.38%
Tummel Bridge | Bonskeid | 266 | FALSE | ('266~common~AMPS~AI')*1.732*0.011 | 0.85141 | 0.69648 | 0.78022 | 1.1082 | 2019-05-27 04:27 | 2019-08-26 03:59 | 2019-09-02 02:22 | 2020-01-06 00:16 | 0 | 0 | 0 | 0 | 3.571%
Tummel Bridge | Calvine | 265 | FALSE | ('265~common~AMPS~AI')*1.732*0.011 | 0.24286 | 0.16889 | 0.17726 | 0.2289 | 2019-05-28 00:36 | 2019-08-09 05:24 | 2019-09-03 00:48 | 2020-01-21 23:03 | 0 | 0 | 0 | 0 | 1.648%
Tummel Bridge | Coshieville | 268 | FALSE | ('268~001~AMPS~AI'+'268~002~AMPS~AI')*1.732*0.011 | 0.23304 | 0.14745 | 0.15269 | 0.088495 | 2019-04-24 01:56 | 2019-06-14 05:25 | 2019-09-04 07:38 | 2019-12-13 14:21 | 0 | 0 | 0 | 0 | 35.44%
Tummel Bridge | Fincastle | 276 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Tummel Bridge | Kinloch Rannoch | 262 | TRUE | ('262~011~AMPS~AI')*1.732*0.011 | 0.25634 | 0.1668 | 0.30021 | 0.37777 | 2019-05-24 01:23 | 2019-08-06 01:38 | 2019-09-23 23:49 | 2019-11-04 02:05 | 0 | 0.00292 | 0.25599 | 0.36207 | 18.13%
Tummel Bridge | Pitlochry | 263 | FALSE | -('263~TR1~MW~AI'+'263~TR2~MW~AI') | 0.94723 | 0.46762 | 0.55155 | 0.53956 | 2019-05-25 02:24 | 2019-06-13 01:34 | 2019-10-01 | 2020-03-09 00:11 | 0 | 0 | 0 | 0 | 27.47%
Willowdale | Denburn | 841 | FALSE | ('841~T1~Amps~ai'+'841~T2~Amps~ai')*1.732*0.011 | 4.3236 | 3.9292 | 4.1376 | 4.1674 | 2019-05-16 04:43 | 2019-07-16 04:17 | 2019-09-22 04:41 | 2020-03-31 00:59 | 0 | 0 | 0 | 0 | 1.648%
Willowdale | Greyfriars | 861 | FALSE | -('861~TR1~MW~AI'+'861~TR2~MW~AI') | 1.6002 | 1.4412 | 1.7183 | 1.9473 | 2019-05-26 04:36 | 2019-06-09 04:33 | 2019-09-01 04:18 | 2020-03-28 03:39 | 0 | 0 | 0 | 0 | 1.648%
Willowdale | Hayton | 867 | FALSE | -('867~T1~MW~AI'+'867~T2~MW~AI') | 0.78944 | 0.85736 | 0.87922 | 1.7558 | 2019-05-12 05:15 | 2019-07-01 06:15 | 2019-09-07 06:08 | 2020-03-28 06:19 | 0.015818 | 0.025123 | 0.017679 | 0.51922 | 6.868%
Willowdale | St Nicholas | 958 | FALSE | -('958~TR1~MW~AI'+'958~TR2~MW~AI') | 1.8114 | 1.587 | 1.7954 | 2.1801 | 2019-05-25 04:39 | 2019-07-14 04:40 | 2019-09-01 04:40 | 2020-03-26 04:40 | 0 | 0 | 0 | 0 | 1.648%
Woodhill | Queens Lane North | 932 | FALSE | ('932~TR1~Amps~AI'+'932~TR3~Amps~AI')*1.732*0.011 | 3.0744 | 2.5903 | 2.9026 | 3.3439 | 2019-05-24 04:29 | 2019-07-28 05:12 | 2019-09-14 03:40 | 2020-03-31 01:58 | 0 | 0 | 0 | 0 | 1.648%
Woodhill | Springhill | 943 | FALSE | ('WOHI~1L5~AMPS~AI')*2*1.732*0.033 | 4.6325 | 4.2641 | 5.3469 | 5.5366 | 2019-05-18 05:19 | 2019-07-14 05:52 | 2019-09-22 03:27 | 2020-03-13 02:21 | 0 | 0 | 0 | 0 | 0%
Woodhill | Woodhill | 986 | FALSE | -('986~TR1~MW~AI'+'986~TR3~MW~AI') | 2.4864 | 2.513 | 2.8709 | 3.3873 | 2019-04-21 05:19 | 2019-06-09 06:06 | 2019-09-25 23:45 | 2020-02-25 23:24 | 0.51236 | 0.16838 | 0.17622 | 0.90632 | 12.91%
Tummel Bridge | Tummel Bridge | 260 | FALSE | ('260~T2_11~AMPS~AI')*1.732*0.011 | 0.21215 | 0.096772 | 0.12003 | 0.18796 | 2019-05-30 00:05 | 2019-08-19 01:35 | 2019-09-01 04:13 | 2020-01-23 03:43 | 0 | 0 | 0 | 0 | 13.19%
Port Ann | Cromalt | 326 | FALSE | -('326~TR1~MW~AI') | 0.2 | 0.144 | 0.184 | 0.232 | 2019-05-16 00:54 | 2019-07-24 01:33 | 2019-09-05 00:54 | 2020-03-31 00:54 | 0 | 0 | 0 | 0 | 1.923%
Dunvegan | Dunvegan | 638 | FALSE | ('638~T1~AMPS~AI')*1.732*0.011 | 0.68671 | 0.48851 | 0.59738 | 0.83559 | 2019-05-14 14:32 | 2019-08-03 05:52 | 2019-09-22 06:24 | 2019-11-04 01:21 | 0 | 0 | 0 | 0 | 3.022%
Dyce | Harvest Avenue | 991 | FALSE | -('991~TR1~MW~AI'+'991~TR2~MW~AI') | Unreliable Data | 0.68 | 0.912 | 1.072 | Missing Data | 2019-08-03 05:27 | 2019-10-07 01:37 | 2019-11-02 02:28 | 0 | 0 | 0 | 0 | 4.121%
Fort Augustus | Ardochy | 894 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Kinlochleven | Kinlochleven | 729 | FALSE | ('729~T1~MW~AI'+'729~T2~MW~AI') | 0.30307 | 0.22103 | 0.27487 | 0.35827 | 2019-05-15 23:54 | 2019-07-30 05:34 | 2019-09-25 23:50 | 2020-03-30 23:51 | 0 | 0 | 0.33219 | 0.24565 | 3.846%
Peterhead Shell | Peterhead Shell | 926 | FALSE | [9 empty] | 0 | 0 | 0 | 0
Dounreay | DSRL |  | FALSE | ('598~T1~MW~AI'+'598~T2~MW~AI') | 2.8954 | 2.5616 | 2.568 | 3.0046 | 2019-04-21 17:48 | 2019-07-27 08:24 | 2019-09-28 12:51 | 2020-03-27 16:15 | 0 | 0 | 0 | 0 | 1.648%
Bridge of Dun | Glaxo (33kV Customer) |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
|  |  | FALSE | [9 empty] | 0 | 0 | 0 | 0
Note on B249: Mills, David: Due to measurement point for generation it is not possible to distinguish between load and generation at this site

## SubstationLoad_Min_GSPs
GSP | Load - Filtered Data (Minimum Net of Generation) |  |  |  | Time of Minimum for Filtered Data |  |  |  | Generation at time of Minimum |  |  |  | Minimum Demand Overall | Time of Minimum Demand Overall | Generation at time of Minimum Demnad Overall
| Minimum Spring | Minimum Summer | Minimum Autumn | Minimum Winter | Minimum Spring | Minimum Summer | Minimum Autumn | Minimum Winter | Minimum Spring | Minimum Summer | Minimum Autumn | Minimum Winter
Abernethy | 10.1566 | 7.3083 | 9.3843 | 9.5657 | 2019-05-27 04:08 | 2019-08-18 02:57 | 2019-09-24 01:31 | 2020-02-08 02:27 | 2.7906 | 8.0394 | 2.7515 | 11.2111 | 7.3083 | 2019-08-18 02:57 | 8.0394
Alness | -16.5177 | -22.039 | -30.0836 | -32.6492 | 2019-04-18 23:46 | 2019-06-29 20:33 | 2019-10-20 01:54 | 2019-12-15 21:27 | 18.9764 | 12.972 | 49.2536 | 39.1021 | -32.6492 | 2019-12-15 21:27 | 39.1021
AN SUIDHE | 0.1807 | 0.07645 | 0.07645 | 0.278 | 2019-05-07 10:21 | 2019-06-05 18:13 | 2019-10-11 07:01 | 2019-11-22 18:01 | 0 | 0 | 0 | 0 | 0.07645 | 2019-06-05 18:13 | 0
Arbroath | 9.6485 | 7.8013 | 8.3031 | 10.2331 | 2019-05-03 13:10 | 2019-08-17 14:36 | 2019-09-21 14:40 | 2020-03-29 10:19 | 6.1695 | 6.5483 | 7.0728 | 7.0953 | 7.8013 | 2019-08-17 14:36 | 6.5483
Ardkinglas | -7.8144 | -6.0984 | -7.788 | -9.0816 | 2019-05-02 20:46 | 2019-08-26 18:42 | 2019-10-13 11:35 | 2020-02-05 08:28 | 0 | 0 | 0 | 0 | -9.0816 | 2020-02-05 08:28 | 0
Ardmore | -18.3115 | -14.0726 | -18.482 | -22.7299 | 2019-04-28 18:36 | 2019-07-10 20:44 | 2019-09-29 23:25 | 2019-11-24 00:29 | 0.95971 | 0.16703 | 0.18266 | 0.24908 | -22.7299 | 2019-11-24 00:29 | 0.24908
Beauly | 6.9556 | 5.3555 | 3.0611 | 2.4373 | 2019-04-20 01:35 | 2019-07-23 23:59 | 2019-09-18 23:20 | 2020-02-02 02:17 | 0.066996 | 0.19727 | 0.19354 | 0.45967 | 2.4373 | 2020-02-02 02:17 | 0.45967
Berryburn | -61.3318 | -70.4365 | -91.397 | -122.5835 | 2019-04-27 03:27 | 2019-06-11 17:13 | 2019-10-31 17:45 | 2020-02-20 10:23 | 0 | 0 | 0 | 0 | -122.5835 | 2020-02-20 10:23 | 0
Boat of Garten | 6.2663 | 3.8984 | 4.3677 | 6.7948 | 2019-05-30 22:52 | 2019-07-11 00:59 | 2019-09-14 20:53 | 2020-03-29 00:51 | 0 | 0.95144 | 9.1746 | 18.655 | 3.8984 | 2019-07-11 00:59 | 0.95144
Braco West | -21.3715 | -27.888 | -43.6391 | -54.1327 | 2019-04-01 20:25 | 2019-08-07 16:29 | 2019-10-21 22:25 | 2019-11-27 23:35 | 0.13864 | 0.13957 | 0.05583 | 0.15539 | -54.1327 | 2019-11-27 23:35 | 0.15539
Bridge of Dun | -2.7441 | -1.3511 | -8.4277 | -12.2808 | 2019-04-24 04:06 | 2019-07-13 23:14 | 2019-10-10 23:10 | 2020-01-24 02:18 | 1.7672 | 0.97659 | 0.66006 | 0.51655 | -12.2808 | 2020-01-24 02:18 | 0.51655
Broadford | 4.0146 | 2.8843 | 2.9743 | 4.2331 | 2019-05-31 23:53 | 2019-08-28 04:22 | 2019-09-02 01:00 | 2020-01-23 23:09 | 0 | 0 | 0 | 0 | 2.8843 | 2019-08-28 04:22 | 0
Brora | 2.6506 | 1.7218 | 1.9257 | 2.7526 | 2019-05-08 23:41 | 2019-08-19 02:30 | 2019-09-02 00:13 | 2019-11-25 23:11 | 0 | 0 | 0 | 0 | 1.7218 | 2019-08-19 02:30 | 0
Burghmuir | 14.2081 | 12.1038 | 13.474 | 16.3613 | 2019-05-26 05:27 | 2019-07-07 05:27 | 2019-09-02 02:13 | 2020-03-31 23:59 | 0 | 0 | 0 | 0 | 12.1038 | 2019-07-07 05:27 | 0
Cairnford | -25.8004 | -35.7003 | -46.843 | -47.4861 | 2019-05-25 00:39 | 2019-08-08 01:55 | 2019-10-04 03:30 | 2019-11-19 23:41 | 0 | 0 | 0 | 0 | -47.4861 | 2019-11-19 23:41 | 0
Carradale | -35.7967 | -36.886 | -44.0323 | -61.2073 | 2019-05-29 23:58 | 2019-07-06 00:01 | 2019-09-07 02:15 | 2020-03-01 15:57 | 0.16992 | 0.04248 | 0.13623 | 0.3252 | -61.2073 | 2020-03-01 15:57 | 0.3252
Cassley | -1.2259 | -5.2279 | -6.8583 | -8.8457 | 2019-05-10 01:38 | 2019-06-23 16:50 | 2019-10-22 13:35 | 2019-11-28 16:44 | 0.7844 | 2.8847 | 5.8905 | 6.3886 | -8.8457 | 2019-11-28 16:44 | 6.3886
Ceannacroc | -1.6457 | -10.3301 | -8.3221 | -14.9664 | 2019-05-12 01:23 | 2019-08-22 10:44 | 2019-10-11 11:14 | 2019-11-14 06:54 | 0.729 | 1.287 | 0.606 | 0.918 | -14.9664 | 2019-11-14 06:54 | 0.918
Charleston | 7.6797 | 7.3114 | 7.6797 | 7.9925 | 2019-05-19 06:02 | 2019-07-07 05:09 | 2019-09-29 03:09 | 2020-03-24 08:09 | 0 | 0 | 0 | 0 | 7.3114 | 2019-07-07 05:09 | 0
Clachan | -1.7717 | -1.0831 | -1.1299 | 0.082062 | 2019-04-28 18:54 | 2019-06-02 04:18 | 2019-09-15 22:37 | 2020-01-29 13:01 | 0.12094 | 0.94136 | 0.19443 | 1.9352 | -1.7717 | 2019-04-28 18:54 | 0.12094
Clayhills | 8.9815 | 8.5415 | 10.4775 | 10.7635 | 2019-05-25 04:35 | 2019-07-06 04:39 | 2019-09-12 04:13 | 2020-03-27 01:59 | 0 | 0 | 0 | 0 | 8.5415 | 2019-07-06 04:39 | 0
Coupar Angus | -9.9185 | -9.5903 | -10.6471 | -11.197 | 2019-04-04 08:17 | 2019-08-15 20:56 | 2019-10-22 16:53 | 2020-01-30 04:44 | 5.1589 | 1.8136 | 3.9148 | 1.488 | -11.197 | 2020-01-30 04:44 | 1.488
Craigiebuckler | 8.0868 | 7.4472 | 8.3498 | 9.3421 | 2019-05-19 05:56 | 2019-07-14 05:34 | 2019-09-01 04:30 | 2020-03-23 04:41 | 0 | 0.92793 | 0.93689 | 0.9476 | 7.4472 | 2019-07-14 05:34 | 0.92793
Dallas | -53.9745 | -82.1014 | -104.1652 | -109.9995 | 2019-05-30 22:33 | 2019-08-04 22:14 | 2019-10-01 16:47 | 2019-12-13 13:22 | 0 | 0 | 0 | 0 | -109.9995 | 2019-12-13 13:22 | 0
Dounreay | -5.2523 | -4.5387 | -5.6674 | -5.0135 | 2019-05-11 13:49 | 2019-06-08 15:27 | 2019-09-03 23:19 | 2020-02-28 21:27 | 35.0765 | 19.5564 | 33.4582 | 41.5294 | -5.6674 | 2019-09-03 23:19 | 33.4582
Dudhope | 14.4327 | 12.7261 | 14.0738 | 15.297 | 2019-05-25 05:24 | 2019-08-04 05:56 | 2019-09-02 02:05 | 2020-03-31 02:25 | 0 | 0 | 0 | 0 | 12.7261 | 2019-08-04 05:56 | 0
Dunbeath Dube | -11.3412 | -11.9659 | -13.7796 | -17.1961 | 2019-05-22 15:51 | 2019-06-08 15:44 | 2019-09-07 05:52 | 2020-03-22 00:55 | 0 | 0 | 0 | 0 | -17.1961 | 2020-03-22 00:55 | 0
Dunvegan | -19.5788 | -19.1031 | -36.6916 | -31.7115 | 2019-04-29 02:07 | 2019-07-11 04:55 | 2019-09-30 14:38 | 2019-12-30 00:01 | 0 | 0 | 0 | 0 | -36.6916 | 2019-09-30 14:38 | 0
Dunoon | -1.9855 | -3.5286 | -6.8962 | -8.0747 | 2019-05-17 01:15 | 2019-06-04 23:57 | 2019-10-17 20:08 | 2020-03-21 21:39 | 0 | 0.29404 | 0.46897 | 0.067926 | -8.0747 | 2020-03-21 21:39 | 0.067926
Dyce | 3.0299 | 1.1163 | -1.6803 | -5.0854 | 2019-04-17 00:05 | 2019-07-03 02:26 | 2019-10-25 05:58 | 2019-11-23 22:17 | 0.42798 | 0.31912 | 0.52986 | 4.8551 | -5.0854 | 2019-11-23 22:17 | 4.8551
Edinbane | -17.2469 | -11.6187 | -21.16 | -26.0394 | 2019-05-07 19:19 | 2019-08-14 23:36 | 2019-10-12 07:47 | 2020-03-17 13:48 | 0 | 0 | 0 | 0 | -26.0394 | 2020-03-17 13:48 | 0
Elgin | 14.9483 | 12.9552 | 14.2839 | 16.9414 | 2019-05-19 02:39 | 2019-06-23 04:49 | 2019-09-15 02:22 | 2019-12-29 02:15 | 0 | 0 | 0 | 0 | 12.9552 | 2019-06-23 04:49 | 0
Fasnakyle | -40.0636 | -45.0595 | -44.8121 | -62.2215 | 2019-05-15 18:05 | 2019-06-21 08:06 | 2019-09-12 21:56 | 2019-12-22 19:50 | 0 | 0 | 0 | 0 | -62.2215 | 2019-12-22 19:50 | 0
Fort Augustus | No Data | -1.8064 | -1.3126 | -4.0496 | Missing Data | 2019-08-24 00:17 | 2019-10-14 02:15 | 2020-03-12 16:40 | 0 | 1.3052 | 1.0128 | 2.4758 | -4.0496 | 2020-03-12 16:40 | 2.4758
Fetteresso | -58.3392 | -67.0032 | -91.224 | -108.3304 | 2019-05-22 18:10 | 2019-07-14 06:29 | 2019-09-29 10:27 | 2019-11-08 05:14 | 0 | 0 | 0 | 0 | -108.3304 | 2019-11-08 05:14 | 0
Fiddes | -28.606 | -29.5619 | -48.7719 | -71.1041 | 2019-04-05 11:40 | 2019-06-29 18:01 | 2019-10-16 11:50 | 2020-02-20 14:52 | 2.2516 | 3.4354 | 5.0141 | 6.8763 | -71.1041 | 2020-02-20 14:52 | 6.8763
Fraserburgh | 3.9011 | 3.6146 | 3.0908 | 4.1008 | 2019-05-25 01:37 | 2019-07-01 05:42 | 2019-10-07 00:47 | 2020-03-28 07:46 | 0 | 0 | 0 | 0 | 3.0908 | 2019-10-07 00:47 | 0
Fort William | -3.6607 | 5.0908 | -11.088 | -19.047 | 2019-04-06 17:35 | 2019-07-27 15:23 | 2019-10-20 05:27 | 2020-01-09 02:54 | 1.1098 | 2.6349 | 1.5515 | 1.7944 | -19.047 | 2020-01-09 02:54 | 1.7944
Glenagnes | No Data | 0.031399 | 0.029306 | No Data | Missing Data | 2019-08-27 | 2019-10-01 13:51 | Missing Data | 0 | 0 | 0 | 0 | 0.029306 | 2019-10-01 13:51 | 0
Grudie Bridge | 1.441 | -14.2584 | -17.9721 | -27.5823 | 2019-05-20 23:45 | 2019-08-02 02:44 | 2019-09-20 00:54 | 2020-03-22 02:27 | 0 | 0.086536 | 0.32381 | 1.6265 | -27.5823 | 2020-03-22 02:27 | 1.6265
Inverness | 15.2308 | 10.5977 | 10.5116 | 14.7445 | 2019-04-09 02:28 | 2019-08-19 02:25 | 2019-09-06 04:53 | 2020-01-30 04:44 | 2.9242 | 10.7281 | 19.2855 | 26.8562 | 10.5116 | 2019-09-06 04:53 | 19.2855
Keith | -63.0429 | -69.5243 | -120.1741 | -136.5143 | 2019-04-27 00:18 | 2019-07-08 17:09 | 2019-09-28 11:23 | 2020-01-12 23:47 | 7.3336 | 7.5247 | 9.8149 | 9.2218 | -136.5143 | 2020-01-12 23:47 | 9.2218
Macduff | -13.2111 | -11.4133 | -20.3571 | -24.4862 | 2019-04-18 18:13 | 2019-08-08 01:57 | 2019-10-08 01:20 | 2020-03-02 23:34 | 9.2924 | 12.0559 | 12.1565 | 13.0321 | -24.4862 | 2020-03-02 23:34 | 13.0321
Killin | -7.2727 | -10.1892 | -12.2624 | -12.8357 | 2019-04-28 00:06 | 2019-06-20 03:54 | 2019-10-03 21:33 | 2020-02-27 12:00 | 4.2752 | 3.8124 | 0.47833 | 1.0287 | -12.8357 | 2020-02-27 12:00 | 1.0287
Kinlochleven | 19.9102 | 19.5925 | 18.1888 | 20.0195 | 2019-05-02 13:23 | 2019-07-27 13:09 | 2019-10-30 13:20 | 2019-11-04 09:12 | 0 | 2.88 | 2.9906 | 3.1944 | 18.1888 | 2019-10-30 13:20 | 2.9906
Kintore | 2.2186 | -6.6937 | -14.0801 | -21.3819 | 2019-05-25 00:46 | 2019-07-03 22:52 | 2019-10-12 13:29 | 2020-02-19 08:08 | 5.6733 | 5.0677 | 5.7395 | 11.957 | -21.3819 | 2020-02-19 08:08 | 11.957
Lairg | -31.9948 | -33.2888 | -48.9113 | -51.6585 | 2019-04-19 01:37 | 2019-07-25 16:01 | 2019-09-23 18:11 | 2019-12-13 08:44 | 0 | 0 | 0 | 0 | -51.6585 | 2019-12-13 08:44 | 0
Lunanhead | 10.6291 | 8.7107 | 9.9347 | 10.577 | 2019-05-23 00:25 | 2019-06-30 03:19 | 2019-09-06 02:31 | 2020-01-03 02:25 | 0 | 1.0511 | 1.5993 | 0.78758 | 8.7107 | 2019-06-30 03:19 | 1.0511
Lyndhurst | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0
Milton of Craigie | 9.5624 | 8.0301 | 8.6685 | 11.1701 | 2019-05-26 05:24 | 2019-07-13 05:23 | 2019-09-11 02:17 | 2020-02-22 02:26 | 0.11448 | 0 | 0.48394 | 0.47708 | 8.0301 | 2019-07-13 05:23 | 0
Mybster | -113.6888 | -96.7783 | -143.2909 | -164.576 | 2019-05-08 13:39 | 2019-06-15 10:09 | 2019-09-01 12:32 | 2019-11-14 14:47 | 7.7151 | 3.8935 | 11.6026 | 14.5557 | -164.576 | 2019-11-14 14:47 | 14.5557
Nairn | 9.3788 | 7.9196 | 8.7552 | 11.6577 | 2019-05-07 01:58 | 2019-07-25 02:10 | 2019-09-27 00:17 | 2019-12-21 23:36 | 0 | 0.16098 | 0.079092 | 0.14144 | 7.9196 | 2019-07-25 02:10 | 0.16098
Orrin | No Data | -0.7907 | 0.049648 | 11.634 | Missing Data | 2019-08-08 23:35 | 2019-10-28 15:26 | 2020-03-03 16:00 | 0 | 0 | 0.058608 | 0 | -0.7907 | 2019-08-08 23:35 | 0
Glenfarclas | -48.7388 | -55.676 | -67.3204 | -92.5914 | 2019-04-08 23:58 | 2019-06-05 13:32 | 2019-10-16 13:38 | 2020-01-24 00:02 | 0 | 0 | 0 | 0 | -92.5914 | 2020-01-24 00:02 | 0
Peterhead Grange | -33.953 | -33.9937 | -34.3752 | -33.0841 | 2019-05-26 16:17 | 2019-06-05 05:45 | 2019-10-29 00:47 | 2020-03-31 15:48 | 0.07326 | 0.072527 | 0.059341 | 0.83736 | -34.3752 | 2019-10-29 00:47 | 0.059341
Peterhead Shell | -5.3476 | -4.8286 | -4.9952 | -5.119 | 2019-04-14 10:15 | 2019-08-25 13:39 | 2019-09-15 10:55 | 2020-02-02 11:36 | 0 | 0 | 0 | 0 | -5.3476 | 2019-04-14 10:15 | 0
Persley | 13.6703 | 11.1502 | 12.0293 | 13.7143 | 2019-05-16 04:43 | 2019-08-11 05:38 | 2019-09-22 02:59 | 2020-03-27 03:49 | 0 | 0 | 0 | 0 | 11.1502 | 2019-08-11 05:38 | 0
Port Ann | -23.4351 | -29.3464 | -34.2503 | -35.8396 | 2019-05-15 13:48 | 2019-06-09 03:19 | 2019-10-02 05:35 | 2020-01-22 09:37 | 5.2339 | 6.36 | 7.4819 | 6.4204 | -35.8396 | 2020-01-22 09:37 | 6.4204
Rannoch | -28.9237 | -29.8013 | -19.8337 | -41.3937 | 2019-05-10 18:55 | 2019-07-04 23:34 | 2019-10-11 05:36 | 2019-11-17 20:55 | 0 | 0 | 0 | 0 | -41.3937 | 2019-11-17 20:55 | 0
Redmoss | 9.331 | 5.9484 | 1.951 | 1.5029 | 2019-05-12 18:29 | 2019-06-01 00:28 | 2019-09-26 00:12 | 2020-01-29 03:54 | 1.2505 | 0.39543 | 0.68387 | 0.58059 | 1.5029 | 2020-01-29 03:54 | 0.58059
St Fergus Gas | -5.2978 | -8.4892 | -15.0997 | -16.3314 | 2019-05-17 21:42 | 2019-08-27 16:30 | 2019-10-09 19:24 | 2020-01-19 11:58 | 0 | 0.79844 | 0.62834 | 1.1191 | -16.3314 | 2020-01-19 11:58 | 1.1191
St Fillans | -1.1552 | No Data | 0.5054 | 0.7558 | 2019-04-24 08:10 | Missing Data | 2019-10-30 06:08 | 2020-02-21 17:45 | 0 | 0 | 0 | 0 | -1.1552 | 2019-04-24 08:10 | 0
Shetland | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0
Shin | -28.4395 | -31.2187 | -33.6812 | -46.5654 | 2019-05-07 17:01 | 2019-08-06 15:05 | 2019-10-28 | 2020-01-26 02:47 | 0 | 0 | 0 | 0 | -46.5654 | 2020-01-26 02:47 | 0
Sloy | -1.1733 | 0.6615 | 2.2384 | 4.2146 | 2019-05-29 18:54 | 2019-08-09 06:18 | 2019-09-09 | 2019-12-14 03:21 | 0.39889 | 1.1633 | 2.3388 | 4.1811 | -1.1733 | 2019-05-29 18:54 | 0.39889
Strathleven | -6.9 | -2.5303 | -2.9406 | -2.8836 | 2019-05-21 03:14 | 2019-06-27 22:40 | 2019-10-09 23:24 | 2019-11-27 05:54 | 0 | 0 | 0 | 0 | -6.9 | 2019-05-21 03:14 | 0
Strichen | -13.3207 | -14.2404 | -16.5895 | -18.1859 | 2019-05-26 11:15 | 2019-06-22 14:57 | 2019-10-12 14:16 | 2019-11-05 00:01 | 0 | 0 | 0 | 0 | -18.1859 | 2019-11-05 00:01 | 0
Tarland | -8.6789 | -19.8971 | -22.3695 | -22.4904 | 2019-05-02 11:44 | 2019-06-23 17:13 | 2019-09-03 00:02 | 2019-11-18 01:39 | 0 | 0 | 0 | 0 | -22.4904 | 2019-11-18 01:39 | 0
Taynuilt | -15.568 | -9.5421 | 4.8339 | 0.97974 | 2019-05-27 21:25 | 2019-07-18 21:20 | 2019-10-14 18:56 | 2020-01-15 13:19 | 0 | 0 | 0 | 0 | -15.568 | 2019-05-27 21:25 | 0
Thurso | No Data | No Data | No Data | No Data | Missing Data | Missing Data | Missing Data | Missing Data | 0 | 0 | 0 | 0
Tummel Bridge | -8.6278 | -13.6771 | -23.373 | -38.5314 | 2019-05-04 11:26 | 2019-07-19 14:34 | 2019-09-15 02:10 | 2019-11-18 15:49 | 0 | 0 | 0 | 0 | -38.5314 | 2019-11-18 15:49 | 0
Willowdale | 10.6396 | 9.2899 | 9.408 | 10.6355 | 2019-05-25 04:35 | 2019-08-30 04:39 | 2019-09-01 04:32 | 2020-03-28 05:37 | 0 | 0 | 0 | 0 | 9.2899 | 2019-08-30 04:39 | 0
Woodhill | 10.4601 | 8.8745 | 8.8811 | 11.5166 | 2019-05-18 03:54 | 2019-07-19 02:38 | 2019-09-02 03:34 | 2020-03-24 00:47 | 0 | 0 | 0 | 0 | 8.8745 | 2019-07-19 02:38 | 0
Quoich | [8 empty] | 0 | 0 | 0 | 0
Stornoway | [8 empty] | 0 | 0 | 0 | 0
Harris | [8 empty] | 0 | 0 | 0 | 0
Helensburgh (SP) | [8 empty] | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 | 0
Formulas:
Time of Minimum Demand Overall = IF([Minimum Demand Overall]="","",IF([Minimum Demand Overall]=[Minimum Spring],[Time of Minimum for Filtered Data],IF([Minimum Demand Overall]=[Minimum Summer],[Minimum Summer],IF([Minimum Demand Overall]=[Minimum Autumn],[Minimum Autumn],IF([Minimum Demand Overall]=[Minimum Winter],[Minimum Winter])))))

## Sheet1
Change on Min
CONON FALLS | 514 | removed Tag that doesn’t work | Y | Done
GLAXO (33kV Customer) | #N/A | 33 Customer
INVERALMOND |  | PI tag does work but data not being considered due to only being since November | Y | Done
BP BALBEGGIE | #N/A | 33 Customer
CRAIGIEBUCKLER | 830 | Manual Calc Req |  | Done
CRAIGTON | 834 | Manual Calc Req |  | Done
RUTHRIESTON | 939 | Manual Calc Req |  | Done
DUNVEGAN | #N/A | Added | Y | Run required
HARVEST AVENUE | #N/A | Added | Y | Run required
ARDOCHY | #N/A | Added | Y | Run required
DUNMAGLASS | #N/A | Removed |  | Done
KINLOCHLEVEN | #N/A | Added + Gen | Y | Run required
LAIRG | 534 | Changed text to 'Lairg' | Y | Done
NORTH HOY 33KV TRANSFORMER | #N/A | NRN incorrect, changed in GSP lookup to Tressady |  | Done
MACDUFF NEW | 406 | PI tag does work but data not being considered | Y | Manual
NORTH STREET | #N/A | Changed to PHEAD |  | Done
PETERHEAD SHELL | #N/A | Manual Calc Req
CROMALT | #N/A | Added | Y | Run required
QUOICH PRIMARY | 748 | Add Prim + Gen (requires fixing) | Y
GREMISTA (LERWICK) | 686
SETTER SANDWICK | #N/A | Removed Setter |  | Done
SHETLAND GAS PLANT | #N/A | 33 Customer
ST FILLANS 33/LV | #N/A | Removed |  | Removed
SALEN | 315 | Removed 'Mull Primary' text | Y | Done
ABERFELDY | 267 | Can't figure out why PI tag isnt being picked up |  | Manual
TUMMEL BRIDGE | #N/A | PI tag not carring into calculator | Y | Manual
DSRL |  | Manual Calc Req
BETTYHILL |  | Change to Dounreay GSP | Y | Done
COLDBACKIE |  | Change to Dounreay GSP | Y | Done
FORSS |  | Change to Dounreay GSP | Y | Done
MELVICH |  | Change to Dounreay GSP | Y | Done